## ORCdata
NOTE: | THERMAL power output - substract 2kW thermal loss at the turbine and piping; substract ballast heat in lubrication oil - 0.05*m_dot_MM, cp oil is xx |  |  |  |  | m_dot_mm is a result of balance of the condenser (thermal power output, enthalpy of the condensate)
| "steady states" : | kW | start time | end time | =0,0042*t (°C)+2,096 | you can close the balance with heat input to the cycle (neglect pressure drops at the liquid and consider temperature after pump equal to the condensate)
|  | 120 | 10:42 | 12:07
|  | 100 | 13:04 | 14:17 |  | electrical efficiency of the generator:
|  | 80 | 14:26 | 15:10 |  |  | y = 0.0057x3 - 0.0968x2 + 0.5295x + 2E-13
|  | 60 | 16:15 | 17:38
Time Stamp | Turbine inlet temperature (°C) | Turbine inlet superheat (K) | Condensate temperature (°C) | Turbine inlet pressure (kPa abs) | Turbine outlet pressure (kPa abs) | Thermal power output (kW) | turbine rpm | Generator el. power (W) | Generator sum electricity produced (kWh) | Total heat produced (GJ)
2023-05-18 09:00 |  | -81.9 | 9.5 | 79.4
2023-05-18 09:01 |  | -81.8 | 9.4 | 79.3
2023-05-18 09:02 |  |  | 9.5 | 79.4
2023-05-18 09:03 |  |  |  | 79.3
2023-05-18 09:04 |  |  |  |  | 79.5
2023-05-18 09:05 |  | -81.8 |  | 79.3 | 79.6
2023-05-18 09:06 |  | -81.9 |  | 79.4 | 79.6
2023-05-18 09:07 | 11 | -82 |  | 79.5 | 79.7
2023-05-18 09:08 | 11.1 | -81.9 |  | 79.6
2023-05-18 09:15 | 11.1 | -81.9 | 9.5 | 79.6 | 79.7
2023-05-18 09:16 | 11 | -72.4 | 9.6 | 60.9 | 61.3
2023-05-18 09:17 | 10.9 | -61.4 | 9.5 | 43.8 | 44.4
2023-05-18 09:18 |  | -54.2 | 9.6 | 32.8 | 33.5
2023-05-18 09:19 | 10.9 | -48.3 |  | 25.5 | 26.1
2023-05-18 09:20 | 10.8 | -43.1 |  | 20 | 20.7
2023-05-18 09:21 |  | -38.1 |  | 16.4 | 17
2023-05-18 09:22 |  | -33.9 |  | 14 | 14.6
2023-05-18 09:23 |  | -30.8 |  | 12.4 | 13
2023-05-18 09:24 |  | -28.3 |  | 11.1 | 11.9
2023-05-18 09:25 |  | -26.2 |  | 10.2 | 10.6
2023-05-18 09:26 |  | -25.6 |  | 9.9 | 10.4
2023-05-18 09:27 | 10.8 | -23.4 |  | 8.9 | 9.6
2023-05-18 09:28 | 10.7 | -22 |  | 8.3 | 8.9
2023-05-18 09:29 |  | -21 | 9.6 | 7.9 | 8.5
2023-05-18 09:30 |  | -21 | 9.7 | 7.9 | 8.6
2023-05-18 09:31 | 10.7 | -25.7 | 14 | 9.9 | 10.6
2023-05-18 09:32 | 14.6 | -25.3 | 14.5 | 11.5 | 12
2023-05-18 09:33 | 13.8 | -26.1 | 14.7 | 11.5 | 12.2
2023-05-18 09:34 | 26.9 | -18.5 | 14.5 | 14.5 | 13.2
2023-05-18 09:35 | 35.8 | -17.4 | 14.7 | 19.6 | 15.4 |  | 0
2023-05-18 09:36 | 53.1 | -11.6 | 15.7 | 32.5 | 17.3 |  | 22
2023-05-18 09:37 | 75.8 | -14.1 | 16.8 | 73.1 | 18.8 |  | 1250 | 0
2023-05-18 09:38 | 97.4 | -14.7 | 18.1 | 142.9 | 21.5 |  | 3002 | -187
2023-05-18 09:39 | 120.9 | -10 | 20.7 | 229.2 | 24.3 |  | 3005 | 781
2023-05-18 09:40 | 144 | 8.3 | 26.6 | 256.5 | 27.2 | 0 | 3007 | 1102
2023-05-18 09:41 | 142.1 | 4 | 34.6 | 270.3 | 27.9 | 9.3 | 3007 | 1263
2023-05-18 09:42 | 139 | -6.6 | 38.5 | 324 | 30.3 | 21.9 | 3010 | 1477
2023-05-18 09:43 | 163 | 16.1 | 40.3 | 336.7 | 29.4 | 34 | 3009 | 1734
2023-05-18 09:44 | 160 | 6.4 | 40.2 | 391.5 | 29.7 | 43.7 | 3011 | 2208
2023-05-18 09:45 | 152.9 | 2.8 | 41 | 359.6 | 29.9 | 56 | 3009 | 2021
2023-05-18 09:46 | 150.3 | 2 | 40.3 | 347 | 30.5 | 61.1 | 3007 | 1898
2023-05-18 09:47 | 147.2 | 2.5 | 40.2 | 318.9 |  | 63.8 | 3005 | 1696
2023-05-18 09:48 | 144.1 | 2.7 | 39.9 | 295.1 | 30.5 | 63.9 | 3005 | 1412
2023-05-18 09:49 | 140.9 | 2 | 39.4 | 277.5 | 30.7 | 62.1 | 3004 | 1229
2023-05-18 09:50 | 139.9 | 1.4 | 39 | 273.2 | 31.2 | 59.7 | 3005 | 1183 |  | 855.9
2023-05-18 09:51 | 144.5 | 6.5 | 38.4 | 270.3 | 30.9 | 57.2 | 3006 | 1174 |  | 856
2023-05-18 09:52 | 142.2 | 3.4 | 38 | 275.2 | 32 | 53.8 | 3006 | 1252
2023-05-18 09:53 | 141.2 | 4.1 | 38.9 | 266.1 | 35.5 | 46.1 | 3005 | 1034
2023-05-18 09:54 | 140.4 | 3.4 | 42.5 | 264.7 | 37.2 | 45 | 3006 | 991
2023-05-18 09:55 | 142.3 | 5.2 | 44.9 | 268.4 | 36.8 | 45.7 | 3007 | 955
2023-05-18 09:56 | 140.3 | 4.7 | 46.1 | 254.8 | 39.6 | 43.4 | 3004 | 837 | 9427
2023-05-18 09:57 | 143.2 | 4.6 | 47.9 | 276.8 | 40.8 | 42.3 | 3006 | 933 | 9428
2023-05-18 09:58 | 145.1 | 4.7 | 49.5 | 288.2 | 42.8 | 41.9 | 3005 | 992
2023-05-18 09:59 | 153.3 | 11.2 | 51.6 | 299.4 | 42.7 | 44.1 | 3004 | 1003
2023-05-18 10:00 | 151.3 | 7 | 52.7 | 314.6 | 44.2 | 46.5 | 3005 | 1263
2023-05-18 10:01 | 155.1 | 7.6 | 53.6 | 343.4 | 42.7 | 51.2 | 3005 | 1421
2023-05-18 10:02 | 151.3 | 4.1 | 53.6 | 333.5 | 44.7 | 54.8 | 3004 | 1370
2023-05-18 10:03 | 151.9 | 4.6 | 54.1 | 340 | 44.3 | 56.8 | 3004 | 1378
2023-05-18 10:04 | 149.6 | 3.2 | 54.4 | 331.4 | 44.8 | 59.5 | 3003 | 1298
2023-05-18 10:05 | 148.4 | 3.6 | 54.5 | 321.1 | 44.4 | 59.8 |  | 1198
2023-05-18 10:06 | 149.3 | 0.8 | 54.1 | 346 | 45.7 | 59.4 | 3003 | 1378
2023-05-18 10:07 | 161.3 | 8.2 | 54.2 | 383.4 | 45.4 | 59.9 | 3006 | 1684
2023-05-18 10:08 | 169.9 | 12.9 | 54.6 | 405.5 | 46.4 | 63.2 | 3007 | 1987
2023-05-18 10:09 | 179.8 | 13.2 | 55.4 | 505.1 | 46.5 | 70.4 | 3009 | 2823
2023-05-18 10:10 | 169.1 | 6.3 | 55.9 | 469.1 | 45.1 | 80.1 | 3008 | 2508
2023-05-18 10:11 | 163.1 | 2.7 | 55 | 446.8 | 44.9 | 88.4 | 3007 | 2287
2023-05-18 10:12 | 160.3 | 2.3 | 54.4 | 430.6 | 44.5 | 88.9 |  | 2088
2023-05-18 10:13 | 158.7 | 1.7 | 54 | 417.2 | 44.8 | 89.2 |  | 1986
2023-05-18 10:14 | 155.9 | 2.5 | 53.8 | 388.2 | 44.1 | 86.8 |  | 1772
2023-05-18 10:15 | 155.4 | 1.8 | 53.2 | 388.5 | 44.4 | 84.6 |  | 1791
2023-05-18 10:16 | 157.8 | 4.7 | 52.8 | 384.3 | 45.3 | 79.5 | 3007 | 1780
2023-05-18 10:17 | 158.4 | 4.5 | 53.3 | 389.9 | 45.6 | 76.7 | 3006 | 1804 |  | 856
2023-05-18 10:18 | 162.8 | 8.9 | 53.6 | 389.4 | 45.9 | 75.8 | 3007 | 1846 |  | 856.1
2023-05-18 10:19 | 162.4 | 6.8 | 53.6 | 408.1 | 45.7 | 75.6 | 3008 | 1988
2023-05-18 10:20 | 163 | 7 | 53.7 | 407.9 | 46 | 74.5 | 3009 | 1971
2023-05-18 10:21 | 165.2 | 7.2 | 54 | 422.5 | 46.8 | 76.3 | 3009 | 2101
2023-05-18 10:22 | 166.8 | 6.1 | 54.6 | 450.6 | 47.7 | 77 | 3010 | 2303
2023-05-18 10:23 | 169.6 | 6.5 | 55.6 | 466.9 | 47.6 | 81.3 | 3011 | 2458
2023-05-18 10:24 | 174.8 | 9.2 | 55.6 | 493.7 | 47.4 | 85.2 | 3011 | 2685
2023-05-18 10:25 | 170.6 | 5.5 | 55.5 | 490.7 | 47.5 | 89.7 | 3010 | 2651
2023-05-18 10:26 | 167.8 | 4.4 | 55.5 | 474.1 | 47 | 94.9 | 3010 | 2516
2023-05-18 10:27 | 165.1 | 2 | 55.1 | 470.6 | 47 | 95.7 | 3011 | 2409
2023-05-18 10:28 | 166.8 | 4 | 55 | 465.1 | 47.1 | 95.8 |  | 2436 | 9428
2023-05-18 10:29 | 167 | 4 | 54.8 | 467.6 | 47.2 | 94.8 | 3011 | 2465 | 9429
2023-05-18 10:30 | 169.6 | 5.9 | 54.5 | 474.2 | 46.9 | 95.6 | 3013 | 2556
2023-05-18 10:31 | 170.2 | 5.9 | 54.2 | 480.7 | 47 | 94.3 | 3012 | 2594
2023-05-18 10:32 | 172.4 | 5.4 | 54.2 | 503.1 | 47.8 | 95.1 | 3013 | 2719
2023-05-18 10:33 | 186.1 | 15 | 54.8 | 535.3 | 48.2 | 95.9 | 3014 | 3108
2023-05-18 10:34 | 180.6 | 9.2 | 56 | 551.4 | 49 | 100 | 3014 | 3185
2023-05-18 10:35 | 176.1 | 4.4 | 56.2 | 555 | 48.5 | 107.6 | 3015 | 3118 |  | 856.1
2023-05-18 10:36 | 175.2 | 4.7 | 55.8 | 545.8 | 48 | 110.9 |  | 3049 |  | 856.2
2023-05-18 10:37 | 173.8 | 2.2 | 55.4 | 553.2 | 48 | 113 |  | 3069
2023-05-18 10:38 | 174.6 | 2.7 | 55.3 | 555.3 | 48.1 | 115.7 | 3015 | 3118
2023-05-18 10:39 | 177 | 4.3 | 55.1 | 564.4 | 48.1 | 115.7 | 3016 | 3195
2023-05-18 10:40 | 182.4 | 7.3 | 54.9 | 587.6 | 48.5 | 116.4 | 3017 | 3456
2023-05-18 10:41 | 184.3 | 8.2 | 55.1 | 604.4 | 48.3 | 117 | 3018 | 3594
2023-05-18 10:42 | 181.7 | 6.1 | 55.2 | 597.5 | 48 | 121.3 | 3017 | 3504
2023-05-18 10:43 | 179.6 | 4.5 | 54.9 | 590.6 | 47.9 | 124.4 |  | 3438
2023-05-18 10:44 | 179.5 | 2.8 | 54.8 | 607.2 | 48.2 | 124.6 |  | 3531
2023-05-18 10:45 | 182.7 | 6.1 | 54.9 | 606.8 | 48.4 | 125 |  | 3608
2023-05-18 10:46 | 182.2 | 5.8 | 55 | 605.5 | 48.1 | 126.3 | 3017 | 3562
2023-05-18 10:47 | 181.4 | 5.8 | 54.6 | 596.5 | 47.9 | 127.4 | 3016 | 3500 | 9429
2023-05-18 10:48 | 179.5 | 4 | 54.4 | 596.4 | 48 | 128.7 | 3015 | 3451 | 9430
2023-05-18 10:49 | 178.4 | 2.8 | 54.5 | 596.3 | 48 | 127.5 | 3016 | 3416 |  | 856.2
2023-05-18 10:50 | 179.4 | 2.9 | 54.7 | 606.9 | 48.4 | 126.6 | 3017 | 3507 |  | 856.3
2023-05-18 10:51 | 183.1 | 6.4 | 54.7 | 607.2 | 48.2 | 126.1 | 3018 | 3622
2023-05-18 10:52 | 182.8 | 6.6 | 54.4 | 603.6 | 47.8 | 129 | 3019 | 3569
2023-05-18 10:53 | 183.9 | 6.7 | 54.2 | 612.6 | 48.2 | 129.7 |  | 3669
2023-05-18 10:54 | 184.3 | 6.4 | 54.3 | 624.1 | 48.5 | 129.9 |  | 3703
2023-05-18 10:55 | 185.6 | 7.6 | 54.6 | 630.3 | 48.6 | 132.4 | 3019 | 3748
2023-05-18 10:56 | 181.2 | 5 | 55.1 | 606.5 | 48.3 | 133.8 | 3017 | 3507
2023-05-18 10:57 | 177.1 | 2.7 | 55 | 583.9 | 48 | 134.8 | 3016 | 3294
2023-05-18 10:58 | 176.2 | 2.3 | 54.7 | 576.7 | 48.2 | 131.5 |  | 3246
2023-05-18 10:59 | 176.1 | 2.5 | 54.9 | 575 | 49.1 | 128.2 |  | 3237
2023-05-18 11:00 | 178.4 | 4.2 | 55.3 | 580.8 | 49.3 | 126.1 | 3016 | 3309
2023-05-18 11:01 | 182.3 | 6.9 | 55.2 | 593.5 | 49.2 | 123.6 | 3014 | 3451
2023-05-18 11:02 | 183 | 6.7 | 55.3 | 604.5 | 50 | 123.5 | 3014 | 3527 |  | 856.3
2023-05-18 11:03 | 184.4 | 8.3 | 56.1 | 600.8 | 50.2 | 123.4 | 3013 | 3508 |  | 856.4
2023-05-18 11:04 | 179.3 | 4.6 | 56.3 | 587.5 | 50.3 | 123.9 | 3012 | 3317 | 9430
2023-05-18 11:05 | 179 | 3.6 | 56.5 | 594.8 | 50.5 | 124.3 | 3014 | 3352 | 9431
2023-05-18 11:06 | 182.7 | 6.8 | 56.4 | 599.2 | 50.8 | 124.5 |  | 3457
2023-05-18 11:07 | 183.3 | 7.4 | 56.6 | 599.4 | 50.6 | 124.6 | 3014 | 3440
2023-05-18 11:08 | 181.4 | 5.5 | 56.7 | 597.9 | 50.9 | 124.7 | 3015 | 3417
2023-05-18 11:09 | 179.8 | 3.6 | 56.7 | 607.9 | 50.8 | 123.7 |  | 3412
2023-05-18 11:10 | 180.3 | 3.9 | 57 | 606 | 51.2 | 125.8 |  | 3435
2023-05-18 11:11 | 178.2 | 2.5 | 57.3 | 602.2 | 50.8 | 125.5 |  | 3333
2023-05-18 11:12 | 181.3 | 4.6 | 56.7 | 602.9 | 50.5 | 126.9 | 3015 | 3489
2023-05-18 11:13 | 179.3 | 4 | 56.3 | 598.9 | 50.2 | 127.8 | 3014 | 3416
2023-05-18 11:14 | 179.9 | 3.7 | 55.7 | 603.3 | 49.7 | 128.8 | 3013 | 3441
2023-05-18 11:15 | 181.9 | 6 | 55.2 | 599.6 | 49.5 | 128.4 |  | 3468 |  | 856.4
2023-05-18 11:16 | 182.1 | 6.6 | 54.8 | 595.4 | 49.3 | 129.2 |  | 3454 |  | 856.5
2023-05-18 11:17 | 182.1 | 6.1 | 54.8 | 593.6 | 49.2 | 128.7 |  | 3463
2023-05-18 11:18 | 180.3 | 3.6 | 54.6 | 608.8 |  | 129.3 | 3013 | 3462
2023-05-18 11:19 | 185.4 | 7.7 | 54.6 | 614 | 49.2 | 129 | 3016 | 3610
2023-05-18 11:20 | 187.6 | 8.7 | 54.4 | 634.7 | 49.3 | 130.6 | 3017 | 3802
2023-05-18 11:21 | 188.3 | 8.1 | 54.8 | 651.3 | 49.9 | 134.3 | 3016 | 3904 | 9431
2023-05-18 11:22 | 185.4 | 5.6 | 55.5 | 646 | 49.6 | 138.6 |  | 3819 | 9432
2023-05-18 11:23 | 182.8 | 3.6 | 55.2 | 638.7 | 49.5 | 142.1 |  | 3717
2023-05-18 11:24 | 182.9 | 3.9 | 55 | 635.9 | 49.5 | 142.7 | 3016 | 3711
2023-05-18 11:25 | 182.9 | 4.6 | 54.9 | 627.9 | 49.3 | 143.9 | 3015 | 3673
2023-05-18 11:26 | 180.8 | 2.7 | 54.8 | 628 | 49 | 143.1 | 3016 | 3612
2023-05-18 11:27 | 181.7 | 3 | 54.6 | 632.5 | 49.3 | 142.4 | 3014 | 3675 |  | 856.5
2023-05-18 11:28 | 183.2 | 5.2 | 54.5 | 624 | 48.9 | 142.2 | 3015 | 3676 |  | 856.6
2023-05-18 11:29 | 181.3 | 3.8 | 54.2 | 619 |  | 142 | 3016 | 3602
2023-05-18 11:30 | 181.7 | 4.3 | 54.1 | 617.5 | 48.9 | 140.1 | 3015 | 3600
2023-05-18 11:31 | 181.1 | 4.5 | 54 | 609 | 48.7 | 138.5 | 3013 | 3529
2023-05-18 11:32 | 179.9 | 3.6 | 53.8 | 605.9 | 48.5 | 138.4 | 3014 | 3487
2023-05-18 11:33 | 178.9 | 3.3 | 53.8 | 596.7 | 48.3 | 136.7 | 3014 | 3411
2023-05-18 11:34 | 176.3 | 2.2 | 53.5 | 579.2 | 47.7 | 135.2 | 3013 | 3230
2023-05-18 11:35 | 175.5 | 1.7 | 53.2 | 576.1 | 47.5 | 134 | 3014 | 3229
2023-05-18 11:36 | 174.6 | 2.8 | 52.8 | 555.5 | 47.5 | 131 |  | 3091
2023-05-18 11:37 | 173.1 | 2.2 | 52.9 | 545.9 | 48 | 128.1 |  | 2994
2023-05-18 11:38 | 173.6 | 3 | 53 | 543.3 | 48.4 | 123.6 |  | 3003
2023-05-18 11:39 | 176.2 | 5.2 | 53.4 | 548.4 | 48.3 | 120.8 |  | 3032 | 9432
2023-05-18 11:40 | 176.5 | 6.5 | 53.4 | 537.1 | 48.8 | 117.5 |  | 3004 | 9433
2023-05-18 11:41 | 179 | 8.2 | 53.3 | 545 | 48.8 | 116.5 |  | 3057 |  | 856.6
2023-05-18 11:42 | 177.8 | 6.3 | 53.5 | 552.3 | 49 | 114.4 | 3014 | 3088 |  | 856.7
2023-05-18 11:43 | 178.5 | 5.8 | 53.9 | 563.8 | 49.4 | 114.2 | 3015 | 3153
2023-05-18 11:44 | 180.4 | 6.9 | 54.1 | 573.7 | 49.3 | 115.6 |  | 3270
2023-05-18 11:45 | 180.7 | 6.3 | 54.3 | 581.6 | 49.8 | 117.9 |  | 3310
2023-05-18 11:46 | 183.1 | 7.1 | 54.8 | 594.2 | 50 | 119.3 |  | 3425
2023-05-18 11:47 | 181.1 | 5.3 | 55.1 | 599.3 | 50.3 | 122.1 | 3015 | 3423
2023-05-18 11:48 | 180 | 5.2 | 55.4 | 590 | 50.3 | 124.2 | 3016 | 3320
2023-05-18 11:49 | 177.9 | 3.3 | 55.5 | 585.5 | 50 | 125.4 | 3015 | 3265
2023-05-18 11:50 | 178.7 | 4.7 | 54.9 | 579.1 | 49.8 | 125.2 | 3014 | 3252
2023-05-18 11:51 | 179 | 3.6 | 54.7 | 594.9 | 50.2 | 124 | 3015 | 3348
2023-05-18 11:52 | 182.6 | 6.7 | 54.7 | 598.7 | 50.1 | 124.3 | 3016 | 3453
2023-05-18 11:53 | 182.8 | 7.4 | 54.6 | 599.4 | 49.6 | 126.2 | 3016 | 3407
2023-05-18 11:54 | 183 | 7.1 | 54.4 | 598.6 | 49.7 | 127.5 | 3014 | 3446 |  | 856.7
2023-05-18 11:55 | 181.1 | 4.9 | 54.4 | 603.1 | 49.9 | 129.1 | 3016 | 3430 |  | 856.8
2023-05-18 11:56 | 182.4 | 5.1 | 54.5 | 612.6 | 50 | 129.8 | 3016 | 3503
2023-05-18 11:57 | 183.4 | 7 | 54.6 | 608.2 | 49.8 | 130.8 | 3015 | 3485 | 9433
2023-05-18 11:58 | 183.1 | 6.7 | 54.5 | 606.4 | 50 | 131.4 | 3016 | 3471 | 9434
2023-05-18 11:59 | 183.1 | 5.7 | 54.8 | 616.4 | 50.5 | 133 | 3016 | 3537
2023-05-18 12:00 | 185.3 | 8.6 | 55.1 | 608.3 | 50.5 | 132.9 | 3015 | 3489
2023-05-18 12:01 | 180.2 | 4.4 | 55.3 | 598.8 | 50.9 | 133.6 | 3013 | 3352
2023-05-18 12:02 | 180.7 | 4.7 | 55.5 | 598.1 | 50.8 | 132.5 | 3012 | 3382
2023-05-18 12:03 | 177.9 | 2.9 | 55.3 | 590 | 50.3 | 131.8 |  | 3239
2023-05-18 12:04 | 176.9 | 2.5 | 55.1 | 582 | 50.5 | 131.2 | 3012 | 3196
2023-05-18 12:05 | 173.2 | 2.5 | 55.1 | 545 | 49.5 | 129.8 | 3011 | 2861
2023-05-18 12:06 | 172.5 | 1.6 | 54.5 | 545.5 | 49.9 | 126.4 |  | 2905
2023-05-18 12:07 | 171.7 | 2.5 | 54.1 | 529 | 49.4 | 123.1 |  | 2801
2023-05-18 12:08 | 171.8 | 3.2 | 53.6 | 522.7 | 49.2 | 120.5 | 3011 | 2788 |  | 856.8
2023-05-18 12:09 | 171.7 | 4.5 | 52.9 | 509.8 | 48.5 | 116.5 | 3012 | 2726 |  | 856.9
2023-05-18 12:10 | 169.5 | 3.3 | 52.8 | 499.3 | 48.9 | 112.3 |  | 2611
2023-05-18 12:11 | 168.7 | 2.4 | 53 | 500.8 | 49 | 108.9 |  | 2569
2023-05-18 12:12 | 169.6 | 3.5 | 53.1 | 498.1 | 48.7 | 106.7 |  | 2581
2023-05-18 12:13 | 171 | 5.4 | 53.1 | 493.3 | 49.2 | 104.5 | 3012 | 2587
2023-05-18 12:14 | 169.7 | 4.9 | 53.2 | 486.7 | 49.2 | 102.6 | 3011 | 2522
2023-05-18 12:15 | 167.7 | 3.4 | 53.2 | 481.1 | 49 | 102.3 | 3010 | 2435
2023-05-18 12:16 | 167.9 | 2.9 | 53.1 | 488.3 | 49.4 | 100.7 | 3009 | 2494
2023-05-18 12:17 | 168.7 | 4.1 | 53.4 | 483.6 | 49.4 | 98.7 | 3010 | 2463
2023-05-18 12:18 | 167.6 | 3.5 | 53.5 | 480 | 49.5 | 98.3 | 3009 | 2424 | 9434
2023-05-18 12:19 | 166.5 | 2.6 | 53.6 | 478.2 | 49.5 | 96.9 | 3009 | 2378 | 9435
2023-05-18 12:20 | 166.4 | 3.6 | 53.7 | 467.4 | 49.4 | 96.5 | 3011 | 2298
2023-05-18 12:21 | 165.6 | 3.3 | 53.9 | 462.2 | 49.9 | 96 | 3011 | 2253
2023-05-18 12:22 | 170.2 | 6.9 | 53.7 | 470.5 |  | 94.9 | 3012 | 2403
2023-05-18 12:23 | 169.5 | 4.9 | 53.5 | 483.6 | 49.9 | 94.7 | 3010 | 2494
2023-05-18 12:24 | 167.5 | 3.4 | 53.6 | 480 | 49.5 | 95.4 | 3011 | 2406
2023-05-18 12:25 | 164.2 | 2 | 53.7 | 462.5 | 49.3 | 95.2 | 3011 | 2203 |  | 856.9
2023-05-18 12:26 | 162 | 2.2 | 53.7 | 443.6 | 48.9 | 95.8 | 3009 | 2042 |  | 857
2023-05-18 12:27 | 162.2 | 2 | 53.3 | 444.4 | 49 | 94.4 |  | 2073
2023-05-18 12:28 | 162.2 | 2.5 | 52.9 | 439.1 | 49.2 | 92.8 | 3009 | 2060
2023-05-18 12:29 | 162.6 | 4 | 52.8 | 430.2 | 49.7 | 88.9 | 3010 | 2016
2023-05-18 12:30 | 160.3 | 3.2 | 52.9 | 417.2 | 49.5 | 86.2 | 3008 | 1863
2023-05-18 12:31 | 161 | 4.2 | 52.9 | 414.4 | 49.9 | 84.5 | 3007 | 1875
2023-05-18 12:32 | 160.1 | 4.3 | 53 | 406.8 | 49.7 | 82.9 | 3007 | 1774
2023-05-18 12:33 | 157.5 | 3.8 |  | 390.3 | 49.5 | 80.9 | 3005 | 1629
2023-05-18 12:34 | 156.4 | 2.9 |  | 386.3 | 49.8 | 79.3 | 3007 | 1583
2023-05-18 12:35 | 154.2 | 3.4 | 53 | 365.9 | 49.5 | 77.5 | 3006 | 1423
2023-05-18 12:36 | 150.4 | 2.8 | 52.9 | 340.8 | 49.7 | 74.8 | 3004 | 1205
2023-05-18 12:37 | 146.7 | 2.2 | 52.8 | 317 | 49.9 | 71 | 3004 | 985
2023-05-18 12:38 | 145 | 2.4 |  | 303.9 | 50.2 | 67.3 | 3003 | 898
2023-05-18 12:39 | 146.3 | 4 |  | 299.9 | 50.7 | 62.8 | 3004 | 864
2023-05-18 12:40 | 146.6 | 4.4 | 52.8 | 299.3 | 51.1 | 58.8 | 3002 | 864
2023-05-18 12:41 | 149.1 | 5 | 53 | 314.4 | 51.4 | 56.8 | 3003 | 932
2023-05-18 12:42 | 156.4 | 9.4 | 53.2 | 336.6 | 51 | 55.5 | 3004 | 1053
2023-05-18 12:43 | 159.3 | 9 | 53.5 | 362 | 51.9 | 55 | 3004 | 1292
2023-05-18 12:44 | 159.3 | 7.1 | 54.3 | 374.7 | 52.3 | 59.6 | 3006 | 1443
2023-05-18 12:45 | 162.4 | 7.1 | 54.8 | 403 | 52 | 62.9 | 3008 | 1685
2023-05-18 12:46 | 163 | 6.6 | 55 | 411.4 | 51.4 | 67.5 | 3007 | 1774
2023-05-18 12:47 | 161.9 | 5.1 | 54.7 | 415.7 | 51.4 | 71.2 | 3009 | 1797
2023-05-18 12:48 | 161.6 | 4.5 | 54.7 | 417.6 | 51.6 | 74.1 | 3008 | 1804 |  | 857
2023-05-18 12:49 | 160.7 | 4.6 | 54.9 | 410.4 | 51.4 | 76.5 |  | 1745 |  | 857.1
2023-05-18 12:50 | 160.4 | 3 | 54.7 | 418.2 | 51.3 | 79.3 |  | 1824
2023-05-18 12:51 | 160.3 | 4.2 | 54.3 | 408.9 | 50.9 | 79 | 3008 | 1766
2023-05-18 12:52 | 156.4 | 3.2 | 54.1 | 385.2 | 50.5 | 79 | 3007 | 1535
2023-05-18 12:53 | 155.5 | 2.4 | 53.9 | 383 | 51 | 78.3 |  | 1508 | 9435
2023-05-18 12:54 | 158.2 | 4.8 | 53.6 | 385.6 | 50.7 | 77.4 |  | 1554 | 9436
2023-05-18 12:55 | 162.1 | 9.6 | 53.3 | 376.1 | 51.1 | 76.3 | 3007 | 1574
2023-05-18 12:56 | 161.6 | 5.4 | 53 | 409.9 | 51 | 74.8 | 3008 | 1777
2023-05-18 12:57 | 164.8 | 7.2 | 53.1 | 422.6 | 50.9 | 74.7 | 3009 | 1834
2023-05-18 12:58 | 164.4 | 6.5 | 53.5 | 423.6 | 51.4 | 75.5 | 3009 | 1887
2023-05-18 12:59 | 164.9 | 5.7 | 54 | 435.9 | 51.9 | 77.4 | 3008 | 1962
2023-05-18 13:00 | 167.7 | 6.5 | 54.5 | 453.1 | 52.4 | 78.7 | 3009 | 2108
2023-05-18 13:01 | 170.1 | 6.8 | 55.1 | 471.5 | 52.8 | 82.1 | 3009 | 2260
2023-05-18 13:02 | 172.5 | 6.6 | 55.5 | 496.8 | 53.1 | 85.5 | 3011 | 2473
2023-05-18 13:03 | 174.6 | 7.4 | 55.8 | 509.5 | 52.9 | 91 | 3012 | 2601
2023-05-18 13:04 | 176.1 | 7.5 |  | 522.3 | 53.3 | 94.9 | 3010 | 2744
2023-05-18 13:05 | 178.7 | 7.6 | 55.8 | 547.5 | 53.4 | 100.1 | 3013 | 2949
2023-05-18 13:06 | 177.3 | 5.7 | 56 | 553.1 | 53.5 | 105 |  | 2973
2023-05-18 13:07 | 175.7 | 4.3 | 55.9 | 551.4 | 53.4 | 108.1 | 3013 | 2929 |  | 857.1
2023-05-18 13:08 | 175.1 | 3.8 | 55.7 | 550.7 | 53.1 | 110.7 | 3012 | 2902 |  | 857.2
2023-05-18 13:09 | 172.1 | 3.9 | 55.4 | 521.9 | 52.4 | 112.3 | 3011 | 2678
2023-05-18 13:10 | 169.8 | 1.3 | 55.1 | 521.5 | 52.5 | 112.1 | 3010 | 2621
2023-05-18 13:11 | 170.8 | 2 | 54.7 | 525.3 | 52.5 | 112 | 3010 | 2674
2023-05-18 13:12 | 172.8 | 5 | 54.4 | 515.3 | 52.1 | 109.5 | 3011 | 2681
2023-05-18 13:13 | 170.5 | 3.6 | 54.1 | 505.5 | 52 | 107.6 | 3011 | 2575
2023-05-18 13:14 | 170.6 | 3 | 53.8 | 511.9 | 52 | 106.6 | 3009 | 2622
2023-05-18 13:15 | 173.4 | 6.3 | 53.5 | 506.5 | 51.8 | 106.1 | 3010 | 2640
2023-05-18 13:16 | 172.4 | 5.5 | 53.3 | 506.9 | 51.7 | 106.1 | 3011 | 2599
2023-05-18 13:17 | 173.8 | 7.2 | 53.2 | 503.6 | 51.7 | 105 | 3010 | 2634
2023-05-18 13:18 | 174.8 | 7.3 | 53.1 | 507.5 | 51.8 | 105.8 | 3011 | 2678 | 9436
2023-05-18 13:19 | 170.8 | 4.9 | 53.1 | 496.5 | 51.3 | 104.4 | 3011 | 2520 | 9437
2023-05-18 13:20 | 169.1 | 4.5 | 53 | 484.2 | 51.1 | 104.2 | 3010 | 2425
2023-05-18 13:21 | 169 | 3.2 | 52.7 | 495.5 | 51.3 | 103.2 | 3012 | 2490
2023-05-18 13:22 | 172.6 | 5 | 52.7 | 512.1 | 52 | 101.1 | 3010 | 2674
2023-05-18 13:23 | 175.4 | 7.4 | 53.3 | 519 | 51.8 | 102 | 3011 | 2697 |  | 857.2
2023-05-18 13:24 | 174.3 | 7 | 53.7 | 510.7 | 52.3 | 103.2 |  | 2647 |  | 857.3
2023-05-18 13:25 | 172.8 | 5.5 | 53.9 | 508.2 | 52.5 | 103.8 | 3011 | 2637
2023-05-18 13:26 | 169.8 | 3.1 | 54 | 504.8 | 51.9 | 104 | 3009 | 2532
2023-05-18 13:27 | 169.1 | 2.4 | 54 | 503 | 52.4 | 104.1 | 3011 | 2514
2023-05-18 13:28 | 167.5 | 2.8 | 54.1 | 485.2 | 52.1 | 103.4 | 3009 | 2357
2023-05-18 13:29 | 166.4 | 2.4 | 53.8 | 478.3 | 52 | 103.9 | 3010 | 2315
2023-05-18 13:30 | 168.9 | 5 | 53.3 | 475.9 | 51.9 | 101.2 | 3010 | 2354
2023-05-18 13:31 | 166.9 | 4.4 | 53 | 465.4 | 51.5 | 99.9 | 3009 | 2251
2023-05-18 13:32 | 166 | 3.6 | 52.8 | 463.8 | 51.5 | 98.2 | 3009 | 2237
2023-05-18 13:33 | 167 | 2.3 | 52.7 | 483.8 | 52.5 | 96 | 3010 | 2365
2023-05-18 13:34 | 175 | 7.2 | 53.2 | 514.4 | 52.4 | 95.4 | 3012 | 2644
2023-05-18 13:35 | 177.2 | 9 | 53.4 | 519.3 | 51.7 | 97.6 |  | 2749
2023-05-18 13:36 | 172.1 | 6.6 | 53.3 | 493 | 51.5 | 101.2 |  | 2561
2023-05-18 13:37 | 168 | 0 | 53 | 517.8 | 51.6 | 102.3 |  | 2560
2023-05-18 13:38 | 173 | 4.4 | 52.8 | 522.9 | 51.8 | 103.7 | 3012 | 2757
2023-05-18 13:39 | 171.1 | 3.5 | 52.9 | 514.7 | 51.9 | 103.8 | 3011 | 2668
2023-05-18 13:40 | 172 | 5.5 | 53 | 503.9 | 51.8 | 104.1 | 3011 | 2577 |  | 857.3
2023-05-18 13:41 | 172.9 | 6.1 | 52.8 | 504.6 | 51.9 | 104.2 | 3012 | 2607 |  | 857.4
2023-05-18 13:42 | 173.2 | 5.8 | 52.8 | 511 | 52.2 | 103.5 | 3011 | 2637 | 9437
2023-05-18 13:43 | 175.6 | 9.2 | 52.9 | 499.8 | 51.9 | 102.7 | 3012 | 2611 | 9438
2023-05-18 13:44 | 172.2 | 5.3 | 52.8 | 506.1 | 52.7 | 102.7 |  | 2615
2023-05-18 13:45 | 175.5 | 7 | 53 | 521.9 | 52.4 | 103.7 |  | 2748
2023-05-18 13:46 | 173.8 | 5.2 | 53.3 | 522.1 | 52.4 | 105.1 |  | 2719
2023-05-18 13:47 | 172.6 | 4.2 | 53.3 | 521.9 | 52.3 | 105 | 3012 | 2703
2023-05-18 13:48 | 172.3 | 4.2 | 52.7 | 517.5 | 50.5 | 108.5 | 3013 | 2727
2023-05-18 13:49 | 170.9 | 2.9 | 50.9 | 516.8 | 50 | 110.6 |  | 2691
2023-05-18 13:50 | 172.3 | 4.2 | 50.5 | 517.4 | 49.9 | 110.4 |  | 2755
2023-05-18 13:51 | 170.8 | 3.8 | 50.4 | 506.7 | 49.8 | 109.7 |  | 2666
2023-05-18 13:52 | 171.9 | 4 | 50.2 | 513.1 | 50.1 | 109.1 | 3013 | 2725
2023-05-18 13:53 | 175.6 | 6.5 | 50 | 526 | 49.8 | 110.1 | 3014 | 2865
2023-05-18 13:54 | 174.7 | 6.5 | 49.7 | 520.4 | 49.2 | 109.6 | 3013 | 2815
2023-05-18 13:55 | 171.5 | 4.3 | 49.4 | 510.3 | 49 | 111.4 | 3012 | 2690
2023-05-18 13:56 | 172.2 | 4.6 | 49.2 | 512.5 | 49.5 | 110.8 | 3013 | 2736 |  | 857.4
2023-05-18 13:57 | 173.8 | 6.3 | 49.2 | 514.2 | 49.3 | 110 | 3013 | 2743 |  | 857.5
2023-05-18 13:58 | 175.5 | 8.4 | 49.1 | 508.6 | 49.2 | 110.3 | 3012 | 2749
2023-05-18 13:59 | 172.2 | 4.8 | 48.9 | 511 | 49 | 111 |  | 2726
2023-05-18 14:00 | 171.3 | 4.3 | 48.8 | 507.3 | 48.7 | 111 |  | 2682
2023-05-18 14:01 | 169.3 | 1.5 | 49.2 | 514.2 | 49.7 | 109.7 | 3012 | 2664
2023-05-18 14:02 | 169.2 | 3.1 | 49.8 | 498.8 | 49.2 | 109.3 | 3010 | 2574
2023-05-18 14:03 | 170.2 | 4.2 | 49.6 | 497.5 | 49.5 | 108.5 | 3011 | 2606
2023-05-18 14:04 | 171.6 | 6.1 | 49.3 | 493 | 49.3 | 106.8 | 3009 | 2607 | 9438
2023-05-18 14:05 | 167.5 | 3.5 | 49.2 | 479.4 | 48.9 | 106.7 | 3009 | 2420 | 9439
2023-05-18 14:06 | 168.7 | 2.9 | 49.1 | 495.7 | 49.7 | 107.2 | 3010 | 2566
2023-05-18 14:07 | 170.2 | 4.5 | 49 | 494.4 | 48.9 | 105.5 | 3009 | 2561
2023-05-18 14:08 | 169.5 | 3.7 | 48.8 | 494.3 | 49.4 | 106 | 3010 | 2578
2023-05-18 14:09 | 170 | 4.9 | 49.1 | 489.1 | 49.5 | 105.5 | 3010 | 2540
2023-05-18 14:10 | 169.4 | 4.4 | 49.2 | 487.9 | 49.4 | 104.3 | 3009 | 2509
2023-05-18 14:11 | 169.2 | 3.4 | 49.4 | 495.8 | 49.8 | 103.6 | 3010 | 2552 |  | 857.5
2023-05-18 14:12 | 169.3 | 4.2 | 49.7 | 489.2 | 50 | 103.2 | 3011 | 2493 |  | 857.6
2023-05-18 14:13 | 168.9 | 2.2 | 49.9 | 504.2 | 50.3 | 102.7 | 3012 | 2568
2023-05-18 14:14 | 174.2 | 6.7 | 50 | 512 | 50 | 102.6 | 3011 | 2715
2023-05-18 14:15 | 170.7 | 4.4 | 50 | 500.8 | 50.1 | 104.2 | 3011 | 2588
2023-05-18 14:16 | 167.7 | 2.4 | 50.3 | 490.7 | 50 | 104.8 | 3010 | 2468
2023-05-18 14:17 | 166.1 | 3 | 50.3 | 470 | 50 | 103.6 | 3009 | 2305
2023-05-18 14:18 | 163.9 | 2.8 | 50.1 | 452.6 | 49.8 | 102.9 | 3008 | 2143
2023-05-18 14:19 | 160.9 | 2 | 49.7 | 432.6 | 49.5 | 100.1 |  | 1948
2023-05-18 14:20 | 161.3 | 2.7 | 49 | 429.2 | 49.8 | 97.5 |  | 1983
2023-05-18 14:21 | 161.6 | 3.4 | 48.5 | 425.9 | 49.3 | 93.8 | 3008 | 1964
2023-05-18 14:22 | 160.8 | 4.4 | 48 | 411.2 | 49.3 | 90.3 | 3007 | 1859
2023-05-18 14:23 | 158.5 | 3.4 | 47.9 | 399.6 | 49.7 | 87.2 | 3005 | 1742
2023-05-18 14:24 | 158.7 | 3.7 | 48 | 399.5 | 49.8 | 84.3 | 3006 | 1720
2023-05-18 14:25 | 160.9 | 5.9 | 48.1 | 400.7 | 49.4 | 81.6 | 3007 | 1729
2023-05-18 14:26 | 158.3 | 2.8 | 48.2 | 403.7 | 49.5 | 80.2 | 3006 | 1739
2023-05-18 14:27 | 159.3 | 3.2 | 48.3 | 407.6 | 49.7 | 79.1 | 3007 | 1785
2023-05-18 14:28 | 159.3 | 4.3 | 48.4 | 399.6 | 49.4 | 79.7 |  | 1738
2023-05-18 14:29 | 156.5 | 2.9 | 48.4 | 388.3 | 49.2 | 78.3 | 3007 | 1602
2023-05-18 14:30 | 155.5 | 1.8 | 48.3 | 388.3 | 49.7 | 77.3 | 3006 | 1591
2023-05-18 14:31 | 155.4 | 2.9 | 48.4 | 379.7 | 49.5 | 76.9 | 3007 | 1527 |  | 857.6
2023-05-18 14:32 | 155.2 | 3.8 | 48.3 | 370.2 | 49.7 | 75.1 | 3006 | 1452 |  | 857.7
2023-05-18 14:33 | 154.5 | 4.4 | 48.3 | 359.5 | 49.7 | 73.9 | 3005 | 1374 | 9439
2023-05-18 14:34 | 154.5 | 4.6 | 48.2 | 358.1 | 50.1 | 72.4 |  | 1376 | 9440
2023-05-18 14:35 | 156.1 | 4.2 | 48.1 | 371.8 | 50.4 | 70.6 |  | 1489
2023-05-18 14:36 | 161.9 | 9.8 | 48.3 | 376.2 | 50.1 | 69.5 | 3005 | 1490
2023-05-18 14:37 | 159.6 | 6.8 | 48.5 | 381.5 | 50.5 | 69.7 | 3006 | 1563
2023-05-18 14:38 | 157.7 | 5.2 | 48.8 | 381.5 | 50.3 | 70.3 | 3006 | 1545
2023-05-18 14:39 | 155.4 | 3.7 | 49.2 | 373.5 | 50.6 | 71.5 | 3007 | 1457
2023-05-18 14:40 | 155.6 | 4.1 | 49.3 | 371 |  | 71.5 | 3006 | 1452
2023-05-18 14:41 | 155.4 | 3.7 | 49.3 | 372.3 | 50.6 | 71.2 | 3005 | 1457
2023-05-18 14:42 | 156 | 3.9 | 49.2 | 375.9 | 50.8 | 71.7 | 3006 | 1492
2023-05-18 14:43 | 156.2 | 4.4 | 49.3 | 373.8 |  | 71.7 | 3005 | 1472
2023-05-18 14:44 | 155 | 3.5 |  | 372.7 | 50.8 | 71.6 | 3005 | 1443
2023-05-18 14:45 | 155.5 | 3.9 | 49.3 | 371.1 | 50.7 | 71.9 | 3006 | 1451
2023-05-18 14:46 | 155.4 | 3.6 | 49.1 | 373.9 | 50.8 | 71.6 | 3006 | 1455
2023-05-18 14:47 | 155.7 | 4.4 | 49.1 | 369.5 | 50.6 | 73 | 3005 | 1443
2023-05-18 14:48 | 153.6 | 3 | 49 | 364.5 | 50.5 | 72 | 3006 | 1367
2023-05-18 14:49 | 154.7 | 3.3 | 48.9 | 367.9 | 51.1 | 71.5 |  | 1413
2023-05-18 14:50 | 156.5 | 4.3 | 49 | 375.8 | 51.5 | 70.7 | 3006 | 1493
2023-05-18 14:51 | 160.3 | 6.3 | 49.1 | 392.1 | 50.9 | 71.2 | 3007 | 1615
2023-05-18 14:52 | 158.8 | 5.1 | 49.2 | 388.4 | 51.1 | 71.3 | 3006 | 1591
2023-05-18 14:53 | 157.8 | 4.1 | 49.5 | 389 | 51.3 | 72.1 | 3007 | 1583
2023-05-18 14:54 | 156.4 | 3.3 | 49.7 | 385.1 | 51.2 | 72.7 | 3006 | 1509 |  | 857.7
2023-05-18 14:55 | 156.2 | 2.1 | 49.7 | 392.5 | 51.6 | 74.1 | 3007 | 1538 |  | 857.8
2023-05-18 14:56 | 158.7 | 4.3 | 49.8 | 395 | 51.7 | 73.6 | 3007 | 1589
2023-05-18 14:57 | 161.1 | 6.4 | 50 | 397.6 | 52 | 74 | 3006 | 1638
2023-05-18 14:58 | 161.3 | 5.9 | 50.1 | 402.5 | 52.2 | 74.8 | 3005 | 1695
2023-05-18 14:59 | 161.7 | 6.9 | 50.4 | 397.5 |  | 75.8 | 3007 | 1657
2023-05-18 15:00 | 159.7 | 4.3 | 50.4 | 402.7 | 52.2 | 76.2 |  | 1677
2023-05-18 15:01 | 160.1 | 5.8 | 50.3 | 394.4 | 51.9 | 77.7 | 3007 | 1621
2023-05-18 15:02 | 158.5 | 4.3 | 50 | 393.5 | 51.7 | 77.7 | 3006 | 1595
2023-05-18 15:03 | 157.3 | 3.6 | 49.8 | 388.7 | 51.5 | 77.4 | 3007 | 1552
2023-05-18 15:04 | 156.1 | 3.1 | 49.6 | 383 | 51.4 | 76.9 | 3005 | 1509
2023-05-18 15:05 | 155.9 | 3.4 | 49.4 | 379.2 | 51.3 | 76.4 | 3006 | 1488
2023-05-18 15:06 | 155.7 | 3.5 | 49.2 | 375.2 | 51.6 | 75.6 | 3006 | 1464
2023-05-18 15:07 | 156.4 | 4.3 | 48.9 | 375.8 | 51.2 | 75.1 | 3007 | 1457
2023-05-18 15:08 | 156.3 | 3.8 | 48.6 | 379.6 | 51.4 | 73.2 | 3006 | 1471
2023-05-18 15:09 | 158.2 | 8.3 | 48.4 | 358.8 | 50.8 | 73.4 | 3006 | 1324
2023-05-18 15:10 | 154.7 | 5.6 | 48 | 348.9 | 51.3 | 72 | 3005 | 1280
2023-05-18 15:11 | 152.9 | 3.5 | 47.8 | 356.4 | 50.8 | 69.8 |  | 1265
2023-05-18 15:12 | 154.4 | 4.8 | 48.1 | 356.1 | 51.5 | 69.5 | 3005 | 1311
2023-05-18 15:13 | 151.5 | 3.3 | 48.4 | 345.4 | 50.9 | 69.7 | 3006 | 1217 | 9440
2023-05-18 15:14 | 150.5 | 2.7 | 48.3 | 342.5 | 51.4 | 69.2 | 3006 | 1190 | 9441
2023-05-18 15:15 | 150 | 2.3 | 48 | 341.5 | 51.5 | 67.9 | 3004 | 1159
2023-05-18 15:16 | 151.6 | 4.1 | 47.9 | 339.3 |  | 66.1 | 3005 | 1139
2023-05-18 15:17 | 150.9 | 5.1 | 48 | 326.7 | 51.5 | 64.4 | 3004 | 1034
2023-05-18 15:18 | 151 | 4.3 | 48 | 333.6 | 52 | 63 | 3003 | 1089 |  | 857.8
2023-05-18 15:19 | 154.6 | 8.8 | 48.1 | 327 | 51.8 | 61.5 | 3004 | 1053 |  | 857.9
2023-05-18 15:20 | 151.4 | 5.9 | 48.2 | 323.9 | 52.7 | 61 | 3003 | 1056
2023-05-18 15:21 | 149.9 | 3.8 | 48.5 | 332.5 | 51.8 | 61.2 |  | 1064
2023-05-18 15:22 | 148 | 1.9 | 48.8 | 327.5 | 52.4 | 61.9 |  | 1027
2023-05-18 15:23 | 146.6 | 2.9 | 49.1 | 311.7 | 52.2 | 62.4 | 3003 | 925
2023-05-18 15:24 | 143.9 | 2.4 | 49 | 295 | 51.9 | 61.8 | 3002 | 797
2023-05-18 15:25 | 144.5 | 3.3 | 48.4 | 291.6 | 52.3 | 60.4 |  | 765
2023-05-18 15:26 | 146.5 | 4.6 | 48.1 | 296.7 | 52.8 | 56.8 |  | 805
2023-05-18 15:27 | 149 | 8.2 | 48.2 | 289.6 | 52.8 | 55.3 |  | 740
2023-05-18 15:28 | 147.1 | 5.9 | 48.4 | 292.7 | 53.4 | 53.9 |  | 794
2023-05-18 15:29 | 147.7 | 5.3 | 48.6 | 304.7 | 52.6 | 53.5 |  | 850
2023-05-18 15:30 | 148.1 | 6.5 | 48.7 | 294 | 53.7 | 53.4 | 3002 | 805
2023-05-18 15:31 | 153.5 | 8.7 | 48.8 | 320 | 52.8 | 53.8 | 3003 | 949
2023-05-18 15:32 | 149.9 | 5.8 | 48.7 | 313.5 | 53.3 | 54.2 | 3003 | 923
2023-05-18 15:33 | 148.4 | 4.3 | 49.1 | 314.7 | 53.5 | 54.6 | 3004 | 937
2023-05-18 15:34 | 149.2 | 4.7 | 49.5 | 317.3 | 54.1 | 55.7 |  | 953
2023-05-18 15:35 | 151.4 | 7.9 | 49.9 | 310 | 53.4 | 56.3 | 3004 | 893
2023-05-18 15:36 | 149.4 | 6.5 | 49.9 | 305.4 | 54.1 | 56.2 | 3003 | 888
2023-05-18 15:37 | 149 | 3.9 | 50 | 323.3 | 53.8 | 56.5 | 3003 | 987
2023-05-18 15:38 | 148.8 | 3.3 | 50.1 | 324.6 | 54.3 | 56.9 | 3002 | 1022
2023-05-18 15:39 | 148.3 | 3.5 | 50.4 | 318.8 | 54.1 | 58.1 | 3002 | 985
2023-05-18 15:40 | 146.3 | 2.1 | 50.5 | 315.2 | 54.1 | 58.2 | 3003 | 923
2023-05-18 15:41 | 147.8 | 3.2 | 50.4 | 316.1 | 53.9 | 59 | 3003 | 943
2023-05-18 15:42 | 150.5 | 5.3 | 49.8 | 320.9 | 53.4 | 60.6 | 3002 | 1018
2023-05-18 15:43 | 150.1 | 3.8 | 49 | 331.4 | 52.3 | 61.7 | 3004 | 1078
2023-05-18 15:44 | 149.1 | 2.2 | 48.4 | 335.5 | 52.5 | 61.6 |  | 1124
2023-05-18 15:45 | 150.5 | 3.6 | 48.1 | 335.3 |  | 62.6 | 3004 | 1139
2023-05-18 15:46 | 152.8 | 4.4 | 47.7 | 345 | 52.5 | 62.8 | 3005 | 1221 |  | 857.9
2023-05-18 15:47 | 159.6 | 10.9 | 47.2 | 350.7 | 51.2 | 63.1 | 3006 | 1247 |  | 858
2023-05-18 15:48 | 153.2 | 5.7 | 47 | 339.5 | 52 | 63.1 | 3004 | 1198
2023-05-18 15:49 | 149.6 | 4 | 47.3 | 325.7 | 51.7 | 63.5 |  | 1098
2023-05-18 15:50 | 146.5 | 2.5 | 47.3 | 313.4 | 51.5 | 63.8 |  | 993
2023-05-18 15:51 | 144.6 | 2.2 | 47 | 300.9 | 51.5 | 63.5 |  | 892
2023-05-18 15:52 | 143.1 | 2.4 | 46.5 | 289.1 | 51.4 | 62.4 |  | 803
2023-05-18 15:53 | 142.6 | 3.4 | 46 | 278.5 | 51.1 | 60.1 |  | 735
2023-05-18 15:54 | 142.6 | 4.4 | 45.5 | 270.3 | 51.6 | 57.2 | 3004 | 692
2023-05-18 15:55 | 141.8 | 3.7 | 45.3 | 270.9 | 51.6 | 54.1 | 3003 | 680
2023-05-18 15:56 | 140.8 | 3.6 | 45.3 | 266 | 51.8 | 51.6 | 3003 | 635
2023-05-18 15:57 | 141.1 | 4 | 45.4 | 265.6 | 52 | 50.6 | 3004 | 632
2023-05-18 15:58 | 142.3 | 4.9 | 45.4 | 267.6 | 52 | 48.9 | 3004 | 639
2023-05-18 15:59 | 143.4 | 6.5 | 45.5 | 264.8 | 52.2 | 47.7 | 3003 | 615
2023-05-18 16:00 | 142.2 | 5.5 | 45.7 | 263.6 | 52.2 | 48 | 3004 | 616
2023-05-18 16:01 | 141.2 | 5.4 | 45.8 | 259.1 | 51.6 | 48.6 | 3003 | 584
2023-05-18 16:02 | 138.9 | 3.2 | 45.5 | 256.9 | 51.4 | 49 | 3002 | 576
2023-05-18 16:03 | 139 | 2.8 | 45 | 259.6 | 51.4 | 48.7 | 3003 | 591
2023-05-18 16:04 | 140.8 | 4.2 | 44.8 | 262.3 | 51.8 | 48.2 |  | 625
2023-05-18 16:05 | 145.2 | 6.4 | 44.6 | 275.3 | 50.8 | 47.8 | 3003 | 690
2023-05-18 16:06 | 142.1 | 2.1 | 44.6 | 284.1 | 51.3 | 47.5 | 3002 | 755
2023-05-18 16:07 | 143.1 | 4.3 | 44.8 | 276.7 | 50.9 | 48.2 | 3001 | 710
2023-05-18 16:08 | 141 | 2.4 | 45 | 273.4 | 51.9 | 49.3 | 3002 | 682
2023-05-18 16:09 | 145.1 | 6.3 | 45.1 | 275.3 | 51.3 | 49.6 | 3001 | 702
2023-05-18 16:10 | 143.6 | 3.2 | 44.9 | 286.5 | 51.1 | 49.8 | 3002 | 792
2023-05-18 16:11 | 144.3 | 4.5 | 44.7 | 282.3 | 50.5 | 51.7 | 3001 | 776
2023-05-18 16:12 | 142.9 | 3.2 | 44.3 | 281.5 | 50.1 | 52.4 | 3001 | 779
2023-05-18 16:13 | 141.3 | 2.6 | 43.8 | 275.4 | 49.5 | 53 | 3002 | 743
2023-05-18 16:14 | 140.8 | 2 | 43.2 | 274.9 | 50.2 | 53.1 |  | 747
2023-05-18 16:15 | 144.1 | 4.9 | 42.9 | 278.5 | 49.5 | 52.9 | 3002 | 763
2023-05-18 16:16 | 143.9 | 4.8 | 42.5 | 276.9 | 49.8 | 52 | 3004 | 764
2023-05-18 16:17 | 146 | 7.1 | 42.3 | 276.4 | 49.7 | 51.9 | 3005 | 764
2023-05-18 16:18 | 147.8 | 7.3 | 42.1 | 287.9 | 49.4 | 52 | 3005 | 832
2023-05-18 16:19 | 146.5 | 6.2 | 41.9 | 285.9 | 49.4 | 51.3 | 3004 | 834 |  | 858
2023-05-18 16:20 | 144.2 | 4.3 | 42 | 283 | 49.7 | 51.5 | 3003 | 824 |  | 858.1
2023-05-18 16:21 | 144.4 | 4 | 42.1 | 286.7 |  | 51.9 | 3004 | 833
2023-05-18 16:22 | 145.3 | 5.3 | 42 | 283.9 | 49.7 | 52.5 | 3004 | 811 | 9441
2023-05-18 16:23 | 144.8 | 4.6 |  | 285.2 | 49.8 | 51.9 | 3003 | 823 | 9442
2023-05-18 16:24 | 146.3 | 5.4 | 42 | 290.6 | 50 | 52.3 | 3002 | 863
2023-05-18 16:25 | 149.8 | 8.6 | 42.1 | 292.5 | 49.8 | 52.9 | 3002 | 873
2023-05-18 16:26 | 148.2 | 5.2 | 42.2 | 305.6 | 50.4 | 53.1 | 3003 | 978
2023-05-18 16:27 | 151.2 | 7.3 | 42.4 | 312.5 | 49 | 53.6 |  | 1000
2023-05-18 16:28 | 146.9 | 4 | 42.5 | 305 | 50.2 | 55 | 3003 | 982
2023-05-18 16:29 | 150.4 | 8.4 | 42.5 | 298.1 | 49.8 | 56.3 | 3002 | 915
2023-05-18 16:30 | 147.1 | 4.5 | 42.1 | 303.1 | 49.9 | 56.6 | 3003 | 951
2023-05-18 16:31 | 147.9 | 6.3 | 42 | 295.8 | 49.5 | 56.5 | 3004 | 895
2023-05-18 16:32 | 145.2 | 3.2 | 41.9 | 298.3 | 49.5 | 56.2 |  | 914
2023-05-18 16:33 | 143.8 | 2.7 | 41.8 | 292.1 | 49.3 | 56.6 |  | 875
2023-05-18 16:34 | 142.8 | 1.9 | 41.7 | 290.3 | 49.7 | 56.2 | 3004 | 856
2023-05-18 16:35 | 142.9 | 3.2 | 41.6 | 282 | 49.4 | 56 | 3002 | 783
2023-05-18 16:36 | 142.6 | 4.5 | 41.4 | 270.3 | 50 | 55.3 | 3003 | 725
2023-05-18 16:37 | 142.2 | 3.5 | 41.1 | 274.9 | 49.6 | 54.2 | 3003 | 741
2023-05-18 16:38 | 142 | 3.9 | 40.9 | 270.8 | 49.6 | 53.2 | 3002 | 713
2023-05-18 16:39 | 142.6 | 5.6 | 40.7 | 265.1 | 49.5 | 52.1 | 3001 | 682
2023-05-18 16:40 | 141.4 | 2.8 | 40.6 | 274 | 49.7 | 51.4 | 3002 | 737
2023-05-18 16:41 | 145.1 | 7.5 | 40.4 | 269.3 | 49.7 | 51 | 3002 | 715
2023-05-18 16:42 | 145 | 5.6 | 40.2 | 280 | 49.6 | 50.6 | 3003 | 779
2023-05-18 16:43 | 145.6 | 6.7 | 40.2 | 276.2 | 49.4 | 50.6 |  | 748
2023-05-18 16:44 | 143.2 | 2.2 | 40.3 | 291.5 | 49.9 | 50 |  | 853
2023-05-18 16:45 | 145.3 | 4.8 | 40.6 | 287.9 | 49.6 | 51.1 | 3003 | 831
2023-05-18 16:46 | 142.5 | 2.9 | 40.9 | 281.1 | 49.8 | 52.1 | 3002 | 786
2023-05-18 16:47 | 142.5 | 2.4 | 41 | 285.1 | 50.2 | 52.1 | 3004 | 797
2023-05-18 16:48 | 145.6 | 4.8 | 41 | 289.7 | 50.2 | 52.3 |  | 820
2023-05-18 16:49 | 147.4 | 6.6 | 41.1 | 290 | 50.5 | 52.6 | 3004 | 833
2023-05-18 16:50 | 149.1 | 6.7 | 41.3 | 301.3 | 50.8 | 52.5 | 3003 | 910 |  | 858.1
2023-05-18 16:51 | 153.7 | 10.3 | 41.5 | 308.8 | 49.6 | 52.9 | 3004 | 946 |  | 858.2
2023-05-18 16:52 | 145.5 | 3.9 | 41.7 | 295.4 | 50.6 | 53.5 | 3003 | 895
2023-05-18 16:53 | 144.5 | 2.5 | 42.1 | 298.3 | 51 | 55.3 | 3002 | 880
2023-05-18 16:54 | 146.2 | 4 | 42.4 | 300.1 | 51.5 | 55 | 3003 | 892
2023-05-18 16:55 | 146.3 | 4.4 | 42.6 | 297.6 | 51 | 55.3 | 3004 | 875
2023-05-18 16:56 | 144.1 | 2.6 |  | 294.9 | 51.1 | 55.2 | 3004 | 842
2023-05-18 16:57 | 143.8 | 2 | 42.6 | 296.9 | 51.1 | 56 | 3003 | 847
2023-05-18 16:58 | 145.7 | 4.3 | 42.5 | 294.3 | 51.6 | 55.9 | 3002 | 849
2023-05-18 16:59 | 146.4 | 4.9 | 42.2 | 295.1 | 50.7 | 55.7 | 3003 | 846
2023-05-18 17:00 | 143.5 | 1.9 | 42 | 295.4 | 51 | 55.9 | 3006 | 843
2023-05-18 17:01 | 143.7 | 2.8 | 41.9 | 290.4 | 51.1 | 55.7 | 3004 | 805
2023-05-18 17:02 | 144.9 | 4.9 | 41.8 | 284.5 | 51.4 | 55.5 | 3006 | 771
2023-05-18 17:03 | 143.9 | 4.2 | 41.6 | 281.6 | 50.8 | 54.9 | 3004 | 756
2023-05-18 17:04 | 141.6 | 2.1 | 41.3 | 280.8 | 51 | 54.9 | 3003 | 738
2023-05-18 17:05 | 142.3 | 4 | 41.2 | 272.1 | 51 | 53.9 | 3004 | 699
2023-05-18 17:06 | 141.1 | 4.1 | 41.1 | 265.1 | 51.1 | 53.2 | 3002 | 658
2023-05-18 17:07 | 141.2 | 4.7 | 40.8 | 262 | 51.6 | 52.1 | 3003 | 647
2023-05-18 17:08 | 143.7 | 4.7 | 40.5 | 277.1 | 51.4 | 51.2 | 3004 | 735
2023-05-18 17:09 | 146.8 | 9.2 | 40.3 | 269.2 | 51.3 | 50.5 | 3003 | 692
2023-05-18 17:10 | 144.5 | 4.9 | 40.3 | 281.3 | 51.5 | 50.3 | 3004 | 781
2023-05-18 17:11 | 144.9 | 5 | 40.5 | 283.6 | 50.7 | 49.7 | 3003 | 766
2023-05-18 17:12 | 142.5 | 2 | 40.6 | 287.4 | 51.4 | 50.6 | 3002 | 816
2023-05-18 17:13 | 143.8 | 3.7 | 40.8 | 284.8 |  | 51.6 |  | 798
2023-05-18 17:14 | 143.5 | 4 | 40.9 | 280.2 | 51.4 | 52 |  | 759
2023-05-18 17:15 | 143.8 | 5.4 | 40.9 | 273 | 51.5 | 52.4 |  | 714
2023-05-18 17:16 | 142.5 | 3 | 40.8 | 280.3 | 51.6 | 51.8 | 3002 | 747
2023-05-18 17:17 | 144.8 | 5.3 |  | 280.4 | 51.9 | 51.9 | 3003 | 758
2023-05-18 17:18 | 147.3 | 6.9 | 40.8 | 287.2 | 52.1 |  | 3004 | 808
2023-05-18 17:19 | 150.6 | 8.7 | 40.9 | 297.6 | 51.4 | 51.9 | 3005 | 858
2023-05-18 17:20 | 146.5 | 5.9 | 40.9 | 288.2 | 52 | 52.4 | 3004 | 835
2023-05-18 17:21 | 144.3 | 2.9 | 41.3 | 294.2 | 51.5 | 53.2 | 3003 | 851
2023-05-18 17:22 | 142.7 | 2 | 41.5 | 289.5 | 51.9 | 53.4 | 3003 | 815 |  | 858.2
2023-05-18 17:23 | 142.6 | 2.9 | 41.7 | 282.3 | 52.4 | 54.7 | 3002 | 769 |  | 858.3
2023-05-18 17:24 | 142.6 | 3.8 | 41.6 | 275.3 | 52 | 54.3 | 3000 | 712
2023-05-18 17:25 | 142 | 4.8 | 41.4 | 266.2 | 52.2 | 53.4 |  | 652
2023-05-18 17:26 | 141.2 | 4.1 | 41.2 | 265.8 | 52.3 | 52.3 |  | 643
2023-05-18 17:27 | 142.1 | 4.7 | 41 | 267.5 | 52.5 | 51.5 |  | 649
2023-05-18 17:28 | 144.7 | 7.2 | 40.8 | 268.8 | 52.6 | 50.5 | 3000 | 672
2023-05-18 17:29 | 147.7 | 8.3 | 40.6 | 279.9 | 51.9 | 50.3 | 3001 | 732
2023-05-18 17:30 | 143.1 | 4.7 | 40.5 | 272.5 | 52.1 | 50.2 | 3001 | 701
2023-05-18 17:31 | 140.9 | 2.1 | 40.5 | 276 | 52.2 | 50.5 | 3003 | 685
2023-05-18 17:32 | 147 | 7.8 | 40.6 | 278.5 | 52.8 | 50.5 | 3004 | 728
2023-05-18 17:33 | 149.8 | 5.3 | 40.7 | 316.7 | 52.4 | 50.9 | 3004 | 1005
2023-05-18 17:34 | 150 | 7.4 | 41 | 303 | 51.8 | 52.3 | 3003 | 900
2023-05-18 17:35 | 143.2 | 3.1 | 41.5 | 285 | 52.1 | 53.3 | 3002 | 792
2023-05-18 17:36 | 138.9 | 2.4 | 41.8 | 261.9 | 51.7 | 54.1 | 3001 | 607
2023-05-18 17:37 | 135.2 | 1.8 | 41.7 | 242.1 | 51.7 | 54.5 | 3001 | 459
2023-05-18 17:38 | 131.9 | 1.8 | 41.4 | 223.5 | 51.9 | 53.3 | 3000 | 343
2023-05-18 17:39 | 128.8 | 2 | 40.9 | 206.3 | 52.4 | 50.9 | 2999 | 249
2023-05-18 17:40 | 125.9 | 2.4 | 40.5 | 190.7 | 52.9 | 47 |  | 170
2023-05-18 17:41 | 123.4 | 2 | 40.4 | 181.1 | 53.1 | 42.9 |  | 116 | 9442
2023-05-18 17:42 | 121.4 | 1.4 |  | 174.7 | 53.3 | 39.4 | 2999 | 71 | 9443
2023-05-18 17:43 | 119.9 | 1.2 | 40.4 | 169 | 53.3 | 36.6 | 2998 | 38
2023-05-18 17:44 | 118.7 | 0.9 | 40.5 | 165.1 | 53.4 | 34.5 | 2998 | 14
2023-05-18 17:45 | 117.8 | 0.7 | 40.6 | 162.5 | 53.5 | 32.7 | 2997 | 7

## drucken
Time | Drucksensor_1 (Arith. Mean) | Drucksensor_2 (Arith. Mean) | Drucksensor_3 (Arith. Mean) | Drucksensor_4 (Arith. Mean) | Drucksensor_5 (Arith. Mean) | Drucksensor_6 (Arith. Mean) | Drucksensor_7 (Arith. Mean) | Drucksensor_8 (Arith. Mean)
43602.4184 | 0.8437 | 0.94663 | 0.91074 | 0.76888 | 0.65875 | 0.6028 | 0.59823 | 0.63318
43602.4182 | 0.80304 | 0.92764 | 0.89734 | 0.75935 | 0.65127 | 0.59802 | 0.59485 | 0.63285
43602.4185 | 0.7924 | 0.92173 | 0.89509 | 0.75789 | 0.65036 | 0.59765 | 0.59313 | 0.63325
43602.4185 | 0.79604 | 0.92221 | 0.8944 | 0.75766 | 0.64887 | 0.5967 | 0.59335 | 0.633
43602.4185 | 0.80083 | 0.92179 | 0.8942 | 0.75779 | 0.64911 | 0.59694 | 0.5935 | 0.63306
43602.4185 | 0.79552 | 0.92168 | 0.89357 | 0.75723 | 0.64941 | 0.59683 | 0.59889 | 0.63304
43602.4186 | 0.78082 | 0.91778 | 0.89411 | 0.75659 | 0.64811 | 0.59599 | 0.59615 | 0.63294
43602.4186 | 0.80954 | 0.92502 | 0.89566 | 0.75891 | 0.64899 | 0.59667 | 0.59442 | 0.6334
43602.4186 | 0.81137 | 0.92533 | 0.89697 | 0.76 | 0.65139 | 0.59804 | 0.59329 | 0.63384
43602.4186 | 0.81127 | 0.92883 | 0.89928 | 0.76114 | 0.65061 | 0.59768 | 0.59206 | 0.6333
43602.4186 | 0.81023 | 0.92894 | 0.8993 | 0.76119 | 0.65347 | 0.59969 | 0.59471 | 0.63406
43602.4186 | 0.78046 | 0.91816 | 0.89456 | 0.75589 | 0.64914 | 0.5967 | 0.59175 | 0.63268
43602.4186 | 0.80549 | 0.92612 | 0.89677 | 0.75934 | 0.6482 | 0.59652 | 0.59423 | 0.63302
43602.4186 | 0.81624 | 0.92976 | 0.89901 | 0.7611 | 0.65231 | 0.59911 | 0.59603 | 0.63423
43602.4186 | 0.80936 | 0.92682 | 0.89801 | 0.75965 | 0.65124 | 0.59816 | 0.59245 | 0.63343
43602.4187 | 0.79874 | 0.92654 | 0.89848 | 0.76039 | 0.65147 | 0.59843 | 0.59399 | 0.63377
43602.4187 | 0.79124 | 0.92234 | 0.8965 | 0.75807 | 0.64986 | 0.59753 | 0.59836 | 0.63326
43602.4187 | 0.80973 | 0.92874 | 0.89915 | 0.76097 | 0.65087 | 0.59833 | 0.59599 | 0.63387
43602.4187 | 0.80277 | 0.92724 | 0.89877 | 0.75984 | 0.65161 | 0.59876 | 0.59536 | 0.63382
43602.4187 | 0.81814 | 0.93121 | 0.90047 | 0.7617 | 0.65119 | 0.5986 | 0.59247 | 0.63384
43602.4187 | 0.80083 | 0.92706 | 0.89905 | 0.76068 | 0.65279 | 0.59957 | 0.59371 | 0.63423
43602.4187 | 0.80167 | 0.92817 | 0.89964 | 0.76118 | 0.65126 | 0.59852 | 0.59815 | 0.63387
43602.4187 | 0.79947 | 0.92729 | 0.89918 | 0.76101 | 0.65172 | 0.59898 | 0.59667 | 0.63394
43602.4188 | 0.80467 | 0.92517 | 0.8979 | 0.7596 | 0.65053 | 0.59815 | 0.59446 | 0.63356
43602.4188 | 0.80531 | 0.92528 | 0.89829 | 0.76004 | 0.65053 | 0.59829 | 0.59323 | 0.6339
43602.4188 | 0.79179 | 0.92241 | 0.8968 | 0.75841 | 0.64965 | 0.59768 | 0.59438 | 0.63357
43602.4188 | 0.7918 | 0.92344 | 0.8974 | 0.75955 | 0.64992 | 0.59783 | 0.59498 | 0.63382
43602.4188 | 0.78741 | 0.92258 | 0.89658 | 0.75886 | 0.64947 | 0.59764 | 0.59418 | 0.63383
43602.4188 | 0.79966 | 0.92687 | 0.89843 | 0.76116 | 0.65023 | 0.59847 | 0.59375 | 0.63426
43602.4188 | 0.79054 | 0.92314 | 0.89601 | 0.75865 | 0.65094 | 0.59861 | 0.59356 | 0.63456
43602.4188 | 0.78324 | 0.91864 | 0.89381 | 0.75641 | 0.6477 | 0.59644 | 0.59165 | 0.63368
43602.4188 | 0.79474 | 0.92236 | 0.89458 | 0.75791 | 0.64833 | 0.597 | 0.6033 | 0.63435
43602.4189 | 0.78802 | 0.91915 | 0.89377 | 0.75645 | 0.64802 | 0.5966 | 0.5972 | 0.63384
43602.4189 | 0.80911 | 0.92594 | 0.89617 | 0.76019 | 0.64907 | 0.59721 | 0.59606 | 0.63436
43602.4189 | 0.78617 | 0.91875 | 0.89401 | 0.75711 | 0.64971 | 0.59773 | 0.59318 | 0.63451
43602.4189 | 0.77195 | 0.91339 | 0.89061 | 0.75361 | 0.646 | 0.59552 | 0.59106 | 0.63351
43602.4189 | 0.78448 | 0.91569 | 0.89061 | 0.75486 | 0.64524 | 0.5952 | 0.5903 | 0.63391
43602.4189 | 0.77615 | 0.91406 | 0.891 | 0.75418 | 0.64649 | 0.59602 | 0.59272 | 0.6344
43602.4189 | 0.78545 | 0.91621 | 0.88996 | 0.75455 | 0.64551 | 0.59542 | 0.59223 | 0.63373
43602.4189 | 0.78499 | 0.91592 | 0.89013 | 0.75512 | 0.64713 | 0.59604 | 0.5928 | 0.63474
43602.4189 | 0.77577 | 0.91114 | 0.88706 | 0.75214 | 0.64502 | 0.59475 | 0.5917 | 0.63403
43602.419 | 0.76441 | 0.90756 | 0.88632 | 0.7516 | 0.64346 | 0.59379 | 0.58923 | 0.63382
43602.419 | 0.76604 | 0.9074 | 0.88645 | 0.75114 | 0.64301 | 0.59339 | 0.59236 | 0.63384
43602.419 | 0.77423 | 0.90921 | 0.88634 | 0.75174 | 0.64367 | 0.59375 | 0.59411 | 0.63436
43602.419 | 0.76558 | 0.90783 | 0.88537 | 0.75156 | 0.64344 | 0.59347 | 0.59114 | 0.63423
43602.419 | 0.76521 | 0.90512 | 0.88368 | 0.74976 | 0.64319 | 0.59342 | 0.5892 | 0.63445
43602.419 | 0.76146 | 0.9027 | 0.8821 | 0.74829 | 0.64125 | 0.59232 | 0.58887 | 0.63389
43602.419 | 0.76445 | 0.90448 | 0.88336 | 0.74953 | 0.64128 | 0.59223 | 0.59115 | 0.63426
43602.419 | 0.76374 | 0.90473 | 0.88321 | 0.7502 | 0.64245 | 0.59303 | 0.59207 | 0.63482
43602.419 | 0.77082 | 0.90346 | 0.88003 | 0.74771 | 0.6415 | 0.59222 | 0.59667 | 0.63414
43602.4191 | 0.75837 | 0.89937 | 0.8788 | 0.74667 | 0.63991 | 0.59117 | 0.59019 | 0.63372
43602.4191 | 0.76102 | 0.89903 | 0.87774 | 0.74636 | 0.63949 | 0.59085 | 0.5896 | 0.63368
43602.4191 | 0.75111 | 0.89511 | 0.87626 | 0.74524 | 0.63872 | 0.59026 | 0.58655 | 0.6339
43602.4191 | 0.7471 | 0.89356 | 0.87668 | 0.74475 | 0.63776 | 0.58983 | 0.58605 | 0.63384
43602.4191 | 0.76569 | 0.89725 | 0.87527 | 0.74481 | 0.6382 | 0.59006 | 0.58696 | 0.63428
43602.4191 | 0.75279 | 0.89346 | 0.87446 | 0.74419 | 0.63756 | 0.5895 | 0.58569 | 0.63399
43602.4191 | 0.75019 | 0.89286 | 0.87363 | 0.74363 | 0.63673 | 0.5891 | 0.58884 | 0.63376
43602.4191 | 0.74917 | 0.89265 | 0.87386 | 0.74342 | 0.63678 | 0.58915 | 0.5878 | 0.63433
43602.4191 | 0.75999 | 0.89508 | 0.87327 | 0.74338 | 0.63712 | 0.58917 | 0.58639 | 0.63407
43602.4192 | 0.75174 | 0.89304 | 0.87322 | 0.7434 | 0.63672 | 0.5887 | 0.58486 | 0.63374
43602.4192 | 0.75463 | 0.89223 | 0.87204 | 0.74304 | 0.63664 | 0.58865 | 0.59136 | 0.6339
43602.4192 | 0.75398 | 0.89072 | 0.87084 | 0.74158 | 0.63607 | 0.58817 | 0.59283 | 0.63363
43602.4192 | 0.7522 | 0.89127 | 0.87077 | 0.74169 | 0.63487 | 0.58749 | 0.5882 | 0.63333
43602.4192 | 0.76384 | 0.89263 | 0.87088 | 0.74218 | 0.63557 | 0.58798 | 0.58584 | 0.63353
43602.4192 | 0.7523 | 0.89005 | 0.8698 | 0.74127 | 0.6355 | 0.5876 | 0.58396 | 0.63325
43602.4192 | 0.73969 | 0.88456 | 0.8686 | 0.7394 | 0.63428 | 0.58692 | 0.58313 | 0.6331
43602.4192 | 0.75743 | 0.88868 | 0.8682 | 0.74051 | 0.63385 | 0.58678 | 0.58375 | 0.63322
43602.4192 | 0.75939 | 0.8908 | 0.87016 | 0.74177 | 0.63493 | 0.58733 | 0.58654 | 0.63377
43602.4193 | 0.7559 | 0.88927 | 0.86902 | 0.74116 | 0.63484 | 0.58701 | 0.5853 | 0.6328
43602.4193 | 0.75448 | 0.88929 | 0.86873 | 0.74049 | 0.63463 | 0.58703 | 0.58376 | 0.63292
43602.4193 | 0.76151 | 0.89052 | 0.86909 | 0.74075 | 0.63411 | 0.58687 | 0.5842 | 0.63286
43602.4193 | 0.76407 | 0.89225 | 0.86991 | 0.74154 | 0.6348 | 0.58687 | 0.58303 | 0.63286
43602.4193 | 0.75329 | 0.89033 | 0.86945 | 0.74137 | 0.635 | 0.58706 | 0.58606 | 0.63269
43602.4193 | 0.75796 | 0.89107 | 0.86999 | 0.74142 | 0.63473 | 0.58695 | 0.58615 | 0.63246
43602.4193 | 0.77089 | 0.89513 | 0.87082 | 0.74318 | 0.63581 | 0.58753 | 0.58669 | 0.63309
43602.4193 | 0.77334 | 0.89631 | 0.87142 | 0.74315 | 0.63628 | 0.58781 | 0.59293 | 0.63276
43602.4193 | 0.77737 | 0.89778 | 0.87235 | 0.74392 | 0.63684 | 0.58808 | 0.58737 | 0.63273
43602.4194 | 0.77404 | 0.89731 | 0.8718 | 0.74297 | 0.63624 | 0.5875 | 0.58574 | 0.63197
43602.4194 | 0.78167 | 0.90019 | 0.87321 | 0.74388 | 0.63701 | 0.58796 | 0.5839 | 0.63211
43602.4194 | 0.77865 | 0.89894 | 0.87311 | 0.74443 | 0.63707 | 0.58798 | 0.58412 | 0.63212
43602.4194 | 0.79372 | 0.90339 | 0.87498 | 0.74536 | 0.63765 | 0.58843 | 0.58491 | 0.63235
43602.4194 | 0.79757 | 0.90572 | 0.87674 | 0.74718 | 0.63921 | 0.5893 | 0.58552 | 0.63213
43602.4194 | 0.78526 | 0.90082 | 0.87308 | 0.74347 | 0.63777 | 0.58821 | 0.58749 | 0.63132
43602.4194 | 0.78396 | 0.90137 | 0.874 | 0.74461 | 0.63707 | 0.58789 | 0.5867 | 0.63152
43602.4194 | 0.78134 | 0.90182 | 0.87464 | 0.74499 | 0.63667 | 0.58779 | 0.58376 | 0.63128
43602.4194 | 0.79812 | 0.90497 | 0.8748 | 0.74534 | 0.63823 | 0.58905 | 0.58507 | 0.63173
43602.4195 | 0.79514 | 0.90487 | 0.87514 | 0.74562 | 0.63934 | 0.58945 | 0.58557 | 0.63223
43602.4195 | 0.79528 | 0.90479 | 0.87584 | 0.74628 | 0.63785 | 0.58816 | 0.58554 | 0.63121
43602.4195 | 0.79541 | 0.90646 | 0.87723 | 0.74732 | 0.63962 | 0.58958 | 0.59429 | 0.63157
43602.4195 | 0.80153 | 0.90844 | 0.87685 | 0.74684 | 0.6402 | 0.59002 | 0.59106 | 0.63157
43602.4195 | 0.78917 | 0.90565 | 0.87563 | 0.7462 | 0.63864 | 0.58895 | 0.58746 | 0.63095
43602.4195 | 0.80099 | 0.90921 | 0.87801 | 0.74806 | 0.63951 | 0.5896 | 0.5865 | 0.63124
43602.4195 | 0.80373 | 0.9069 | 0.87653 | 0.74684 | 0.63984 | 0.58976 | 0.58508 | 0.63125
43602.4195 | 0.79786 | 0.90634 | 0.87594 | 0.74621 | 0.63894 | 0.58893 | 0.5845 | 0.63077
43602.4195 | 0.80548 | 0.90888 | 0.87743 | 0.74705 | 0.63934 | 0.58925 | 0.58522 | 0.63088
43602.4196 | 0.81729 | 0.91389 | 0.88087 | 0.74946 | 0.64129 | 0.59065 | 0.58846 | 0.63123
43602.4196 | 0.80623 | 0.90957 | 0.87826 | 0.7478 | 0.64097 | 0.5905 | 0.58984 | 0.63059
43602.4196 | 0.80373 | 0.90888 | 0.87758 | 0.74675 | 0.64007 | 0.58984 | 0.59092 | 0.63064
43602.4196 | 0.81698 | 0.91545 | 0.88157 | 0.74984 | 0.64052 | 0.59038 | 0.58757 | 0.63096
43602.4196 | 0.81605 | 0.91749 | 0.88359 | 0.75123 | 0.64392 | 0.5924 | 0.5886 | 0.63127
43602.4196 | 0.78841 | 0.90923 | 0.87924 | 0.74797 | 0.64117 | 0.59063 | 0.58561 | 0.63055
43602.4196 | 0.82207 | 0.91894 | 0.88487 | 0.75217 | 0.64202 | 0.59135 | 0.58683 | 0.63123
43602.4196 | 0.79074 | 0.90801 | 0.87838 | 0.74688 | 0.64231 | 0.59145 | 0.58587 | 0.63079
43602.4196 | 0.80807 | 0.9092 | 0.87887 | 0.74704 | 0.63883 | 0.5893 | 0.5874 | 0.63038
43602.4197 | 0.80256 | 0.91267 | 0.8816 | 0.74991 | 0.64202 | 0.59153 | 0.58841 | 0.63139
43602.4197 | 0.79672 | 0.90867 | 0.87883 | 0.74755 | 0.64033 | 0.59046 | 0.58692 | 0.63077
43602.4197 | 0.83061 | 0.91876 | 0.88539 | 0.75226 | 0.64209 | 0.59173 | 0.58648 | 0.6313
43602.4197 | 0.81353 | 0.91376 | 0.88234 | 0.7505 | 0.64325 | 0.59243 | 0.58724 | 0.6314
43602.4197 | 0.8039 | 0.91174 | 0.88171 | 0.74943 | 0.64189 | 0.59134 | 0.59496 | 0.63095
43602.4197 | 0.81329 | 0.91413 | 0.88267 | 0.7503 | 0.64214 | 0.59173 | 0.59358 | 0.63127
43602.4197 | 0.79688 | 0.9098 | 0.88048 | 0.74834 | 0.64205 | 0.59162 | 0.5894 | 0.6313
43602.4197 | 0.80288 | 0.91055 | 0.8796 | 0.74771 | 0.63993 | 0.59033 | 0.58599 | 0.63078
43602.4197 | 0.8181 | 0.91779 | 0.88428 | 0.75115 | 0.64218 | 0.59164 | 0.58649 | 0.63148
43602.4198 | 0.80079 | 0.91355 | 0.88197 | 0.74991 | 0.64355 | 0.59253 | 0.58725 | 0.63151
43602.4198 | 0.80548 | 0.91294 | 0.8822 | 0.7498 | 0.641 | 0.59091 | 0.58659 | 0.63103
43602.4198 | 0.80278 | 0.91171 | 0.88133 | 0.74935 | 0.64289 | 0.59235 | 0.58932 | 0.63178
43602.4198 | 0.80332 | 0.90966 | 0.88023 | 0.74885 | 0.64023 | 0.59045 | 0.58844 | 0.63128
43602.4198 | 0.80228 | 0.91242 | 0.88105 | 0.74952 | 0.64193 | 0.59152 | 0.59051 | 0.63176
43602.4198 | 0.81602 | 0.91264 | 0.88188 | 0.75023 | 0.64176 | 0.59172 | 0.58645 | 0.63169
43602.4198 | 0.81174 | 0.91093 | 0.88064 | 0.74933 | 0.64248 | 0.59172 | 0.58681 | 0.63173
43602.4198 | 0.80021 | 0.91074 | 0.88086 | 0.74931 | 0.64191 | 0.59153 | 0.59062 | 0.63176
43602.4198 | 0.80169 | 0.90937 | 0.88019 | 0.74924 | 0.64068 | 0.5906 | 0.58855 | 0.63135
43602.4199 | 0.81005 | 0.91334 | 0.88244 | 0.75078 | 0.64236 | 0.59179 | 0.58933 | 0.63202
43602.4199 | 0.80348 | 0.91339 | 0.88301 | 0.751 | 0.64381 | 0.59303 | 0.58913 | 0.63233
43602.4199 | 0.82125 | 0.91601 | 0.88486 | 0.75197 | 0.64234 | 0.59214 | 0.58726 | 0.63205
43602.4199 | 0.81034 | 0.91634 | 0.88579 | 0.75256 | 0.6458 | 0.59455 | 0.59112 | 0.63298
43602.4199 | 0.79975 | 0.91378 | 0.8844 | 0.75154 | 0.64357 | 0.5927 | 0.59148 | 0.63198
43602.4199 | 0.80343 | 0.91418 | 0.88493 | 0.75167 | 0.64323 | 0.59286 | 0.58942 | 0.63235
43602.4199 | 0.82566 | 0.92238 | 0.88958 | 0.75573 | 0.64486 | 0.59382 | 0.59281 | 0.63265
43602.4199 | 0.8094 | 0.92017 | 0.88945 | 0.75496 | 0.64745 | 0.59553 | 0.59785 | 0.63295
43602.4199 | 0.8164 | 0.92248 | 0.89136 | 0.75552 | 0.64618 | 0.5947 | 0.59261 | 0.63262
43602.42 | 0.82433 | 0.93005 | 0.89765 | 0.76079 | 0.64999 | 0.59766 | 0.59362 | 0.63366
43602.42 | 0.8168 | 0.92627 | 0.89484 | 0.75829 | 0.64974 | 0.59725 | 0.59123 | 0.63311
43602.42 | 0.82108 | 0.9296 | 0.89677 | 0.75977 | 0.64962 | 0.5973 | 0.59174 | 0.6329
43602.42 | 0.82328 | 0.93221 | 0.89968 | 0.7612 | 0.65126 | 0.59861 | 0.59271 | 0.63365
43602.42 | 0.83609 | 0.93835 | 0.90435 | 0.76541 | 0.65369 | 0.60072 | 0.59658 | 0.63409
43602.42 | 0.84136 | 0.94271 | 0.90797 | 0.76754 | 0.65672 | 0.60259 | 0.59861 | 0.63445
43602.42 | 0.84288 | 0.94173 | 0.90698 | 0.76678 | 0.65472 | 0.60115 | 0.59462 | 0.63372
43602.42 | 0.84739 | 0.94643 | 0.91102 | 0.76956 | 0.65838 | 0.60369 | 0.59681 | 0.63478
43602.42 | 0.85101 | 0.95397 | 0.9184 | 0.77512 | 0.66125 | 0.60637 | 0.60284 | 0.63534
43602.4201 | 0.86974 | 0.96238 | 0.92498 | 0.7795 | 0.66499 | 0.60911 | 0.60373 | 0.63633
43602.4201 | 0.83574 | 0.95145 | 0.91832 | 0.77398 | 0.66544 | 0.60946 | 0.60357 | 0.63631
43602.4201 | 0.84511 | 0.95384 | 0.91965 | 0.77487 | 0.66201 | 0.60706 | 0.60058 | 0.63559
43602.4201 | 0.84954 | 0.95696 | 0.9216 | 0.77665 | 0.66508 | 0.60967 | 0.60224 | 0.63647
43602.4201 | 0.8358 | 0.95296 | 0.91945 | 0.77492 | 0.66248 | 0.60772 | 0.60245 | 0.63631
43602.4201 | 0.83816 | 0.96231 | 0.92845 | 0.78175 | 0.66766 | 0.61161 | 0.60661 | 0.63764
43602.4201 | 0.82936 | 0.95173 | 0.9203 | 0.7749 | 0.66534 | 0.60997 | 0.6117 | 0.63746
43602.4201 | 0.83599 | 0.95493 | 0.9222 | 0.77675 | 0.66475 | 0.60944 | 0.60504 | 0.63768
43602.4202 | 0.82996 | 0.95305 | 0.92123 | 0.77583 | 0.66412 | 0.60918 | 0.60416 | 0.63771
43602.4202 | 0.81997 | 0.94927 | 0.91946 | 0.77404 | 0.66447 | 0.60973 | 0.60327 | 0.63841
43602.4202 | 0.81917 | 0.94624 | 0.91712 | 0.77219 | 0.66166 | 0.60781 | 0.60055 | 0.6381
43602.4202 | 0.8332 | 0.95322 | 0.92101 | 0.77642 | 0.66366 | 0.60953 | 0.60265 | 0.63907
43602.4202 | 0.82157 | 0.95022 | 0.92018 | 0.77496 | 0.6651 | 0.61011 | 0.60312 | 0.63937
43602.4202 | 0.8256 | 0.95208 | 0.92162 | 0.776 | 0.66414 | 0.60999 | 0.60634 | 0.63949
43602.4202 | 0.81695 | 0.95214 | 0.92339 | 0.77721 | 0.66587 | 0.61098 | 0.60553 | 0.6399
43602.4202 | 0.81794 | 0.95245 | 0.92294 | 0.77735 | 0.66533 | 0.61104 | 0.60403 | 0.64027
43602.4202 | 0.81036 | 0.94857 | 0.92262 | 0.77499 | 0.66582 | 0.61125 | 0.60979 | 0.64075
43602.4203 | 0.80665 | 0.94918 | 0.92323 | 0.77617 | 0.66407 | 0.61028 | 0.61001 | 0.64057
43602.4203 | 0.81894 | 0.95206 | 0.924 | 0.77717 | 0.66642 | 0.61195 | 0.60869 | 0.64157
43602.4203 | 0.80154 | 0.94886 | 0.92549 | 0.77681 | 0.66617 | 0.61221 | 0.60667 | 0.6417
43602.4203 | 0.81507 | 0.95397 | 0.92614 | 0.77892 | 0.66705 | 0.61306 | 0.60617 | 0.64226
43602.4203 | 0.81254 | 0.9517 | 0.92556 | 0.77782 | 0.66787 | 0.61353 | 0.60627 | 0.64286
43602.4203 | 0.79666 | 0.945 | 0.92354 | 0.77361 | 0.66605 | 0.61244 | 0.60615 | 0.6425
43602.4203 | 0.7967 | 0.94263 | 0.92107 | 0.7719 | 0.6638 | 0.61133 | 0.60731 | 0.64264
43602.4203 | 0.7855 | 0.93925 | 0.92105 | 0.7717 | 0.66312 | 0.61114 | 0.60648 | 0.64296
43602.4203 | 0.78197 | 0.93792 | 0.92027 | 0.77185 | 0.66349 | 0.61148 | 0.60638 | 0.64391
43602.4204 | 0.77996 | 0.9356 | 0.91833 | 0.76985 | 0.6627 | 0.61089 | 0.61341 | 0.6439
43602.4204 | 0.78822 | 0.93628 | 0.91623 | 0.7695 | 0.66213 | 0.61058 | 0.60816 | 0.64428
43602.4204 | 0.78256 | 0.93278 | 0.91524 | 0.76849 | 0.6615 | 0.61033 | 0.60684 | 0.64422
43602.4204 | 0.77735 | 0.93046 | 0.91358 | 0.76717 | 0.66096 | 0.61003 | 0.60468 | 0.64462
43602.4204 | 0.77313 | 0.92729 | 0.91188 | 0.7658 | 0.66003 | 0.60953 | 0.60367 | 0.64485
43602.4204 | 0.7706 | 0.92456 | 0.90922 | 0.76416 | 0.65866 | 0.60867 | 0.60341 | 0.64449
43602.4204 | 0.76595 | 0.92286 | 0.90863 | 0.76426 | 0.65829 | 0.60831 | 0.60449 | 0.64507
43602.4204 | 0.77055 | 0.92212 | 0.9071 | 0.7636 | 0.65818 | 0.60816 | 0.60562 | 0.64512
43602.4204 | 0.75889 | 0.91762 | 0.90518 | 0.76246 | 0.65719 | 0.60737 | 0.60483 | 0.64518
43602.4205 | 0.76176 | 0.9156 | 0.90202 | 0.7605 | 0.65603 | 0.6068 | 0.60143 | 0.64512
43602.4205 | 0.75835 | 0.91416 | 0.90047 | 0.75921 | 0.65491 | 0.60595 | 0.60105 | 0.64487
43602.4205 | 0.75453 | 0.91168 | 0.89921 | 0.75946 | 0.65406 | 0.60539 | 0.6038 | 0.64482
43602.4205 | 0.75516 | 0.9106 | 0.89767 | 0.7579 | 0.65355 | 0.60488 | 0.60282 | 0.6447
43602.4205 | 0.75437 | 0.90819 | 0.89564 | 0.75631 | 0.65279 | 0.60426 | 0.60246 | 0.64464
43602.4205 | 0.7423 | 0.90316 | 0.89501 | 0.75548 | 0.65169 | 0.60346 | 0.5996 | 0.64463
43602.4205 | 0.74614 | 0.90375 | 0.89448 | 0.755 | 0.65093 | 0.60318 | 0.60227 | 0.64458
43602.4205 | 0.74723 | 0.90386 | 0.89293 | 0.7549 | 0.65034 | 0.60247 | 0.60443 | 0.64414
43602.4205 | 0.74434 | 0.90321 | 0.89351 | 0.75537 | 0.65035 | 0.60203 | 0.6003 | 0.64417
43602.4206 | 0.75775 | 0.90599 | 0.89226 | 0.75428 | 0.65003 | 0.60159 | 0.59869 | 0.64377
43602.4206 | 0.75002 | 0.90401 | 0.89264 | 0.75416 | 0.64975 | 0.6015 | 0.59708 | 0.64389
43602.4206 | 0.74457 | 0.90202 | 0.8925 | 0.75389 | 0.64893 | 0.60097 | 0.59629 | 0.64361
43602.4206 | 0.74787 | 0.90467 | 0.89341 | 0.75451 | 0.6491 | 0.60097 | 0.59929 | 0.64355
43602.4206 | 0.74861 | 0.90538 | 0.89473 | 0.75545 | 0.64962 | 0.6014 | 0.59889 | 0.64347
43602.4206 | 0.7493 | 0.90575 | 0.89566 | 0.75603 | 0.64981 | 0.60107 | 0.5988 | 0.64302
43602.4206 | 0.74714 | 0.90569 | 0.89728 | 0.75635 | 0.65003 | 0.60088 | 0.59592 | 0.64262
43602.4206 | 0.7497 | 0.90697 | 0.8975 | 0.75651 | 0.64952 | 0.60051 | 0.59641 | 0.64221
43602.4206 | 0.74901 | 0.90794 | 0.90009 | 0.75764 | 0.65003 | 0.60062 | 0.59586 | 0.6422
43602.4207 | 0.75665 | 0.91246 | 0.90178 | 0.75826 | 0.65043 | 0.60073 | 0.59953 | 0.64177
43602.4207 | 0.75292 | 0.91335 | 0.90463 | 0.76007 | 0.65134 | 0.60131 | 0.60608 | 0.64163
43602.4207 | 0.76277 | 0.91753 | 0.90667 | 0.76055 | 0.65282 | 0.60227 | 0.59997 | 0.64186
43602.4207 | 0.76405 | 0.91968 | 0.90908 | 0.76232 | 0.65335 | 0.6024 | 0.5987 | 0.64157
43602.4207 | 0.76021 | 0.91968 | 0.91151 | 0.76319 | 0.65379 | 0.60242 | 0.59701 | 0.64141
43602.4207 | 0.7688 | 0.92522 | 0.91458 | 0.76491 | 0.65484 | 0.60325 | 0.59699 | 0.64148
43602.4207 | 0.76828 | 0.9281 | 0.91891 | 0.76781 | 0.6563 | 0.60417 | 0.59874 | 0.64144
43602.4207 | 0.77372 | 0.93123 | 0.92146 | 0.76841 | 0.65747 | 0.60496 | 0.6003 | 0.64144
43602.4207 | 0.77186 | 0.93202 | 0.92317 | 0.76874 | 0.65815 | 0.60551 | 0.60047 | 0.64123
43602.4208 | 0.78114 | 0.93668 | 0.92592 | 0.77091 | 0.65886 | 0.60586 | 0.59966 | 0.64143
43602.4208 | 0.78661 | 0.94123 | 0.92841 | 0.77248 | 0.66036 | 0.60666 | 0.5994 | 0.6414
43602.4208 | 0.78397 | 0.94329 | 0.93174 | 0.7742 | 0.66186 | 0.60761 | 0.60478 | 0.64143
43602.4208 | 0.78305 | 0.94341 | 0.93389 | 0.7745 | 0.66258 | 0.6083 | 0.60367 | 0.64154
43602.4208 | 0.78717 | 0.94782 | 0.93848 | 0.77687 | 0.66342 | 0.6092 | 0.60362 | 0.64171
43602.4208 | 0.78958 | 0.95026 | 0.93978 | 0.77785 | 0.66497 | 0.61011 | 0.60235 | 0.64182
43602.4208 | 0.80526 | 0.95759 | 0.94294 | 0.78025 | 0.66627 | 0.61108 | 0.60584 | 0.64189
43602.4208 | 0.80319 | 0.95933 | 0.94668 | 0.78229 | 0.66798 | 0.6121 | 0.60977 | 0.64182
43602.4208 | 0.80434 | 0.96145 | 0.94794 | 0.78199 | 0.66843 | 0.61221 | 0.60657 | 0.64186
43602.4209 | 0.80725 | 0.96491 | 0.95116 | 0.78417 | 0.6692 | 0.61293 | 0.60567 | 0.64198
43602.4209 | 0.80288 | 0.96674 | 0.95471 | 0.78549 | 0.67101 | 0.61447 | 0.60565 | 0.64245
43602.4209 | 0.80814 | 0.96862 | 0.95687 | 0.78641 | 0.67194 | 0.61531 | 0.60694 | 0.64262
43602.4209 | 0.82156 | 0.97619 | 0.95937 | 0.78756 | 0.67295 | 0.61603 | 0.60927 | 0.64267
43602.4209 | 0.81964 | 0.97952 | 0.96428 | 0.79074 | 0.67441 | 0.6168 | 0.61109 | 0.64269
43602.4209 | 0.82243 | 0.98343 | 0.96792 | 0.79312 | 0.67722 | 0.61896 | 0.61042 | 0.64349
43602.4209 | 0.82985 | 0.98793 | 0.97077 | 0.79605 | 0.67852 | 0.61986 | 0.61015 | 0.64362
43602.4209 | 0.83015 | 0.99107 | 0.97396 | 0.79691 | 0.68091 | 0.6216 | 0.61275 | 0.64419
43602.4209 | 0.83191 | 0.99635 | 0.98009 | 0.79946 | 0.68191 | 0.62252 | 0.61484 | 0.64428
43602.421 | 0.83508 | 0.99906 | 0.98109 | 0.80246 | 0.68442 | 0.62439 | 0.61572 | 0.64472
43602.421 | 0.84055 | 1.0033 | 0.98513 | 0.80446 | 0.68653 | 0.62509 | 0.6251 | 0.64504
43602.421 | 0.83951 | 1.0039 | 0.98637 | 0.8042 | 0.68703 | 0.62611 | 0.62021 | 0.64512
43602.421 | 0.84115 | 1.0059 | 0.98867 | 0.80477 | 0.68768 | 0.62701 | 0.6202 | 0.64566
43602.421 | 0.85003 | 1.0122 | 0.99214 | 0.80692 | 0.68928 | 0.62836 | 0.61926 | 0.64627
43602.421 | 0.85667 | 1.0175 | 0.99428 | 0.8102 | 0.6912 | 0.62962 | 0.61881 | 0.64634
43602.421 | 0.85054 | 1.0186 | 0.99832 | 0.81197 | 0.69307 | 0.63113 | 0.61997 | 0.64689
43602.421 | 0.85948 | 1.022 | 0.99965 | 0.81275 | 0.69435 | 0.6325 | 0.62171 | 0.64732
43602.421 | 0.86774 | 1.0311 | 1.0054 | 0.8162 | 0.6961 | 0.63335 | 0.62479 | 0.64757
43602.4211 | 0.86974 | 1.0339 | 1.0077 | 0.81806 | 0.69865 | 0.63553 | 0.62646 | 0.64834
43602.4211 | 0.86923 | 1.0331 | 1.0089 | 0.81855 | 0.69971 | 0.63655 | 0.62604 | 0.64892
43602.4211 | 0.87034 | 1.0355 | 1.012 | 0.81868 | 0.70015 | 0.63726 | 0.62539 | 0.64906
43602.4211 | 0.87099 | 1.0413 | 1.0172 | 0.82358 | 0.7027 | 0.63926 | 0.63094 | 0.64967
43602.4211 | 0.88043 | 1.0464 | 1.0172 | 0.82724 | 0.70582 | 0.64084 | 0.63448 | 0.65015
43602.4211 | 0.87481 | 1.0415 | 1.0179 | 0.82326 | 0.70574 | 0.64097 | 0.6318 | 0.65019
43602.4211 | 0.87578 | 1.0392 | 1.0176 | 0.8206 | 0.70332 | 0.64028 | 0.63025 | 0.64995
43602.4211 | 0.8867 | 1.0488 | 1.0216 | 0.8265 | 0.7048 | 0.64172 | 0.62965 | 0.65048
43602.4211 | 0.88995 | 1.0532 | 1.0249 | 0.8301 | 0.70925 | 0.64412 | 0.63431 | 0.65172
43602.4212 | 0.8841 | 1.0509 | 1.0251 | 0.82833 | 0.70975 | 0.64471 | 0.63392 | 0.65182
43602.4212 | 0.88434 | 1.0506 | 1.025 | 0.82766 | 0.70929 | 0.64489 | 0.63531 | 0.65205
43602.4212 | 0.88689 | 1.052 | 1.0266 | 0.82856 | 0.70965 | 0.64529 | 0.63292 | 0.65247
43602.4212 | 0.89033 | 1.0558 | 1.0287 | 0.83034 | 0.71079 | 0.64624 | 0.63407 | 0.65294
43602.4212 | 0.89045 | 1.0569 | 1.0296 | 0.83045 | 0.71217 | 0.64732 | 0.64214 | 0.65354
43602.4212 | 0.88774 | 1.0559 | 1.031 | 0.83138 | 0.71271 | 0.64779 | 0.6388 | 0.6538
43602.4212 | 0.88698 | 1.056 | 1.0314 | 0.8321 | 0.71316 | 0.64834 | 0.63793 | 0.65408
43602.4212 | 0.88352 | 1.0542 | 1.0319 | 0.83088 | 0.71325 | 0.64856 | 0.63726 | 0.65443
43602.4212 | 0.88566 | 1.0535 | 1.0317 | 0.82893 | 0.71255 | 0.64851 | 0.63579 | 0.65469
43602.4213 | 0.87728 | 1.0511 | 1.0328 | 0.82996 | 0.71259 | 0.64905 | 0.63707 | 0.65503
43602.4213 | 0.88519 | 1.053 | 1.0333 | 0.83116 | 0.71313 | 0.64921 | 0.6439 | 0.65527
43602.4213 | 0.88902 | 1.0571 | 1.0355 | 0.83244 | 0.71479 | 0.65041 | 0.64399 | 0.65592
43602.4213 | 0.88508 | 1.0557 | 1.0364 | 0.83205 | 0.71484 | 0.65064 | 0.641 | 0.65622
43602.4213 | 0.89092 | 1.0598 | 1.0382 | 0.83322 | 0.71548 | 0.65128 | 0.64011 | 0.65634
43602.4213 | 0.89531 | 1.0632 | 1.0408 | 0.8345 | 0.71731 | 0.65224 | 0.64075 | 0.65696
43602.4213 | 0.89318 | 1.0629 | 1.04 | 0.83526 | 0.71735 | 0.65229 | 0.63922 | 0.65683
43602.4213 | 0.89898 | 1.0648 | 1.0405 | 0.8351 | 0.71795 | 0.65303 | 0.64113 | 0.65743
43602.4213 | 0.89434 | 1.0593 | 1.0386 | 0.83232 | 0.71736 | 0.65272 | 0.64187 | 0.65736
43602.4214 | 0.88788 | 1.0556 | 1.0374 | 0.83055 | 0.7153 | 0.65142 | 0.6409 | 0.65705
43602.4214 | 0.87878 | 1.0518 | 1.0367 | 0.82962 | 0.71487 | 0.65145 | 0.64718 | 0.65725
43602.4214 | 0.88544 | 1.0522 | 1.0343 | 0.82842 | 0.71401 | 0.65113 | 0.64189 | 0.65749
43602.4214 | 0.88546 | 1.0508 | 1.0315 | 0.82581 | 0.71287 | 0.65004 | 0.64087 | 0.6573
43602.4214 | 0.87277 | 1.045 | 1.0306 | 0.82578 | 0.7121 | 0.6495 | 0.63916 | 0.65733
43602.4214 | 0.87483 | 1.044 | 1.0289 | 0.8248 | 0.71126 | 0.64889 | 0.63742 | 0.65736
43602.4214 | 0.85814 | 1.0361 | 1.027 | 0.82238 | 0.71018 | 0.64843 | 0.63648 | 0.65732
43602.4214 | 0.87269 | 1.0385 | 1.0235 | 0.82057 | 0.70909 | 0.6478 | 0.63657 | 0.65708
43602.4214 | 0.85671 | 1.0304 | 1.0206 | 0.81836 | 0.70769 | 0.64643 | 0.63794 | 0.65704
43602.4215 | 0.85655 | 1.0296 | 1.0186 | 0.81781 | 0.70626 | 0.64568 | 0.63704 | 0.65709
43602.4215 | 0.86145 | 1.0283 | 1.0162 | 0.8169 | 0.70554 | 0.64504 | 0.63458 | 0.657
43602.4215 | 0.84749 | 1.0241 | 1.0146 | 0.81526 | 0.70449 | 0.64461 | 0.63432 | 0.65679
43602.4215 | 0.8458 | 1.0219 | 1.0119 | 0.81436 | 0.7037 | 0.64364 | 0.63531 | 0.65685
43602.4215 | 0.84682 | 1.0191 | 1.0108 | 0.81254 | 0.70257 | 0.64313 | 0.63517 | 0.65652
43602.4215 | 0.84496 | 1.0183 | 1.0099 | 0.81067 | 0.70127 | 0.64204 | 0.63405 | 0.65589
43602.4215 | 0.84087 | 1.0159 | 1.0088 | 0.81067 | 0.70027 | 0.64123 | 0.64014 | 0.65584
43602.4215 | 0.84017 | 1.0154 | 1.0079 | 0.81081 | 0.69982 | 0.64072 | 0.6336 | 0.65566
43602.4216 | 0.84468 | 1.016 | 1.0067 | 0.81015 | 0.6994 | 0.64002 | 0.63245 | 0.65536
43602.4216 | 0.8405 | 1.0123 | 1.0065 | 0.80891 | 0.69871 | 0.64036 | 0.63173 | 0.65531
43602.4216 | 0.84699 | 1.0172 | 1.009 | 0.81222 | 0.69859 | 0.63969 | 0.62903 | 0.65496
43602.4216 | 0.84622 | 1.0179 | 1.0107 | 0.81268 | 0.70016 | 0.64001 | 0.62918 | 0.65556
43602.4216 | 0.85052 | 1.0199 | 1.0109 | 0.81236 | 0.69999 | 0.63988 | 0.6301 | 0.65494
43602.4216 | 0.85375 | 1.0211 | 1.0122 | 0.81117 | 0.69955 | 0.63976 | 0.6303 | 0.65445
43602.4216 | 0.85705 | 1.0224 | 1.012 | 0.81107 | 0.69861 | 0.63921 | 0.63088 | 0.65406
43602.4216 | 0.84122 | 1.02 | 1.0154 | 0.81207 | 0.69912 | 0.63926 | 0.62877 | 0.65392
43602.4216 | 0.85689 | 1.0246 | 1.0165 | 0.81243 | 0.69935 | 0.63955 | 0.62788 | 0.65367
43602.4217 | 0.85883 | 1.0284 | 1.0215 | 0.81621 | 0.70021 | 0.63943 | 0.63332 | 0.65328
43602.4217 | 0.86426 | 1.034 | 1.025 | 0.8191 | 0.70213 | 0.64038 | 0.63084 | 0.65333
43602.4217 | 0.85942 | 1.0361 | 1.0289 | 0.82086 | 0.70364 | 0.64131 | 0.63133 | 0.65307
43602.4217 | 0.86253 | 1.0382 | 1.0313 | 0.82025 | 0.70443 | 0.64178 | 0.63047 | 0.65304
43602.4217 | 0.86827 | 1.0408 | 1.0342 | 0.8209 | 0.70432 | 0.64158 | 0.62887 | 0.65242
43602.4217 | 0.87446 | 1.0467 | 1.037 | 0.82253 | 0.70553 | 0.64205 | 0.63172 | 0.65224
43602.4217 | 0.8686 | 1.0465 | 1.041 | 0.82316 | 0.70645 | 0.64295 | 0.6404 | 0.65201
43602.4217 | 0.87817 | 1.0523 | 1.0451 | 0.82589 | 0.70747 | 0.64391 | 0.63463 | 0.65218
43602.4217 | 0.88825 | 1.0606 | 1.0507 | 0.82762 | 0.70938 | 0.64428 | 0.63311 | 0.65156
43602.4218 | 0.89216 | 1.0656 | 1.0558 | 0.83106 | 0.71079 | 0.64508 | 0.63308 | 0.65118
43602.4218 | 0.89799 | 1.071 | 1.0607 | 0.83287 | 0.71329 | 0.64672 | 0.63211 | 0.65152
43602.4218 | 0.90507 | 1.076 | 1.066 | 0.83378 | 0.7145 | 0.64768 | 0.6327 | 0.65138
43602.4218 | 0.91225 | 1.0821 | 1.0712 | 0.83698 | 0.71654 | 0.6487 | 0.63488 | 0.65135
43602.4218 | 0.9009 | 1.084 | 1.0763 | 0.84037 | 0.71843 | 0.64986 | 0.63766 | 0.65167
43602.4218 | 0.90289 | 1.0876 | 1.0812 | 0.84238 | 0.72079 | 0.65173 | 0.63734 | 0.65194
43602.4218 | 0.91343 | 1.096 | 1.0869 | 0.84551 | 0.72223 | 0.65281 | 0.63713 | 0.65216
43602.4218 | 0.92162 | 1.1058 | 1.0941 | 0.85051 | 0.72611 | 0.65492 | 0.643 | 0.65277
43602.4218 | 0.93327 | 1.1126 | 1.0997 | 0.85289 | 0.72902 | 0.65713 | 0.64749 | 0.65315
43602.4219 | 0.92321 | 1.1151 | 1.1055 | 0.85555 | 0.73137 | 0.65893 | 0.6456 | 0.65378
43602.4219 | 0.93468 | 1.1204 | 1.1093 | 0.85775 | 0.73331 | 0.6606 | 0.64556 | 0.65422
43602.4219 | 0.94152 | 1.1274 | 1.1157 | 0.86112 | 0.73587 | 0.6625 | 0.64599 | 0.65476
43602.4219 | 0.93963 | 1.1317 | 1.1209 | 0.8651 | 0.73888 | 0.66443 | 0.6468 | 0.65544
43602.4219 | 0.94464 | 1.1336 | 1.1229 | 0.86505 | 0.74067 | 0.66608 | 0.64745 | 0.65554
43602.4219 | 0.94266 | 1.1386 | 1.1283 | 0.86908 | 0.74187 | 0.66719 | 0.65074 | 0.65587
43602.4219 | 0.9541 | 1.1443 | 1.1321 | 0.87084 | 0.74458 | 0.66881 | 0.65251 | 0.65622
43602.4219 | 0.9514 | 1.149 | 1.1357 | 0.87282 | 0.74631 | 0.67071 | 0.65384 | 0.65709
43602.4219 | 0.95945 | 1.1529 | 1.1403 | 0.87472 | 0.74824 | 0.67175 | 0.65358 | 0.65748
43602.422 | 0.95285 | 1.1544 | 1.142 | 0.87664 | 0.75007 | 0.67382 | 0.66121 | 0.65803
43602.422 | 0.9576 | 1.1592 | 1.1469 | 0.87977 | 0.75153 | 0.67453 | 0.65967 | 0.65802
43602.422 | 0.96749 | 1.1655 | 1.1507 | 0.88135 | 0.75416 | 0.67661 | 0.66005 | 0.65877
43602.422 | 0.96865 | 1.1661 | 1.1525 | 0.88252 | 0.75562 | 0.6778 | 0.65997 | 0.65923
43602.422 | 0.97641 | 1.1725 | 1.157 | 0.88475 | 0.75709 | 0.6789 | 0.65974 | 0.6596
43602.422 | 0.97991 | 1.1752 | 1.1599 | 0.88667 | 0.75956 | 0.68056 | 0.66041 | 0.66032
43602.422 | 0.97983 | 1.1784 | 1.1627 | 0.8888 | 0.76094 | 0.6817 | 0.66238 | 0.6603
43602.422 | 0.98421 | 1.1839 | 1.1667 | 0.891 | 0.76247 | 0.6829 | 0.66585 | 0.66056
43602.422 | 0.98782 | 1.1856 | 1.1679 | 0.89111 | 0.76413 | 0.6842 | 0.66707 | 0.66109
43602.4221 | 0.98258 | 1.1872 | 1.1703 | 0.89318 | 0.76544 | 0.68547 | 0.66596 | 0.66135
43602.4221 | 0.99229 | 1.1898 | 1.1726 | 0.89452 | 0.76643 | 0.68598 | 0.66539 | 0.6614
43602.4221 | 0.99081 | 1.1927 | 1.1755 | 0.8961 | 0.76785 | 0.68708 | 0.66576 | 0.66177
43602.4221 | 0.98691 | 1.1974 | 1.1779 | 0.89833 | 0.76991 | 0.68856 | 0.6732 | 0.66241
43602.4221 | 0.99577 | 1.1995 | 1.1806 | 0.89994 | 0.77127 | 0.68958 | 0.67355 | 0.6626
43602.4221 | 1.0029 | 1.2037 | 1.1832 | 0.90137 | 0.77296 | 0.69099 | 0.67256 | 0.66298
43602.4221 | 1.002 | 1.2057 | 1.1854 | 0.90211 | 0.77322 | 0.69086 | 0.67089 | 0.66235
43602.4221 | 1.0048 | 1.2092 | 1.188 | 0.90424 | 0.77501 | 0.69229 | 0.67214 | 0.66292
43602.4221 | 1.0064 | 1.2119 | 1.1899 | 0.90584 | 0.7762 | 0.69334 | 0.67161 | 0.66339
43602.4222 | 1.0097 | 1.2141 | 1.1923 | 0.90706 | 0.77786 | 0.69423 | 0.67181 | 0.6634
43602.4222 | 1.0092 | 1.2146 | 1.1936 | 0.9085 | 0.77875 | 0.69519 | 0.67424 | 0.66354
43602.4222 | 1.0096 | 1.2172 | 1.1962 | 0.90975 | 0.77966 | 0.69613 | 0.67583 | 0.66411
43602.4222 | 1.0174 | 1.2205 | 1.1981 | 0.91141 | 0.78131 | 0.69712 | 0.68051 | 0.66441
43602.4222 | 1.0199 | 1.2247 | 1.2001 | 0.91293 | 0.78257 | 0.69818 | 0.6778 | 0.66466
43602.4222 | 1.0217 | 1.2261 | 1.2021 | 0.91367 | 0.78397 | 0.69908 | 0.67755 | 0.66508
43602.4222 | 1.0251 | 1.2298 | 1.2036 | 0.91609 | 0.78544 | 0.70024 | 0.67855 | 0.66574
43602.4222 | 1.0314 | 1.2321 | 1.2052 | 0.91604 | 0.78642 | 0.70115 | 0.67803 | 0.66562
43602.4222 | 1.0316 | 1.2329 | 1.2059 | 0.91753 | 0.78736 | 0.70183 | 0.68219 | 0.66595
43602.4223 | 1.0302 | 1.2331 | 1.207 | 0.918 | 0.78793 | 0.70228 | 0.68121 | 0.66612
43602.4223 | 1.0373 | 1.2363 | 1.2086 | 0.91901 | 0.78868 | 0.70269 | 0.68106 | 0.6659
43602.4223 | 1.0325 | 1.2365 | 1.2092 | 0.91951 | 0.78942 | 0.70315 | 0.68198 | 0.6662
43602.4223 | 1.029 | 1.2374 | 1.2103 | 0.92022 | 0.78999 | 0.70375 | 0.68139 | 0.66643
43602.4223 | 1.0357 | 1.2388 | 1.2096 | 0.92091 | 0.79029 | 0.70399 | 0.68148 | 0.66636
43602.4223 | 1.0416 | 1.2419 | 1.2118 | 0.92034 | 0.79042 | 0.70396 | 0.68386 | 0.66642
43602.4223 | 1.0356 | 1.2412 | 1.2125 | 0.92244 | 0.79108 | 0.70496 | 0.68812 | 0.66639
43602.4223 | 1.0409 | 1.2439 | 1.2127 | 0.92296 | 0.79213 | 0.7054 | 0.68458 | 0.66713
43602.4223 | 1.0425 | 1.244 | 1.2128 | 0.92214 | 0.79195 | 0.7055 | 0.6843 | 0.66688
43602.4224 | 1.0501 | 1.2458 | 1.2129 | 0.92326 | 0.79215 | 0.70542 | 0.68379 | 0.66677
43602.4224 | 1.0448 | 1.2456 | 1.2138 | 0.92362 | 0.79298 | 0.70599 | 0.68316 | 0.66696
43602.4224 | 1.0471 | 1.2453 | 1.213 | 0.92417 | 0.79328 | 0.70656 | 0.6826 | 0.66767
43602.4224 | 1.0425 | 1.245 | 1.2127 | 0.924 | 0.79309 | 0.70641 | 0.68564 | 0.66715
43602.4224 | 1.045 | 1.2455 | 1.2123 | 0.92353 | 0.79315 | 0.70668 | 0.68546 | 0.66776
43602.4224 | 1.0423 | 1.2439 | 1.2116 | 0.92307 | 0.7928 | 0.70628 | 0.68418 | 0.66719
43602.4224 | 1.0546 | 1.2461 | 1.2115 | 0.92425 | 0.79296 | 0.70616 | 0.6868 | 0.66764
43602.4224 | 1.0463 | 1.2433 | 1.2101 | 0.92336 | 0.79288 | 0.706 | 0.68754 | 0.66731
43602.4224 | 1.0432 | 1.2428 | 1.2091 | 0.9239 | 0.79222 | 0.7061 | 0.68494 | 0.66759
43602.4225 | 1.0486 | 1.2425 | 1.2079 | 0.92158 | 0.79187 | 0.70567 | 0.68429 | 0.66749
43602.4225 | 1.0405 | 1.2406 | 1.2069 | 0.9214 | 0.79154 | 0.70544 | 0.68329 | 0.66752
43602.4225 | 1.0446 | 1.2392 | 1.2057 | 0.92011 | 0.79088 | 0.70491 | 0.68196 | 0.66725
43602.4225 | 1.0417 | 1.2388 | 1.2047 | 0.9195 | 0.78997 | 0.70414 | 0.6819 | 0.66656
43602.4225 | 1.0397 | 1.2367 | 1.2022 | 0.91892 | 0.78994 | 0.70378 | 0.68236 | 0.66668
43602.4225 | 1.0383 | 1.2354 | 1.2014 | 0.91789 | 0.78839 | 0.70279 | 0.68091 | 0.66614
43602.4225 | 1.0371 | 1.2334 | 1.1996 | 0.91719 | 0.78743 | 0.70204 | 0.68107 | 0.66626
43602.4225 | 1.0331 | 1.2315 | 1.1984 | 0.91617 | 0.78709 | 0.70157 | 0.67951 | 0.6661
43602.4225 | 1.0372 | 1.2299 | 1.1955 | 0.91461 | 0.78605 | 0.70111 | 0.68523 | 0.66557
43602.4226 | 1.0378 | 1.2292 | 1.1947 | 0.91318 | 0.78445 | 0.69988 | 0.68199 | 0.66491
43602.4226 | 1.0317 | 1.225 | 1.1916 | 0.91141 | 0.78274 | 0.69866 | 0.67933 | 0.66446
43602.4226 | 1.0316 | 1.2236 | 1.1904 | 0.91063 | 0.78199 | 0.69813 | 0.67774 | 0.66459
43602.4226 | 1.0214 | 1.2206 | 1.1886 | 0.90902 | 0.78102 | 0.69746 | 0.67614 | 0.66431
43602.4226 | 1.0268 | 1.2193 | 1.1857 | 0.90789 | 0.77989 | 0.69651 | 0.67456 | 0.66403
43602.4226 | 1.0254 | 1.2175 | 1.184 | 0.9067 | 0.77843 | 0.69505 | 0.67281 | 0.66346
43602.4226 | 1.0243 | 1.2158 | 1.1823 | 0.90538 | 0.77739 | 0.69426 | 0.674 | 0.66316
43602.4226 | 1.0244 | 1.2147 | 1.1801 | 0.90473 | 0.77629 | 0.69332 | 0.67499 | 0.66276
43602.4226 | 1.0234 | 1.2118 | 1.1775 | 0.90254 | 0.7749 | 0.69229 | 0.67674 | 0.66264
43602.4227 | 1.0213 | 1.2089 | 1.1761 | 0.90066 | 0.77387 | 0.6914 | 0.67235 | 0.66216
43602.4227 | 1.0219 | 1.2082 | 1.174 | 0.90078 | 0.77237 | 0.69044 | 0.66998 | 0.66163
43602.4227 | 1.0149 | 1.205 | 1.1724 | 0.89868 | 0.77186 | 0.68987 | 0.67035 | 0.66166
43602.4227 | 1.0132 | 1.2028 | 1.1698 | 0.89766 | 0.76997 | 0.68864 | 0.66773 | 0.66086
43602.4227 | 1.0171 | 1.2041 | 1.1694 | 0.89791 | 0.76951 | 0.6878 | 0.6665 | 0.66038
43602.4227 | 1.0105 | 1.2012 | 1.1675 | 0.89613 | 0.7686 | 0.68705 | 0.66851 | 0.66021
43602.4227 | 1.0137 | 1.2001 | 1.166 | 0.89536 | 0.76841 | 0.68665 | 0.67314 | 0.6599
43602.4227 | 1.0081 | 1.1985 | 1.1649 | 0.89495 | 0.76713 | 0.68597 | 0.66926 | 0.65962
43602.4227 | 1.016 | 1.1984 | 1.1628 | 0.89416 | 0.76667 | 0.68518 | 0.66668 | 0.65909
43602.4228 | 1.0088 | 1.1953 | 1.1619 | 0.89238 | 0.76568 | 0.68428 | 0.66463 | 0.6587
43602.4228 | 1.0124 | 1.1957 | 1.1605 | 0.89207 | 0.76465 | 0.68394 | 0.66426 | 0.65843
43602.4228 | 1.0104 | 1.1965 | 1.161 | 0.89357 | 0.76519 | 0.68386 | 0.66308 | 0.65856
43602.4228 | 1.0106 | 1.1954 | 1.1597 | 0.89289 | 0.76532 | 0.68392 | 0.66378 | 0.65846
43602.4228 | 1.0117 | 1.196 | 1.1591 | 0.89296 | 0.76426 | 0.68315 | 0.66431 | 0.65803
43602.4228 | 1.009 | 1.1938 | 1.1567 | 0.89124 | 0.76424 | 0.68312 | 0.67129 | 0.65817
43602.4228 | 1.009 | 1.1926 | 1.1556 | 0.89113 | 0.76305 | 0.68194 | 0.66486 | 0.65741
43602.4228 | 1.0098 | 1.1926 | 1.1548 | 0.89167 | 0.76319 | 0.682 | 0.66305 | 0.6575
43602.4228 | 1.0102 | 1.1933 | 1.1548 | 0.89216 | 0.76322 | 0.68154 | 0.66323 | 0.65726
43602.4229 | 1.0107 | 1.1943 | 1.155 | 0.89315 | 0.76312 | 0.68155 | 0.66134 | 0.6571
43602.4229 | 1.0125 | 1.1924 | 1.1523 | 0.89218 | 0.76277 | 0.6815 | 0.66237 | 0.65698
43602.4229 | 1.01 | 1.1937 | 1.1528 | 0.89312 | 0.76257 | 0.68104 | 0.66316 | 0.65672
43602.4229 | 1.0102 | 1.1918 | 1.1505 | 0.89225 | 0.76237 | 0.68097 | 0.66245 | 0.65634
43602.4229 | 1.0107 | 1.1915 | 1.1499 | 0.89182 | 0.76215 | 0.68093 | 0.66211 | 0.6563
43602.4229 | 1.0153 | 1.191 | 1.1493 | 0.89237 | 0.76233 | 0.68073 | 0.66279 | 0.65619
43602.4229 | 1.0166 | 1.1934 | 1.1493 | 0.89351 | 0.76268 | 0.6806 | 0.66193 | 0.6561
43602.4229 | 1.0153 | 1.1918 | 1.1485 | 0.89343 | 0.76341 | 0.68102 | 0.66246 | 0.65622
43602.423 | 1.0214 | 1.1943 | 1.1486 | 0.89562 | 0.76291 | 0.68093 | 0.6617 | 0.65588
43602.423 | 1.0174 | 1.1922 | 1.1478 | 0.89477 | 0.76398 | 0.68143 | 0.66921 | 0.65625
43602.423 | 1.0182 | 1.1945 | 1.1486 | 0.89628 | 0.76419 | 0.68149 | 0.6644 | 0.65621
43602.423 | 1.0185 | 1.1924 | 1.1473 | 0.89518 | 0.76527 | 0.68207 | 0.66458 | 0.65616
43602.423 | 1.0238 | 1.1949 | 1.1481 | 0.89657 | 0.76432 | 0.68173 | 0.66337 | 0.6561
43602.423 | 1.0251 | 1.1942 | 1.1478 | 0.89662 | 0.76543 | 0.68253 | 0.66276 | 0.6564
43602.423 | 1.0253 | 1.1958 | 1.1487 | 0.89849 | 0.76602 | 0.68309 | 0.66308 | 0.65638
43602.423 | 1.0311 | 1.1965 | 1.1484 | 0.89927 | 0.76697 | 0.68324 | 0.66308 | 0.65632
43602.423 | 1.0288 | 1.1973 | 1.1498 | 0.8999 | 0.76786 | 0.68414 | 0.66601 | 0.65688
43602.4231 | 1.0397 | 1.1988 | 1.1499 | 0.90117 | 0.76875 | 0.68464 | 0.66569 | 0.65698
43602.4231 | 1.0259 | 1.1969 | 1.1486 | 0.89982 | 0.76844 | 0.68476 | 0.67208 | 0.6568
43602.4231 | 1.0445 | 1.2023 | 1.1514 | 0.90348 | 0.77024 | 0.68592 | 0.66739 | 0.65717
43602.4231 | 1.0346 | 1.197 | 1.148 | 0.90055 | 0.77 | 0.68566 | 0.66647 | 0.65688
43602.4231 | 1.0444 | 1.1989 | 1.1482 | 0.90169 | 0.76938 | 0.68525 | 0.66625 | 0.65644
43602.4231 | 1.0435 | 1.2007 | 1.1491 | 0.90297 | 0.76983 | 0.68548 | 0.66507 | 0.65659
43602.4231 | 1.0458 | 1.2019 | 1.1498 | 0.90359 | 0.77073 | 0.68641 | 0.666 | 0.65721
43602.4231 | 1.0329 | 1.1966 | 1.1468 | 0.90006 | 0.7708 | 0.68645 | 0.6662 | 0.65719
43602.4231 | 1.037 | 1.1972 | 1.146 | 0.90027 | 0.76845 | 0.68472 | 0.66538 | 0.65609
43602.4232 | 1.056 | 1.2005 | 1.1483 | 0.90377 | 0.77041 | 0.68617 | 0.66771 | 0.6567
43602.4232 | 1.0375 | 1.194 | 1.1443 | 0.89986 | 0.76919 | 0.68514 | 0.66543 | 0.65618
43602.4232 | 1.043 | 1.1974 | 1.1445 | 0.90081 | 0.76892 | 0.68501 | 0.66905 | 0.65655
43602.4232 | 1.044 | 1.1974 | 1.1462 | 0.90266 | 0.7702 | 0.68578 | 0.67248 | 0.65666
43602.4232 | 1.0473 | 1.1938 | 1.1427 | 0.89945 | 0.76862 | 0.68508 | 0.66752 | 0.65624
43602.4232 | 1.056 | 1.1951 | 1.1433 | 0.90121 | 0.7682 | 0.68435 | 0.66659 | 0.65571
43602.4232 | 1.041 | 1.1913 | 1.1408 | 0.898 | 0.76782 | 0.68374 | 0.6647 | 0.65567
43602.4232 | 1.0405 | 1.193 | 1.1422 | 0.89906 | 0.76688 | 0.68383 | 0.66321 | 0.65592
43602.4232 | 1.0442 | 1.1911 | 1.1396 | 0.89747 | 0.7678 | 0.68401 | 0.66411 | 0.65567
43602.4233 | 1.0519 | 1.1924 | 1.1408 | 0.89891 | 0.76755 | 0.68387 | 0.664 | 0.65601
43602.4233 | 1.0488 | 1.1928 | 1.1405 | 0.89818 | 0.76637 | 0.68293 | 0.66471 | 0.65484
43602.4233 | 1.0489 | 1.1912 | 1.1389 | 0.89787 | 0.76635 | 0.68286 | 0.66401 | 0.65525
43602.4233 | 1.0414 | 1.1879 | 1.1375 | 0.8958 | 0.76726 | 0.68344 | 0.66868 | 0.65532
43602.4233 | 1.0381 | 1.1887 | 1.1377 | 0.8963 | 0.76436 | 0.68165 | 0.66463 | 0.65446
43602.4233 | 1.0408 | 1.1916 | 1.1398 | 0.89809 | 0.76582 | 0.68257 | 0.6642 | 0.65506
43602.4233 | 1.0318 | 1.186 | 1.1362 | 0.89447 | 0.76501 | 0.68216 | 0.66323 | 0.65484
43602.4233 | 1.0437 | 1.1915 | 1.1392 | 0.8981 | 0.76654 | 0.68306 | 0.66414 | 0.65525
43602.4233 | 1.0403 | 1.1861 | 1.1357 | 0.89483 | 0.76464 | 0.68189 | 0.66172 | 0.65491
43602.4234 | 1.0376 | 1.1881 | 1.1363 | 0.89513 | 0.76558 | 0.68248 | 0.66255 | 0.65512
43602.4234 | 1.0506 | 1.1919 | 1.1381 | 0.89767 | 0.76437 | 0.68172 | 0.66305 | 0.65465
43602.4234 | 1.0314 | 1.1826 | 1.1325 | 0.89206 | 0.76452 | 0.68193 | 0.66524 | 0.65464
43602.4234 | 1.031 | 1.184 | 1.1329 | 0.89267 | 0.76214 | 0.68014 | 0.66648 | 0.65415
43602.4234 | 1.0423 | 1.1862 | 1.1341 | 0.8939 | 0.76311 | 0.68079 | 0.66243 | 0.65435
43602.4234 | 1.0269 | 1.1838 | 1.133 | 0.89266 | 0.76274 | 0.68058 | 0.66202 | 0.6547
43602.4234 | 1.0255 | 1.1796 | 1.1296 | 0.88954 | 0.76082 | 0.6791 | 0.66008 | 0.65373
43602.4234 | 1.0298 | 1.1788 | 1.1282 | 0.88882 | 0.75964 | 0.67808 | 0.66113 | 0.65333
43602.4234 | 1.0263 | 1.179 | 1.128 | 0.88824 | 0.7581 | 0.67713 | 0.65914 | 0.6532
43602.4235 | 1.0282 | 1.1784 | 1.1278 | 0.88836 | 0.75994 | 0.67813 | 0.65977 | 0.65346
43602.4235 | 1.0229 | 1.1715 | 1.122 | 0.8839 | 0.75454 | 0.67444 | 0.65661 | 0.65199
43602.4235 | 1.0299 | 1.1763 | 1.1264 | 0.88847 | 0.75711 | 0.67582 | 0.66108 | 0.6527
43602.4235 | 1.0086 | 1.1681 | 1.1201 | 0.8817 | 0.75594 | 0.67522 | 0.65804 | 0.6529
43602.4235 | 1.0176 | 1.1708 | 1.1212 | 0.88321 | 0.75289 | 0.67314 | 0.65603 | 0.65221
43602.4235 | 1.0185 | 1.168 | 1.1192 | 0.88251 | 0.75349 | 0.67341 | 0.65608 | 0.65216
43602.4235 | 1.0162 | 1.1673 | 1.1188 | 0.88174 | 0.75353 | 0.67314 | 0.65452 | 0.65182
43602.4235 | 1.0118 | 1.1653 | 1.1167 | 0.88021 | 0.7522 | 0.67216 | 0.65499 | 0.65164
43602.4235 | 1.0062 | 1.1621 | 1.1146 | 0.87829 | 0.74916 | 0.67023 | 0.65413 | 0.65097
43602.4236 | 1.0027 | 1.1612 | 1.114 | 0.87712 | 0.74998 | 0.67054 | 0.65346 | 0.65114
43602.4236 | 1.0109 | 1.1652 | 1.1148 | 0.87908 | 0.74874 | 0.66973 | 0.65889 | 0.65055
43602.4236 | 1.0051 | 1.1627 | 1.1144 | 0.87843 | 0.75136 | 0.67138 | 0.65886 | 0.65143
43602.4236 | 0.99343 | 1.1557 | 1.1094 | 0.87383 | 0.74719 | 0.66891 | 0.65406 | 0.65028
43602.4236 | 1.0088 | 1.1589 | 1.1107 | 0.876 | 0.74684 | 0.66802 | 0.65291 | 0.65024
43602.4236 | 1.0089 | 1.1607 | 1.1115 | 0.87746 | 0.74784 | 0.66869 | 0.65127 | 0.65041
43602.4236 | 1.0052 | 1.1558 | 1.1088 | 0.87433 | 0.74671 | 0.66775 | 0.65029 | 0.64991
43602.4236 | 1.002 | 1.1576 | 1.1097 | 0.87511 | 0.74705 | 0.66827 | 0.65056 | 0.65022
43602.4236 | 1.0084 | 1.1578 | 1.1093 | 0.87561 | 0.7464 | 0.66773 | 0.65183 | 0.64996
43602.4237 | 1.0013 | 1.1551 | 1.1072 | 0.87339 | 0.74654 | 0.66763 | 0.651 | 0.65
43602.4237 | 1.0093 | 1.1608 | 1.1104 | 0.87699 | 0.74753 | 0.66835 | 0.65098 | 0.65053
43602.4237 | 1.0076 | 1.157 | 1.1085 | 0.87521 | 0.74698 | 0.66814 | 0.65504 | 0.65001
43602.4237 | 0.99754 | 1.1545 | 1.1062 | 0.87272 | 0.7457 | 0.66725 | 0.65109 | 0.64953
43602.4237 | 1.0041 | 1.1574 | 1.1081 | 0.87528 | 0.74626 | 0.66766 | 0.65158 | 0.6498
43602.4237 | 1.0015 | 1.1554 | 1.1058 | 0.87283 | 0.74527 | 0.66676 | 0.64995 | 0.6494
43602.4237 | 1.0062 | 1.1555 | 1.1063 | 0.87375 | 0.74546 | 0.66658 | 0.6489 | 0.64931
43602.4237 | 1.0062 | 1.1551 | 1.105 | 0.87315 | 0.74543 | 0.66687 | 0.65043 | 0.64938
43602.4237 | 0.99954 | 1.1572 | 1.1081 | 0.87561 | 0.7464 | 0.66769 | 0.65456 | 0.64983
43602.4238 | 1.0069 | 1.1572 | 1.1078 | 0.87555 | 0.74635 | 0.66782 | 0.65368 | 0.64969
43602.4238 | 1.0098 | 1.1573 | 1.1078 | 0.87576 | 0.74757 | 0.6683 | 0.65134 | 0.64992
43602.4238 | 1.0049 | 1.1533 | 1.1042 | 0.87284 | 0.74509 | 0.66664 | 0.6497 | 0.64924
43602.4238 | 1.0107 | 1.154 | 1.105 | 0.87334 | 0.74593 | 0.66713 | 0.64953 | 0.64938
43602.4238 | 1.0065 | 1.1552 | 1.1053 | 0.8737 | 0.74579 | 0.66714 | 0.64856 | 0.6494
43602.4238 | 1.0019 | 1.1518 | 1.1029 | 0.87183 | 0.74447 | 0.66611 | 0.65193 | 0.64885
43602.4238 | 1.0059 | 1.1533 | 1.1041 | 0.87347 | 0.7437 | 0.66534 | 0.65248 | 0.64871
43602.4238 | 1.0076 | 1.1528 | 1.1028 | 0.87233 | 0.74484 | 0.66619 | 0.65056 | 0.6489
43602.4238 | 1.0116 | 1.1536 | 1.1028 | 0.87335 | 0.74519 | 0.66634 | 0.64882 | 0.64897
43602.4239 | 1.0021 | 1.1476 | 1.0986 | 0.86851 | 0.7429 | 0.66484 | 0.64722 | 0.64844
43602.4239 | 1.0112 | 1.1519 | 1.1013 | 0.87177 | 0.74324 | 0.66488 | 0.64684 | 0.64863
43602.4239 | 1.0028 | 1.1485 | 1.0985 | 0.86945 | 0.7421 | 0.66431 | 0.64858 | 0.64806
43602.4239 | 1.0042 | 1.1514 | 1.1013 | 0.87249 | 0.7422 | 0.66419 | 0.64922 | 0.64834
43602.4239 | 1.0061 | 1.1487 | 1.0981 | 0.86976 | 0.74364 | 0.66507 | 0.65415 | 0.64852
43602.4239 | 0.99263 | 1.1481 | 1.0986 | 0.86995 | 0.74137 | 0.6638 | 0.65039 | 0.64811
43602.4239 | 0.9981 | 1.145 | 1.0956 | 0.86821 | 0.74214 | 0.66414 | 0.64852 | 0.64838
43602.4239 | 1.0009 | 1.144 | 1.0944 | 0.86758 | 0.74002 | 0.66236 | 0.64684 | 0.64758
43602.4239 | 1.0061 | 1.1464 | 1.0954 | 0.86867 | 0.74062 | 0.66276 | 0.64587 | 0.64788
43602.424 | 1.0014 | 1.1417 | 1.0926 | 0.8663 | 0.74031 | 0.66246 | 0.64458 | 0.6477
43602.424 | 1.0114 | 1.1442 | 1.0939 | 0.86861 | 0.73924 | 0.66163 | 0.64557 | 0.64758
43602.424 | 0.99213 | 1.1404 | 1.0914 | 0.86584 | 0.74013 | 0.66246 | 0.646 | 0.64775
43602.424 | 0.99906 | 1.1419 | 1.0921 | 0.86698 | 0.73852 | 0.66145 | 0.6469 | 0.64739
43602.424 | 1.0051 | 1.1413 | 1.0909 | 0.86617 | 0.73916 | 0.66189 | 0.65188 | 0.64789
43602.424 | 0.99301 | 1.1382 | 1.0889 | 0.86392 | 0.73691 | 0.65976 | 0.64493 | 0.64675
43602.424 | 1.0096 | 1.1429 | 1.0907 | 0.86708 | 0.73852 | 0.66122 | 0.6457 | 0.64724
43602.424 | 1.0003 | 1.1382 | 1.0877 | 0.86384 | 0.73998 | 0.66186 | 0.64517 | 0.64776
43602.424 | 1.0066 | 1.1404 | 1.0883 | 0.86503 | 0.73533 | 0.65863 | 0.64168 | 0.64644
43602.4241 | 0.99704 | 1.1372 | 1.0877 | 0.86331 | 0.73776 | 0.66059 | 0.64523 | 0.64736
43602.4241 | 1.0043 | 1.1407 | 1.0896 | 0.86587 | 0.73777 | 0.66044 | 0.64518 | 0.6471
43602.4241 | 1.0011 | 1.1365 | 1.0861 | 0.86291 | 0.73754 | 0.66031 | 0.64553 | 0.64724
43602.4241 | 1.004 | 1.1393 | 1.0875 | 0.86461 | 0.73586 | 0.65903 | 0.6424 | 0.64659
43602.4241 | 1.0055 | 1.139 | 1.0876 | 0.86501 | 0.73794 | 0.66066 | 0.64499 | 0.6475
43602.4241 | 1.0078 | 1.1429 | 1.0904 | 0.86772 | 0.73989 | 0.66239 | 0.64911 | 0.64774
43602.4241 | 1.0055 | 1.138 | 1.087 | 0.8644 | 0.73744 | 0.66043 | 0.64674 | 0.64703
43602.4241 | 0.99148 | 1.14 | 1.0885 | 0.86537 | 0.73873 | 0.66144 | 0.64499 | 0.64745
43602.4241 | 1.0079 | 1.1396 | 1.0872 | 0.86491 | 0.73704 | 0.66037 | 0.64432 | 0.64672
43602.4242 | 1.0047 | 1.1403 | 1.0877 | 0.86574 | 0.73906 | 0.66155 | 0.64458 | 0.64758
43602.4242 | 1.0053 | 1.1387 | 1.0866 | 0.86533 | 0.73964 | 0.66201 | 0.6452 | 0.6477
43602.4242 | 1.0025 | 1.1367 | 1.0844 | 0.86312 | 0.73581 | 0.65936 | 0.64429 | 0.64655
43602.4242 | 0.99828 | 1.1408 | 1.0878 | 0.86671 | 0.73891 | 0.66143 | 0.64515 | 0.64752
43602.4242 | 1.0099 | 1.139 | 1.0854 | 0.86533 | 0.73778 | 0.66102 | 0.65 | 0.6474
43602.4242 | 0.98685 | 1.1389 | 1.0868 | 0.86519 | 0.73868 | 0.66188 | 0.64828 | 0.64778
43602.4242 | 1.0002 | 1.1362 | 1.0847 | 0.86445 | 0.73845 | 0.66131 | 0.6471 | 0.64748
43602.4242 | 1.0084 | 1.1373 | 1.084 | 0.86464 | 0.73731 | 0.66055 | 0.64637 | 0.64746
43602.4243 | 1.0094 | 1.1405 | 1.0854 | 0.86599 | 0.7375 | 0.66091 | 0.6449 | 0.64727
43602.4243 | 1.013 | 1.1385 | 1.0841 | 0.86544 | 0.73832 | 0.66127 | 0.64438 | 0.64751
43602.4243 | 1.0057 | 1.1354 | 1.0821 | 0.86352 | 0.73706 | 0.66025 | 0.64287 | 0.64713
43602.4243 | 1.0082 | 1.1365 | 1.0826 | 0.86413 | 0.73737 | 0.66057 | 0.64363 | 0.64736
43602.4243 | 1.0076 | 1.1383 | 1.0839 | 0.86492 | 0.73744 | 0.66079 | 0.64405 | 0.64758
43602.4243 | 1.0096 | 1.1342 | 1.0812 | 0.86323 | 0.73662 | 0.6599 | 0.6425 | 0.64741
43602.4243 | 1.0077 | 1.1329 | 1.0797 | 0.86168 | 0.73579 | 0.65931 | 0.64433 | 0.64734
43602.4243 | 0.99521 | 1.1309 | 1.0785 | 0.86061 | 0.73634 | 0.65932 | 0.64404 | 0.64717
43602.4243 | 1.01 | 1.136 | 1.0807 | 0.86369 | 0.73526 | 0.65921 | 0.64996 | 0.64692
43602.4244 | 1.0047 | 1.1317 | 1.0787 | 0.86171 | 0.7355 | 0.65943 | 0.64768 | 0.64705
43602.4244 | 1.0041 | 1.13 | 1.0772 | 0.8608 | 0.73559 | 0.65925 | 0.64511 | 0.64711
43602.4244 | 1.0138 | 1.1329 | 1.0775 | 0.86178 | 0.73476 | 0.65832 | 0.64356 | 0.6467
43602.4244 | 0.99867 | 1.1313 | 1.0781 | 0.86218 | 0.73549 | 0.65932 | 0.64254 | 0.64725
43602.4244 | 1.0089 | 1.1318 | 1.0769 | 0.86159 | 0.73511 | 0.65922 | 0.64178 | 0.64732
43602.4244 | 1.0016 | 1.1294 | 1.0755 | 0.8603 | 0.73392 | 0.65802 | 0.64179 | 0.64649
43602.4244 | 1.0111 | 1.1347 | 1.0788 | 0.86324 | 0.73673 | 0.65968 | 0.64459 | 0.64718
43602.4244 | 1.0015 | 1.1289 | 1.0752 | 0.86021 | 0.73319 | 0.65763 | 0.64262 | 0.6466
43602.4244 | 0.99989 | 1.1293 | 1.0746 | 0.86007 | 0.73552 | 0.65948 | 0.64704 | 0.64721
43602.4245 | 0.99252 | 1.1298 | 1.0758 | 0.86078 | 0.73248 | 0.65728 | 0.64238 | 0.64634
43602.4245 | 1.002 | 1.1269 | 1.0731 | 0.85926 | 0.73507 | 0.65872 | 0.64245 | 0.64688
43602.4245 | 1.0029 | 1.1302 | 1.074 | 0.86018 | 0.73246 | 0.65686 | 0.64142 | 0.64642
43602.4245 | 1.0027 | 1.1275 | 1.0718 | 0.85871 | 0.73337 | 0.65768 | 0.64064 | 0.64659
43602.4245 | 1.0059 | 1.128 | 1.072 | 0.85926 | 0.73267 | 0.65717 | 0.64149 | 0.64659
43602.4245 | 0.99892 | 1.1252 | 1.0713 | 0.8586 | 0.73376 | 0.65795 | 0.64727 | 0.64692
43602.4245 | 0.98878 | 1.1248 | 1.0699 | 0.85706 | 0.73134 | 0.65631 | 0.64265 | 0.64669
43602.4245 | 0.97134 | 1.1252 | 1.0722 | 0.85857 | 0.73242 | 0.65731 | 0.64231 | 0.64687
43602.4245 | 0.99304 | 1.1271 | 1.073 | 0.85968 | 0.73257 | 0.65744 | 0.64208 | 0.64662
43602.4246 | 1.0073 | 1.1275 | 1.0715 | 0.8592 | 0.73411 | 0.65796 | 0.64073 | 0.64709
43602.4246 | 0.99962 | 1.1244 | 1.0695 | 0.85725 | 0.73248 | 0.65696 | 0.64082 | 0.6467
43602.4246 | 1.0119 | 1.128 | 1.0713 | 0.85978 | 0.73258 | 0.65693 | 0.64199 | 0.64694
43602.4246 | 1.0162 | 1.1307 | 1.0725 | 0.86036 | 0.73311 | 0.65763 | 0.64275 | 0.64727
43602.4246 | 1.0017 | 1.1282 | 1.0721 | 0.85964 | 0.73282 | 0.65735 | 0.64183 | 0.64681
43602.4246 | 0.97935 | 1.125 | 1.0716 | 0.8583 | 0.73501 | 0.65904 | 0.64941 | 0.64729
43602.4246 | 0.99626 | 1.129 | 1.0728 | 0.85959 | 0.73305 | 0.6579 | 0.64436 | 0.64675
43602.4246 | 1.0137 | 1.1336 | 1.0744 | 0.86208 | 0.73325 | 0.65779 | 0.64312 | 0.64692
43602.4246 | 1.0102 | 1.1269 | 1.0717 | 0.85946 | 0.73686 | 0.66024 | 0.64433 | 0.64789
43602.4247 | 1.0137 | 1.1347 | 1.0755 | 0.86262 | 0.73517 | 0.65912 | 0.64176 | 0.64732
43602.4247 | 1.0245 | 1.136 | 1.0756 | 0.8637 | 0.7363 | 0.65959 | 0.64249 | 0.64737
43602.4247 | 1.0052 | 1.1338 | 1.0767 | 0.86352 | 0.73832 | 0.66152 | 0.64578 | 0.64809
43602.4247 | 1.0112 | 1.1347 | 1.0767 | 0.86355 | 0.73755 | 0.66103 | 0.64663 | 0.64792
43602.4247 | 0.98746 | 1.1272 | 1.0736 | 0.86024 | 0.73499 | 0.65948 | 0.64738 | 0.6476
43602.4247 | 0.98968 | 1.136 | 1.0801 | 0.86568 | 0.73484 | 0.65945 | 0.64418 | 0.64756
43602.4247 | 0.98535 | 1.1282 | 1.0746 | 0.86087 | 0.73701 | 0.66124 | 0.64449 | 0.64787
43602.4247 | 1.0092 | 1.1352 | 1.0789 | 0.86491 | 0.73754 | 0.66126 | 0.64458 | 0.64815
43602.4247 | 1.0309 | 1.1426 | 1.0818 | 0.86829 | 0.74016 | 0.66311 | 0.64497 | 0.64897
43602.4248 | 1.0087 | 1.1352 | 1.0772 | 0.86379 | 0.73773 | 0.66133 | 0.64757 | 0.64813
43602.4248 | 0.99826 | 1.1317 | 1.0751 | 0.86188 | 0.73743 | 0.66102 | 0.64556 | 0.64842
43602.4248 | 1.0149 | 1.1362 | 1.0778 | 0.86459 | 0.7403 | 0.66317 | 0.64712 | 0.64932
43602.4248 | 1.0295 | 1.1424 | 1.0805 | 0.86793 | 0.73773 | 0.66112 | 0.64404 | 0.64853
43602.4248 | 1.0128 | 1.1367 | 1.0771 | 0.86436 | 0.74006 | 0.66312 | 0.64904 | 0.64923
43602.4248 | 1.0119 | 1.1321 | 1.0738 | 0.86148 | 0.73601 | 0.66007 | 0.64439 | 0.64836
43602.4248 | 1.0254 | 1.1341 | 1.0755 | 0.86352 | 0.73725 | 0.66073 | 0.64505 | 0.64867
43602.4248 | 1.0168 | 1.132 | 1.0743 | 0.86258 | 0.73596 | 0.65994 | 0.64418 | 0.64873
43602.4248 | 1.0066 | 1.1327 | 1.0752 | 0.86277 | 0.73649 | 0.6604 | 0.64481 | 0.64897
43602.4249 | 1.0043 | 1.1333 | 1.0749 | 0.86238 | 0.73665 | 0.66064 | 0.64572 | 0.64922
43602.4249 | 1.0052 | 1.1282 | 1.0715 | 0.85992 | 0.73534 | 0.65966 | 0.64402 | 0.64872
43602.4249 | 0.99476 | 1.1253 | 1.0705 | 0.85885 | 0.73557 | 0.6595 | 0.64863 | 0.64891
43602.4249 | 1.0049 | 1.1283 | 1.0721 | 0.86047 | 0.73378 | 0.65834 | 0.64582 | 0.64875
43602.4249 | 0.99583 | 1.1269 | 1.0711 | 0.85944 | 0.73424 | 0.65878 | 0.64495 | 0.64885
43602.4249 | 0.9864 | 1.1167 | 1.0638 | 0.853 | 0.73157 | 0.65666 | 0.64184 | 0.64828
43602.4249 | 0.99754 | 1.1232 | 1.0686 | 0.85835 | 0.73253 | 0.65734 | 0.64153 | 0.64856
43602.4249 | 0.98767 | 1.1199 | 1.0666 | 0.85635 | 0.7312 | 0.65658 | 0.63989 | 0.64833
43602.4249 | 0.96939 | 1.1182 | 1.0665 | 0.85483 | 0.73128 | 0.65683 | 0.64261 | 0.64841
43602.425 | 0.98577 | 1.1189 | 1.0658 | 0.85504 | 0.72783 | 0.6544 | 0.64018 | 0.64727
43602.425 | 0.9832 | 1.1144 | 1.062 | 0.85218 | 0.73008 | 0.65599 | 0.64107 | 0.64864
43602.425 | 0.98901 | 1.119 | 1.065 | 0.8548 | 0.73162 | 0.65675 | 0.64465 | 0.64878
43602.425 | 0.97271 | 1.1136 | 1.0625 | 0.85238 | 0.7259 | 0.65299 | 0.64294 | 0.64704
43602.425 | 0.9821 | 1.1118 | 1.0607 | 0.85104 | 0.72946 | 0.65517 | 0.6417 | 0.64825
43602.425 | 0.97703 | 1.1104 | 1.0589 | 0.84979 | 0.72493 | 0.65182 | 0.6387 | 0.64702
43602.425 | 0.98498 | 1.1145 | 1.0616 | 0.85285 | 0.7262 | 0.65265 | 0.63759 | 0.64753
43602.425 | 0.97666 | 1.1097 | 1.0589 | 0.8502 | 0.72699 | 0.65329 | 0.63721 | 0.64768
43602.425 | 0.98308 | 1.1089 | 1.0576 | 0.8491 | 0.7261 | 0.65254 | 0.63808 | 0.64762
43602.4251 | 0.98261 | 1.1105 | 1.0591 | 0.85083 | 0.72556 | 0.65227 | 0.63807 | 0.64749
43602.4251 | 0.97489 | 1.1095 | 1.0587 | 0.8503 | 0.72769 | 0.65382 | 0.63951 | 0.6481
43602.4251 | 0.97529 | 1.1059 | 1.0562 | 0.84739 | 0.72419 | 0.65137 | 0.63616 | 0.64685
43602.4251 | 0.97973 | 1.1061 | 1.0554 | 0.84756 | 0.72318 | 0.65059 | 0.63664 | 0.64684
43602.4251 | 0.98243 | 1.1093 | 1.0578 | 0.84986 | 0.72632 | 0.65288 | 0.64531 | 0.64798
43602.4251 | 0.97676 | 1.1037 | 1.0543 | 0.84682 | 0.72414 | 0.65109 | 0.63913 | 0.64738
43602.4251 | 0.98184 | 1.1103 | 1.0588 | 0.85153 | 0.72632 | 0.65264 | 0.63983 | 0.64831
43602.4251 | 0.94254 | 1.0995 | 1.0538 | 0.84525 | 0.72309 | 0.65045 | 0.6361 | 0.64693
43602.4251 | 0.96876 | 1.1041 | 1.0543 | 0.84664 | 0.72173 | 0.65005 | 0.63518 | 0.64708
43602.4252 | 0.97017 | 1.1033 | 1.0537 | 0.84653 | 0.72267 | 0.64994 | 0.63419 | 0.64689
43602.4252 | 0.95821 | 1.1031 | 1.0542 | 0.84666 | 0.72289 | 0.65013 | 0.63747 | 0.64691
43602.4252 | 0.951 | 1.1003 | 1.0527 | 0.84534 | 0.72187 | 0.64983 | 0.63652 | 0.64681
43602.4252 | 0.96647 | 1.1012 | 1.0516 | 0.84488 | 0.72284 | 0.65012 | 0.63585 | 0.64712
43602.4252 | 0.95606 | 1.0981 | 1.0494 | 0.84292 | 0.71983 | 0.64796 | 0.63854 | 0.64644
43602.4252 | 0.9494 | 1.0986 | 1.051 | 0.84486 | 0.72151 | 0.64953 | 0.63817 | 0.64717
43602.4252 | 0.96272 | 1.0955 | 1.0472 | 0.84239 | 0.71917 | 0.64788 | 0.63512 | 0.64667
43602.4252 | 0.96852 | 1.0981 | 1.0475 | 0.84351 | 0.71996 | 0.64828 | 0.63511 | 0.64695
43602.4252 | 0.96447 | 1.0965 | 1.0459 | 0.84149 | 0.71867 | 0.64702 | 0.63217 | 0.64644
43602.4253 | 0.95283 | 1.0897 | 1.0423 | 0.83866 | 0.71809 | 0.64663 | 0.63237 | 0.64645
43602.4253 | 0.9578 | 1.0903 | 1.0413 | 0.83768 | 0.71624 | 0.64514 | 0.63222 | 0.6458
43602.4253 | 0.95868 | 1.0921 | 1.0424 | 0.83988 | 0.71634 | 0.64522 | 0.63268 | 0.64606
43602.4253 | 0.94917 | 1.0855 | 1.038 | 0.83587 | 0.71703 | 0.64574 | 0.63638 | 0.64629
43602.4253 | 0.94329 | 1.0888 | 1.0406 | 0.83789 | 0.71331 | 0.64283 | 0.62992 | 0.64526
43602.4253 | 0.93663 | 1.0811 | 1.0351 | 0.83271 | 0.71271 | 0.64352 | 0.6303 | 0.6453
43602.4253 | 0.94926 | 1.0811 | 1.0335 | 0.83294 | 0.71314 | 0.64282 | 0.62882 | 0.64574
43602.4253 | 0.93909 | 1.0781 | 1.0316 | 0.8319 | 0.7114 | 0.64124 | 0.62806 | 0.64477
43602.4253 | 0.94112 | 1.0778 | 1.0299 | 0.83036 | 0.70982 | 0.64041 | 0.63225 | 0.64489
43602.4254 | 0.94864 | 1.0813 | 1.0322 | 0.83314 | 0.71034 | 0.64089 | 0.62973 | 0.64522
43602.4254 | 0.92598 | 1.0687 | 1.0242 | 0.82515 | 0.70832 | 0.63913 | 0.62738 | 0.64438
43602.4254 | 0.93531 | 1.0693 | 1.0236 | 0.82612 | 0.70539 | 0.63715 | 0.62395 | 0.644
43602.4254 | 0.93391 | 1.0707 | 1.0247 | 0.82706 | 0.70587 | 0.63702 | 0.62365 | 0.64371
43602.4254 | 0.93238 | 1.0696 | 1.0231 | 0.82584 | 0.70466 | 0.63626 | 0.62915 | 0.64351
43602.4254 | 0.94478 | 1.0719 | 1.023 | 0.82649 | 0.70541 | 0.63693 | 0.62889 | 0.6438
43602.4254 | 0.91823 | 1.0651 | 1.0208 | 0.82342 | 0.7055 | 0.63679 | 0.62697 | 0.64373
43602.4254 | 0.91407 | 1.0671 | 1.0225 | 0.82543 | 0.70368 | 0.636 | 0.62442 | 0.64334
43602.4254 | 0.93158 | 1.0686 | 1.021 | 0.82483 | 0.70491 | 0.63662 | 0.6234 | 0.64332
43602.4255 | 0.92337 | 1.0644 | 1.0191 | 0.8235 | 0.70299 | 0.63513 | 0.62182 | 0.64298
43602.4255 | 0.92313 | 1.0631 | 1.0181 | 0.82237 | 0.70361 | 0.63563 | 0.62461 | 0.64342
43602.4255 | 0.9383 | 1.0665 | 1.0189 | 0.82409 | 0.7013 | 0.63344 | 0.62336 | 0.64255
43602.4255 | 0.93244 | 1.065 | 1.018 | 0.82357 | 0.70422 | 0.63579 | 0.62779 | 0.64305
43602.4255 | 0.9455 | 1.0696 | 1.0209 | 0.82648 | 0.70339 | 0.63515 | 0.62328 | 0.64279
43602.4255 | 0.92654 | 1.0621 | 1.0161 | 0.82195 | 0.7063 | 0.63751 | 0.62529 | 0.64353
43602.4255 | 0.94212 | 1.0724 | 1.0224 | 0.82734 | 0.70461 | 0.63609 | 0.62292 | 0.64318
43602.4255 | 0.93557 | 1.063 | 1.0149 | 0.82108 | 0.70145 | 0.63379 | 0.62052 | 0.64226
43602.4255 | 0.93849 | 1.069 | 1.0213 | 0.82738 | 0.70441 | 0.63585 | 0.62362 | 0.64303
43602.4256 | 0.93752 | 1.0638 | 1.0167 | 0.82301 | 0.7034 | 0.6353 | 0.62418 | 0.64224
43602.4256 | 0.94313 | 1.0678 | 1.019 | 0.82543 | 0.7059 | 0.63718 | 0.63134 | 0.64337
43602.4256 | 0.94385 | 1.0667 | 1.0185 | 0.82484 | 0.70408 | 0.63571 | 0.62447 | 0.64248
43602.4256 | 0.95714 | 1.0713 | 1.0201 | 0.82673 | 0.7041 | 0.63599 | 0.6244 | 0.64269
43602.4256 | 0.95015 | 1.0682 | 1.0188 | 0.82527 | 0.70632 | 0.63734 | 0.62395 | 0.643
43602.4256 | 0.94786 | 1.067 | 1.0178 | 0.82467 | 0.70549 | 0.63677 | 0.62336 | 0.64296
43602.4256 | 0.94796 | 1.0666 | 1.0175 | 0.82419 | 0.7056 | 0.63683 | 0.6233 | 0.64286
43602.4256 | 0.96208 | 1.0713 | 1.0186 | 0.82565 | 0.70428 | 0.63593 | 0.62439 | 0.64239
43602.4257 | 0.94167 | 1.0649 | 1.0142 | 0.82152 | 0.70415 | 0.63582 | 0.62371 | 0.64244
43602.4257 | 0.93972 | 1.0635 | 1.0142 | 0.82217 | 0.7025 | 0.63468 | 0.62361 | 0.64186
43602.4257 | 0.9305 | 1.0596 | 1.0115 | 0.8202 | 0.70201 | 0.63413 | 0.62675 | 0.64187
43602.4257 | 0.94417 | 1.0624 | 1.0118 | 0.82131 | 0.70077 | 0.63325 | 0.62243 | 0.64175
43602.4257 | 0.94935 | 1.0639 | 1.0126 | 0.82237 | 0.70344 | 0.63526 | 0.62399 | 0.64249
43602.4257 | 0.93091 | 1.057 | 1.0088 | 0.81866 | 0.69887 | 0.63187 | 0.61848 | 0.641
43602.4257 | 0.95103 | 1.0642 | 1.0122 | 0.82248 | 0.7024 | 0.63443 | 0.62139 | 0.64219
43602.4257 | 0.9275 | 1.0551 | 1.0053 | 0.81654 | 0.69849 | 0.63157 | 0.62161 | 0.64097
43602.4257 | 0.94063 | 1.0567 | 1.0061 | 0.81811 | 0.69959 | 0.63245 | 0.62123 | 0.64139
43602.4258 | 0.94399 | 1.0556 | 1.0041 | 0.81658 | 0.69841 | 0.63101 | 0.62286 | 0.64087
43602.4258 | 0.92881 | 1.0555 | 1.006 | 0.81809 | 0.69718 | 0.63033 | 0.61994 | 0.64062
43602.4258 | 0.91695 | 1.0452 | 0.99814 | 0.8113 | 0.6969 | 0.63022 | 0.61917 | 0.64062
43602.4258 | 0.94179 | 1.0585 | 1.0054 | 0.81845 | 0.6959 | 0.62937 | 0.61751 | 0.6406
43602.4258 | 0.93605 | 1.0517 | 1.0012 | 0.81483 | 0.69775 | 0.63069 | 0.61981 | 0.64085
43602.4258 | 0.93537 | 1.0491 | 0.99908 | 0.81325 | 0.69632 | 0.62962 | 0.62068 | 0.6406
43602.4258 | 0.94171 | 1.0522 | 0.99962 | 0.81379 | 0.69418 | 0.62801 | 0.61681 | 0.63998
43602.4258 | 0.9291 | 1.0562 | 1.0049 | 0.81782 | 0.69792 | 0.631 | 0.61845 | 0.6408
43602.4258 | 0.92804 | 1.045 | 0.99605 | 0.80995 | 0.69486 | 0.62908 | 0.61929 | 0.63998
43602.4259 | 0.95818 | 1.0635 | 1.0068 | 0.8195 | 0.69721 | 0.63065 | 0.61849 | 0.64044
43602.4259 | 0.94588 | 1.0541 | 1.0013 | 0.81456 | 0.69786 | 0.63095 | 0.6187 | 0.6403
43602.4259 | 0.95034 | 1.0616 | 1.0061 | 0.81872 | 0.69883 | 0.63207 | 0.62181 | 0.6409
43602.4259 | 0.95669 | 1.0623 | 1.0064 | 0.8188 | 0.69778 | 0.63088 | 0.62575 | 0.64041
43602.4259 | 0.95465 | 1.0626 | 1.0078 | 0.81995 | 0.70378 | 0.63534 | 0.62479 | 0.64214
43602.4259 | 0.95276 | 1.0627 | 1.0074 | 0.81956 | 0.69729 | 0.6309 | 0.61928 | 0.64044
43602.4259 | 0.95224 | 1.0666 | 1.0108 | 0.82247 | 0.70313 | 0.63516 | 0.6225 | 0.64141
43602.4259 | 0.9813 | 1.0762 | 1.0156 | 0.8272 | 0.70389 | 0.63554 | 0.6213 | 0.64172
43602.4259 | 0.95186 | 1.0654 | 1.0101 | 0.82082 | 0.70505 | 0.63613 | 0.62191 | 0.64143
43602.426 | 0.96134 | 1.0675 | 1.0114 | 0.82267 | 0.70507 | 0.63682 | 0.62541 | 0.64212
43602.426 | 0.98634 | 1.0794 | 1.0181 | 0.82835 | 0.70243 | 0.6349 | 0.62252 | 0.64152
43602.426 | 0.97057 | 1.0738 | 1.0156 | 0.82624 | 0.70979 | 0.64003 | 0.62573 | 0.64318
43602.426 | 0.97422 | 1.0746 | 1.0152 | 0.82586 | 0.70522 | 0.63696 | 0.62776 | 0.6421
43602.426 | 0.96502 | 1.0733 | 1.0158 | 0.8263 | 0.70817 | 0.63909 | 0.62665 | 0.64299
43602.426 | 0.97814 | 1.0785 | 1.0182 | 0.82859 | 0.70776 | 0.63889 | 0.6264 | 0.64277
43602.426 | 0.95302 | 1.073 | 1.0168 | 0.8263 | 0.70641 | 0.63788 | 0.62494 | 0.64238
43602.426 | 0.94742 | 1.0709 | 1.0164 | 0.82564 | 0.70543 | 0.63715 | 0.62525 | 0.6419
43602.426 | 0.92906 | 1.0654 | 1.0144 | 0.82378 | 0.70542 | 0.63744 | 0.62625 | 0.64242
43602.4261 | 0.96302 | 1.0719 | 1.0151 | 0.82471 | 0.70356 | 0.63567 | 0.6236 | 0.64174
43602.4261 | 0.955 | 1.0679 | 1.0128 | 0.82311 | 0.70491 | 0.63656 | 0.62414 | 0.64224
43602.4261 | 0.96359 | 1.0756 | 1.0181 | 0.82789 | 0.70659 | 0.63771 | 0.62614 | 0.64289
43602.4261 | 0.93856 | 1.062 | 1.0106 | 0.82079 | 0.7033 | 0.63561 | 0.62153 | 0.64219
43602.4261 | 0.96783 | 1.0791 | 1.0212 | 0.82939 | 0.70943 | 0.64002 | 0.62643 | 0.64359
43602.4261 | 0.94151 | 1.0669 | 1.0136 | 0.82264 | 0.70034 | 0.63338 | 0.62749 | 0.64119
43602.4261 | 0.95879 | 1.07 | 1.0147 | 0.82465 | 0.70608 | 0.63745 | 0.62708 | 0.64297
43602.4261 | 0.93731 | 1.0602 | 1.008 | 0.81846 | 0.70037 | 0.63306 | 0.62168 | 0.64122
43602.4261 | 0.96107 | 1.0699 | 1.0138 | 0.82359 | 0.70264 | 0.63496 | 0.62297 | 0.64216
43602.4262 | 0.93154 | 1.0541 | 1.0043 | 0.815 | 0.69888 | 0.63137 | 0.61812 | 0.641
43602.4262 | 0.93219 | 1.0581 | 1.0074 | 0.81839 | 0.69861 | 0.63165 | 0.61926 | 0.64153
43602.4262 | 0.94119 | 1.0589 | 1.0078 | 0.81852 | 0.69932 | 0.63201 | 0.62074 | 0.64192
43602.4262 | 0.93238 | 1.0546 | 1.0041 | 0.81523 | 0.6986 | 0.63133 | 0.62056 | 0.64159
43602.4262 | 0.92832 | 1.0529 | 1.0032 | 0.81446 | 0.69588 | 0.62931 | 0.62495 | 0.64071
43602.4262 | 0.93995 | 1.0597 | 1.0087 | 0.81937 | 0.69837 | 0.63146 | 0.62138 | 0.64198
43602.4262 | 0.91545 | 1.0474 | 1.0011 | 0.81141 | 0.69562 | 0.62919 | 0.61839 | 0.64103
43602.4262 | 0.92108 | 1.0527 | 1.0053 | 0.81582 | 0.69505 | 0.62887 | 0.61785 | 0.64108
43602.4262 | 0.92182 | 1.0466 | 0.9997 | 0.81113 | 0.69537 | 0.62902 | 0.61685 | 0.64113
43602.4263 | 0.92625 | 1.0508 | 1.0015 | 0.81294 | 0.69313 | 0.62704 | 0.61502 | 0.64046
43602.4263 | 0.90633 | 1.0409 | 0.99531 | 0.80717 | 0.69246 | 0.62671 | 0.61678 | 0.64058
43602.4263 | 0.91511 | 1.0452 | 0.99829 | 0.81071 | 0.69053 | 0.62531 | 0.61499 | 0.64031
43602.4263 | 0.91304 | 1.0438 | 0.99683 | 0.80959 | 0.69034 | 0.62527 | 0.614 | 0.64033
43602.4263 | 0.90232 | 1.0372 | 0.99259 | 0.80608 | 0.69169 | 0.62613 | 0.61683 | 0.64078
43602.4263 | 0.90536 | 1.042 | 0.99663 | 0.81001 | 0.68985 | 0.62483 | 0.61486 | 0.64055
43602.4263 | 0.90509 | 1.0391 | 0.99434 | 0.80784 | 0.69107 | 0.62542 | 0.61568 | 0.64102
43602.4263 | 0.89523 | 1.034 | 0.99184 | 0.80482 | 0.68721 | 0.62266 | 0.61217 | 0.63993
43602.4263 | 0.89363 | 1.0351 | 0.99231 | 0.80599 | 0.68806 | 0.62313 | 0.61709 | 0.64034
43602.4264 | 0.896 | 1.0342 | 0.99039 | 0.80414 | 0.68708 | 0.6228 | 0.61378 | 0.64025
43602.4264 | 0.8931 | 1.0319 | 0.98859 | 0.80335 | 0.68554 | 0.62157 | 0.61232 | 0.63981
43602.4264 | 0.89069 | 1.0334 | 0.98987 | 0.80418 | 0.6847 | 0.62071 | 0.61179 | 0.63979
43602.4264 | 0.89702 | 1.037 | 0.99321 | 0.80734 | 0.68905 | 0.62389 | 0.61274 | 0.64106
43602.4264 | 0.8878 | 1.029 | 0.9864 | 0.80067 | 0.68492 | 0.62116 | 0.61129 | 0.63985
43602.4264 | 0.89118 | 1.0342 | 0.99143 | 0.80597 | 0.6855 | 0.62149 | 0.61821 | 0.64037
43602.4264 | 0.88169 | 1.0289 | 0.98777 | 0.80107 | 0.68595 | 0.62234 | 0.6148 | 0.64089
43602.4264 | 0.89033 | 1.0316 | 0.9884 | 0.8034 | 0.6832 | 0.62014 | 0.61111 | 0.63997
43602.4264 | 0.87996 | 1.0297 | 0.98893 | 0.80276 | 0.686 | 0.62213 | 0.61208 | 0.64069
43602.4265 | 0.88133 | 1.0277 | 0.98655 | 0.80076 | 0.68366 | 0.62064 | 0.60935 | 0.64028
43602.4265 | 0.90043 | 1.0353 | 0.99042 | 0.80634 | 0.68522 | 0.62126 | 0.61128 | 0.64096
43602.4265 | 0.88491 | 1.029 | 0.98692 | 0.80175 | 0.68628 | 0.62229 | 0.61561 | 0.64098
43602.4265 | 0.88441 | 1.0304 | 0.98769 | 0.80214 | 0.68441 | 0.62111 | 0.61232 | 0.64084
43602.4265 | 0.87759 | 1.0261 | 0.98454 | 0.79917 | 0.68338 | 0.62051 | 0.61099 | 0.64043
43602.4265 | 0.88307 | 1.029 | 0.98716 | 0.80219 | 0.68339 | 0.62055 | 0.61101 | 0.64083
43602.4265 | 0.88748 | 1.0297 | 0.98757 | 0.80296 | 0.68497 | 0.62143 | 0.61161 | 0.64115
43602.4265 | 0.87718 | 1.0263 | 0.98622 | 0.8011 | 0.6836 | 0.62046 | 0.61145 | 0.64082
43602.4265 | 0.87713 | 1.0274 | 0.98747 | 0.80171 | 0.68384 | 0.62081 | 0.61184 | 0.64098
43602.4266 | 0.88679 | 1.0296 | 0.98671 | 0.80195 | 0.68391 | 0.62085 | 0.61261 | 0.64119
43602.4266 | 0.88454 | 1.031 | 0.98888 | 0.80407 | 0.68581 | 0.62223 | 0.61328 | 0.64183
43602.4266 | 0.87541 | 1.024 | 0.98435 | 0.79848 | 0.68341 | 0.62054 | 0.61076 | 0.64105
43602.4266 | 0.88102 | 1.0277 | 0.98582 | 0.80164 | 0.68218 | 0.61953 | 0.60977 | 0.64087
43602.4266 | 0.88403 | 1.0283 | 0.986 | 0.80128 | 0.68442 | 0.62116 | 0.62077 | 0.64172
43602.4266 | 0.88061 | 1.0283 | 0.98685 | 0.80252 | 0.6843 | 0.62142 | 0.61502 | 0.64181
43602.4266 | 0.86948 | 1.0228 | 0.98352 | 0.79754 | 0.6824 | 0.61993 | 0.61244 | 0.64102
43602.4266 | 0.88044 | 1.0272 | 0.98591 | 0.80136 | 0.68202 | 0.61952 | 0.61089 | 0.641
43602.4266 | 0.87345 | 1.0254 | 0.98487 | 0.79984 | 0.68449 | 0.62093 | 0.61027 | 0.64152
43602.4267 | 0.87759 | 1.0249 | 0.98344 | 0.79884 | 0.68119 | 0.61905 | 0.60865 | 0.64088
43602.4267 | 0.87923 | 1.0263 | 0.98397 | 0.79995 | 0.68244 | 0.61976 | 0.61004 | 0.64126
43602.4267 | 0.88119 | 1.0283 | 0.98647 | 0.80208 | 0.6827 | 0.61998 | 0.61223 | 0.64143
43602.4267 | 0.87834 | 1.0274 | 0.98612 | 0.80127 | 0.68616 | 0.62255 | 0.61259 | 0.64294
43602.4267 | 0.88007 | 1.0269 | 0.98555 | 0.80125 | 0.68258 | 0.62027 | 0.60943 | 0.6416
43602.4267 | 0.87664 | 1.0259 | 0.98495 | 0.80046 | 0.68434 | 0.62126 | 0.61733 | 0.64246
43602.4267 | 0.87321 | 1.0257 | 0.98571 | 0.80016 | 0.68262 | 0.62046 | 0.61527 | 0.64193
43602.4267 | 0.87193 | 1.0252 | 0.98528 | 0.79946 | 0.68318 | 0.6209 | 0.61313 | 0.64215
43602.4267 | 0.87728 | 1.0275 | 0.98613 | 0.80201 | 0.68325 | 0.62108 | 0.61218 | 0.64238
43602.4268 | 0.86476 | 1.0242 | 0.98601 | 0.79944 | 0.68412 | 0.62179 | 0.61137 | 0.64294
43602.4268 | 0.88046 | 1.0296 | 0.98745 | 0.80349 | 0.6837 | 0.62178 | 0.61138 | 0.64311
43602.4268 | 0.87449 | 1.0279 | 0.98652 | 0.80171 | 0.68594 | 0.623 | 0.61291 | 0.64373
43602.4268 | 0.87202 | 1.0281 | 0.9881 | 0.80238 | 0.68437 | 0.62216 | 0.6132 | 0.64314
43602.4268 | 0.88008 | 1.03 | 0.98832 | 0.80265 | 0.68606 | 0.62345 | 0.61467 | 0.64405
43602.4268 | 0.87285 | 1.0289 | 0.98933 | 0.80219 | 0.68555 | 0.62328 | 0.61359 | 0.64396
43602.4268 | 0.87495 | 1.0305 | 0.99084 | 0.80374 | 0.68519 | 0.62328 | 0.6172 | 0.6439
43602.4268 | 0.88348 | 1.0335 | 0.99135 | 0.80507 | 0.68894 | 0.62533 | 0.61692 | 0.64528
43602.4268 | 0.88741 | 1.0348 | 0.99232 | 0.80583 | 0.68682 | 0.62409 | 0.61542 | 0.64422
43602.4269 | 0.89354 | 1.0409 | 0.99698 | 0.81161 | 0.69264 | 0.62802 | 0.61755 | 0.64612
43602.4269 | 0.87574 | 1.0322 | 0.99293 | 0.80356 | 0.68986 | 0.62654 | 0.61677 | 0.64505
43602.4269 | 0.87929 | 1.0337 | 0.99295 | 0.80518 | 0.68743 | 0.625 | 0.61449 | 0.64509
43602.4269 | 0.87405 | 1.0362 | 0.99679 | 0.80908 | 0.69037 | 0.62729 | 0.61744 | 0.64603
43602.4269 | 0.88006 | 1.0381 | 0.99611 | 0.809 | 0.69137 | 0.628 | 0.62681 | 0.64661
43602.4269 | 0.87916 | 1.0359 | 0.99469 | 0.80719 | 0.69094 | 0.62735 | 0.62027 | 0.64621
43602.4269 | 0.87531 | 1.0316 | 0.99253 | 0.80441 | 0.68887 | 0.62616 | 0.61841 | 0.64557
43602.4269 | 0.87336 | 1.0322 | 0.99278 | 0.8041 | 0.68758 | 0.62526 | 0.61713 | 0.64572
43602.4269 | 0.87464 | 1.0329 | 0.99307 | 0.80642 | 0.68918 | 0.62696 | 0.61675 | 0.64665
43602.427 | 0.86699 | 1.0265 | 0.98965 | 0.80074 | 0.68749 | 0.6258 | 0.61548 | 0.64634
43602.427 | 0.8647 | 1.0269 | 0.98946 | 0.80141 | 0.68507 | 0.62438 | 0.61531 | 0.64609
43602.427 | 0.87586 | 1.0322 | 0.99142 | 0.80597 | 0.68803 | 0.62583 | 0.61671 | 0.64711
43602.427 | 0.86615 | 1.0288 | 0.99093 | 0.8031 | 0.68941 | 0.62667 | 0.61601 | 0.64747
43602.427 | 0.86362 | 1.0241 | 0.98734 | 0.79981 | 0.68557 | 0.62482 | 0.61385 | 0.6464
43602.427 | 0.86328 | 1.0237 | 0.98646 | 0.80096 | 0.68565 | 0.62488 | 0.61738 | 0.64706
43602.427 | 0.85896 | 1.0191 | 0.98514 | 0.79708 | 0.68434 | 0.62419 | 0.61532 | 0.64698
43602.427 | 0.85949 | 1.0195 | 0.983 | 0.79721 | 0.68273 | 0.62313 | 0.61472 | 0.64671
43602.4271 | 0.85242 | 1.0167 | 0.98378 | 0.7966 | 0.68353 | 0.62371 | 0.61398 | 0.64755
43602.4271 | 0.85057 | 1.0143 | 0.98197 | 0.7957 | 0.68199 | 0.62254 | 0.61668 | 0.64695
43602.4271 | 0.85451 | 1.0144 | 0.98095 | 0.79504 | 0.68233 | 0.62311 | 0.61465 | 0.64743
43602.4271 | 0.85029 | 1.016 | 0.98288 | 0.79609 | 0.68286 | 0.62299 | 0.61433 | 0.64776
43602.4271 | 0.85402 | 1.0157 | 0.98124 | 0.79636 | 0.68246 | 0.623 | 0.61377 | 0.64746
43602.4271 | 0.84456 | 1.0085 | 0.97943 | 0.79283 | 0.68174 | 0.62264 | 0.61281 | 0.64771
43602.4271 | 0.83965 | 1.0066 | 0.97852 | 0.79174 | 0.68001 | 0.62183 | 0.61493 | 0.64758
43602.4271 | 0.84623 | 1.0088 | 0.97758 | 0.79211 | 0.68003 | 0.62179 | 0.61726 | 0.64798
43602.4271 | 0.84309 | 1.0065 | 0.97704 | 0.7921 | 0.6799 | 0.62121 | 0.61297 | 0.64765
43602.4272 | 0.8459 | 1.0085 | 0.97762 | 0.79307 | 0.6804 | 0.62204 | 0.61315 | 0.64805
43602.4272 | 0.84539 | 1.0092 | 0.97858 | 0.79337 | 0.68047 | 0.62197 | 0.61326 | 0.6481
43602.4272 | 0.84357 | 1.0084 | 0.97744 | 0.79286 | 0.68088 | 0.62226 | 0.61317 | 0.64805
43602.4272 | 0.84365 | 1.0073 | 0.97735 | 0.79274 | 0.68098 | 0.62217 | 0.61361 | 0.64821
43602.4272 | 0.84685 | 1.0096 | 0.97828 | 0.79297 | 0.68033 | 0.62188 | 0.61283 | 0.64811
43602.4272 | 0.85123 | 1.0109 | 0.97788 | 0.79471 | 0.68158 | 0.62253 | 0.61984 | 0.64848
43602.4272 | 0.84926 | 1.0097 | 0.97767 | 0.79307 | 0.68136 | 0.62248 | 0.61567 | 0.64799
43602.4272 | 0.84786 | 1.0095 | 0.97767 | 0.79311 | 0.68066 | 0.62232 | 0.61515 | 0.6482
43602.4272 | 0.83711 | 1.0075 | 0.97972 | 0.79292 | 0.68068 | 0.62233 | 0.61326 | 0.64803
43602.4273 | 0.8489 | 1.0125 | 0.97951 | 0.79558 | 0.68184 | 0.62292 | 0.61294 | 0.64877
43602.4273 | 0.84439 | 1.0097 | 0.97917 | 0.79343 | 0.68161 | 0.62272 | 0.6122 | 0.64834
43602.4273 | 0.84519 | 1.0103 | 0.97922 | 0.79416 | 0.6812 | 0.62252 | 0.61511 | 0.6481
43602.4273 | 0.84961 | 1.0133 | 0.97917 | 0.79612 | 0.68256 | 0.62312 | 0.61506 | 0.64849
43602.4273 | 0.8443 | 1.0106 | 0.98122 | 0.79531 | 0.68246 | 0.62293 | 0.61394 | 0.64822
43602.4273 | 0.85094 | 1.0136 | 0.98125 | 0.79602 | 0.68264 | 0.62306 | 0.61805 | 0.64847
43602.4273 | 0.84937 | 1.0144 | 0.98157 | 0.79662 | 0.68293 | 0.62342 | 0.61786 | 0.64845
43602.4273 | 0.84835 | 1.0146 | 0.98352 | 0.7974 | 0.68364 | 0.62399 | 0.61576 | 0.64854
43602.4273 | 0.84452 | 1.015 | 0.98418 | 0.79861 | 0.68433 | 0.62441 | 0.61555 | 0.64867
43602.4274 | 0.85343 | 1.0179 | 0.98396 | 0.79814 | 0.68459 | 0.62449 | 0.61439 | 0.64851
43602.4274 | 0.85504 | 1.019 | 0.98407 | 0.79919 | 0.68539 | 0.62481 | 0.61547 | 0.64866
43602.4274 | 0.84925 | 1.015 | 0.98462 | 0.79625 | 0.68454 | 0.62454 | 0.61586 | 0.64818
43602.4274 | 0.85304 | 1.019 | 0.98513 | 0.79973 | 0.68451 | 0.62482 | 0.61581 | 0.64849
43602.4274 | 0.85977 | 1.0229 | 0.98701 | 0.80129 | 0.68735 | 0.6264 | 0.61569 | 0.64942
43602.4274 | 0.86181 | 1.0227 | 0.98555 | 0.80079 | 0.6869 | 0.62593 | 0.62097 | 0.64897
43602.4274 | 0.86343 | 1.0224 | 0.98598 | 0.80043 | 0.68622 | 0.6254 | 0.61729 | 0.64854
43602.4274 | 0.8635 | 1.0258 | 0.98891 | 0.80273 | 0.68757 | 0.6265 | 0.61815 | 0.64915
43602.4274 | 0.86387 | 1.0261 | 0.98909 | 0.80365 | 0.68889 | 0.62735 | 0.61674 | 0.64951
43602.4275 | 0.85881 | 1.025 | 0.98943 | 0.80172 | 0.6881 | 0.62702 | 0.61832 | 0.64921
43602.4275 | 0.8553 | 1.0235 | 0.9897 | 0.80148 | 0.68762 | 0.62676 | 0.6175 | 0.64898
43602.4275 | 0.85974 | 1.0261 | 0.98909 | 0.80313 | 0.68805 | 0.62727 | 0.61852 | 0.64942
43602.4275 | 0.86195 | 1.0259 | 0.98858 | 0.80175 | 0.68805 | 0.62696 | 0.61763 | 0.6491
43602.4275 | 0.86261 | 1.0272 | 0.98987 | 0.80386 | 0.68862 | 0.62725 | 0.62215 | 0.6492
43602.4275 | 0.86646 | 1.0289 | 0.9907 | 0.80422 | 0.68962 | 0.6277 | 0.62217 | 0.64942
43602.4275 | 0.86606 | 1.0292 | 0.99013 | 0.8047 | 0.68918 | 0.62794 | 0.61906 | 0.64915
43602.4275 | 0.87017 | 1.0307 | 0.99107 | 0.80402 | 0.68995 | 0.62814 | 0.61877 | 0.64947
43602.4275 | 0.87615 | 1.0343 | 0.99263 | 0.8073 | 0.6906 | 0.62862 | 0.61815 | 0.64957
43602.4276 | 0.86456 | 1.031 | 0.99361 | 0.80578 | 0.69232 | 0.62935 | 0.61907 | 0.65004
43602.4276 | 0.86833 | 1.03 | 0.99108 | 0.80423 | 0.68961 | 0.62816 | 0.61813 | 0.64912
43602.4276 | 0.8743 | 1.0342 | 0.99308 | 0.80716 | 0.6908 | 0.62867 | 0.62084 | 0.64957
43602.4276 | 0.87112 | 1.0331 | 0.99456 | 0.80699 | 0.69352 | 0.6304 | 0.6219 | 0.6504
43602.4276 | 0.87103 | 1.0325 | 0.99336 | 0.80657 | 0.69078 | 0.62887 | 0.61901 | 0.64939
43602.4276 | 0.87164 | 1.0324 | 0.99334 | 0.80565 | 0.69285 | 0.63011 | 0.62107 | 0.65043
43602.4276 | 0.86883 | 1.0282 | 0.99005 | 0.80218 | 0.68898 | 0.62787 | 0.61804 | 0.64902
43602.4276 | 0.86392 | 1.0291 | 0.99175 | 0.80499 | 0.68926 | 0.62828 | 0.61786 | 0.64951
43602.4276 | 0.87274 | 1.0318 | 0.99146 | 0.80574 | 0.69073 | 0.62901 | 0.62677 | 0.65002
43602.4277 | 0.86877 | 1.0302 | 0.991 | 0.8052 | 0.69108 | 0.6292 | 0.62152 | 0.65013
43602.4277 | 0.8657 | 1.0272 | 0.99024 | 0.80326 | 0.68971 | 0.62837 | 0.62056 | 0.64963
43602.4277 | 0.86549 | 1.0279 | 0.98947 | 0.80395 | 0.68971 | 0.62849 | 0.61863 | 0.6501
43602.4277 | 0.86259 | 1.0261 | 0.98957 | 0.80319 | 0.68959 | 0.62849 | 0.61792 | 0.65014
43602.4277 | 0.86479 | 1.0275 | 0.99003 | 0.80317 | 0.68929 | 0.62834 | 0.61916 | 0.65031
43602.4277 | 0.86796 | 1.0297 | 0.99066 | 0.80576 | 0.69041 | 0.62902 | 0.61992 | 0.65067
43602.4277 | 0.85833 | 1.0233 | 0.98889 | 0.8005 | 0.68992 | 0.62888 | 0.61942 | 0.65051
43602.4277 | 0.86082 | 1.023 | 0.98658 | 0.80007 | 0.68695 | 0.62719 | 0.61727 | 0.65002
43602.4277 | 0.85858 | 1.024 | 0.98821 | 0.80162 | 0.68786 | 0.62794 | 0.61936 | 0.65041
43602.4278 | 0.85917 | 1.0237 | 0.98846 | 0.80229 | 0.68853 | 0.62834 | 0.62622 | 0.65073
43602.4278 | 0.86183 | 1.0251 | 0.98845 | 0.80285 | 0.6888 | 0.62805 | 0.62047 | 0.65058
43602.4278 | 0.8534 | 1.0221 | 0.98888 | 0.80143 | 0.68916 | 0.62846 | 0.61969 | 0.6508
43602.4278 | 0.85201 | 1.0204 | 0.98781 | 0.79888 | 0.6873 | 0.62773 | 0.61783 | 0.65037
43602.4278 | 0.86732 | 1.0269 | 0.98858 | 0.80241 | 0.68793 | 0.62806 | 0.61822 | 0.65088
43602.4278 | 0.86585 | 1.0267 | 0.98995 | 0.8027 | 0.68997 | 0.62874 | 0.61955 | 0.65115
43602.4278 | 0.85903 | 1.0215 | 0.9869 | 0.79953 | 0.68764 | 0.6276 | 0.61896 | 0.65015
43602.4278 | 0.85872 | 1.0212 | 0.98691 | 0.79932 | 0.68727 | 0.62728 | 0.6171 | 0.65054
43602.4278 | 0.85772 | 1.0197 | 0.98583 | 0.79826 | 0.687 | 0.62718 | 0.61767 | 0.65063
43602.4279 | 0.85574 | 1.0211 | 0.98727 | 0.7992 | 0.68653 | 0.62686 | 0.61875 | 0.65073
43602.4279 | 0.86003 | 1.0234 | 0.9883 | 0.80056 | 0.68753 | 0.6278 | 0.62316 | 0.65118
43602.4279 | 0.86136 | 1.0253 | 0.9883 | 0.80316 | 0.68874 | 0.62817 | 0.62342 | 0.65106
43602.4279 | 0.85642 | 1.0239 | 0.99094 | 0.80196 | 0.69013 | 0.6292 | 0.62073 | 0.65154
43602.4279 | 0.86477 | 1.0262 | 0.98993 | 0.80298 | 0.68931 | 0.6288 | 0.61984 | 0.65127
43602.4279 | 0.8613 | 1.0242 | 0.98989 | 0.80176 | 0.68923 | 0.62878 | 0.61877 | 0.65131
43602.4279 | 0.86033 | 1.0247 | 0.99056 | 0.80128 | 0.68887 | 0.62874 | 0.61785 | 0.65123
43602.4279 | 0.8603 | 1.024 | 0.99003 | 0.80083 | 0.68828 | 0.62837 | 0.61983 | 0.65117
43602.4279 | 0.85872 | 1.0238 | 0.99053 | 0.80102 | 0.68851 | 0.62846 | 0.61923 | 0.65128
43602.428 | 0.86508 | 1.0269 | 0.99208 | 0.80227 | 0.68938 | 0.62903 | 0.61938 | 0.65163
43602.428 | 0.86084 | 1.026 | 0.99213 | 0.80263 | 0.68937 | 0.62935 | 0.62209 | 0.6516
43602.428 | 0.85906 | 1.0257 | 0.99233 | 0.80302 | 0.68995 | 0.62967 | 0.6209 | 0.65208
43602.428 | 0.85894 | 1.0247 | 0.99267 | 0.80156 | 0.68975 | 0.6296 | 0.6205 | 0.65172
43602.428 | 0.85429 | 1.0226 | 0.99079 | 0.80057 | 0.68879 | 0.62935 | 0.62037 | 0.65179
43602.428 | 0.85119 | 1.0221 | 0.99208 | 0.80075 | 0.68902 | 0.62928 | 0.62468 | 0.65184
43602.428 | 0.85427 | 1.0224 | 0.99172 | 0.80027 | 0.68847 | 0.62889 | 0.62071 | 0.65158
43602.428 | 0.85791 | 1.0244 | 0.99194 | 0.80186 | 0.68869 | 0.62909 | 0.6204 | 0.65194
43602.428 | 0.86226 | 1.0271 | 0.9932 | 0.80271 | 0.69018 | 0.62963 | 0.61947 | 0.65204
43602.4281 | 0.8534 | 1.0237 | 0.99405 | 0.80183 | 0.68985 | 0.6296 | 0.61953 | 0.65202
43602.4281 | 0.85444 | 1.0247 | 0.99327 | 0.80128 | 0.68911 | 0.6295 | 0.61955 | 0.65206
43602.4281 | 0.86192 | 1.0272 | 0.99329 | 0.80213 | 0.6898 | 0.62973 | 0.62099 | 0.65222
43602.4281 | 0.86395 | 1.026 | 0.99276 | 0.80122 | 0.68936 | 0.6294 | 0.62517 | 0.65197
43602.4281 | 0.85533 | 1.0218 | 0.9919 | 0.79983 | 0.6886 | 0.62899 | 0.61971 | 0.6518
43602.4281 | 0.85154 | 1.0213 | 0.99209 | 0.79898 | 0.68799 | 0.62891 | 0.61988 | 0.65194
43602.4281 | 0.8561 | 1.0228 | 0.99198 | 0.80043 | 0.68852 | 0.62914 | 0.62038 | 0.652
43602.4281 | 0.85562 | 1.0246 | 0.99366 | 0.8017 | 0.68939 | 0.62972 | 0.62098 | 0.65229
43602.4281 | 0.86252 | 1.0255 | 0.99284 | 0.80105 | 0.68944 | 0.62978 | 0.61992 | 0.65242
43602.4282 | 0.84817 | 1.0208 | 0.99354 | 0.80019 | 0.68877 | 0.62928 | 0.6211 | 0.65221
43602.4282 | 0.8565 | 1.0232 | 0.99327 | 0.80025 | 0.6891 | 0.62987 | 0.62058 | 0.65257
43602.4282 | 0.85997 | 1.0238 | 0.99392 | 0.80082 | 0.68901 | 0.62946 | 0.62094 | 0.65233
43602.4282 | 0.85915 | 1.0267 | 0.99537 | 0.80312 | 0.68974 | 0.62986 | 0.62427 | 0.65237
43602.4282 | 0.85542 | 1.0258 | 0.99545 | 0.80368 | 0.69109 | 0.63061 | 0.62183 | 0.65306
43602.4282 | 0.86281 | 1.0264 | 0.99567 | 0.80165 | 0.68999 | 0.63023 | 0.62107 | 0.65286
43602.4282 | 0.85903 | 1.0254 | 0.9965 | 0.80066 | 0.68958 | 0.63001 | 0.62033 | 0.65235
43602.4282 | 0.8596 | 1.0286 | 0.99666 | 0.80416 | 0.68998 | 0.6305 | 0.62121 | 0.65275
43602.4282 | 0.8546 | 1.0273 | 0.99883 | 0.80362 | 0.69138 | 0.63104 | 0.62126 | 0.65304
43602.4283 | 0.85491 | 1.0276 | 0.99888 | 0.80338 | 0.69119 | 0.63104 | 0.62179 | 0.65287
43602.4283 | 0.86028 | 1.0284 | 0.99828 | 0.804 | 0.69175 | 0.63145 | 0.62619 | 0.65337
43602.4283 | 0.85828 | 1.028 | 0.99915 | 0.80262 | 0.69118 | 0.6311 | 0.62242 | 0.65304
43602.4283 | 0.85256 | 1.0256 | 0.99926 | 0.80217 | 0.69088 | 0.63092 | 0.62256 | 0.65311
43602.4283 | 0.8572 | 1.0297 | 1.0007 | 0.80418 | 0.69149 | 0.63167 | 0.62194 | 0.65349
43602.4283 | 0.85479 | 1.0295 | 1.0022 | 0.80555 | 0.69283 | 0.63256 | 0.6219 | 0.65381
43602.4283 | 0.85629 | 1.0301 | 1.0014 | 0.80455 | 0.69313 | 0.63285 | 0.62284 | 0.65382
43602.4283 | 0.85603 | 1.0278 | 1.0008 | 0.80343 | 0.69198 | 0.63214 | 0.62547 | 0.65358
43602.4283 | 0.8559 | 1.0259 | 0.99965 | 0.80158 | 0.69121 | 0.63148 | 0.62129 | 0.65336
43602.4284 | 0.85383 | 1.0251 | 0.99944 | 0.80178 | 0.69058 | 0.63138 | 0.62069 | 0.6532
43602.4284 | 0.85437 | 1.0252 | 0.99955 | 0.80144 | 0.6909 | 0.63147 | 0.62527 | 0.65339
43602.4284 | 0.85728 | 1.0262 | 0.99832 | 0.80273 | 0.69064 | 0.63119 | 0.62423 | 0.65384
43602.4284 | 0.85955 | 1.025 | 0.99769 | 0.80038 | 0.69055 | 0.63071 | 0.62118 | 0.65326
43602.4284 | 0.8462 | 1.0196 | 0.9965 | 0.79937 | 0.689 | 0.63018 | 0.61923 | 0.65304
43602.4284 | 0.84945 | 1.0208 | 0.99603 | 0.79916 | 0.68916 | 0.63029 | 0.62008 | 0.65334
43602.4284 | 0.85117 | 1.0214 | 0.99535 | 0.79898 | 0.68828 | 0.62971 | 0.62097 | 0.65326
43602.4284 | 0.85123 | 1.0209 | 0.99601 | 0.79838 | 0.68834 | 0.62992 | 0.62224 | 0.65318
43602.4285 | 0.85338 | 1.0217 | 0.9961 | 0.8001 | 0.68923 | 0.63026 | 0.62116 | 0.65326
43602.4285 | 0.8577 | 1.0229 | 0.99514 | 0.80028 | 0.68912 | 0.62992 | 0.62141 | 0.65303
43602.4285 | 0.84072 | 1.0177 | 0.99534 | 0.79858 | 0.68917 | 0.63001 | 0.6287 | 0.65331
43602.4285 | 0.8447 | 1.0159 | 0.99311 | 0.79651 | 0.68795 | 0.62953 | 0.62276 | 0.65326
43602.4285 | 0.83864 | 1.0111 | 0.99042 | 0.79452 | 0.68635 | 0.62841 | 0.62085 | 0.65296
43602.4285 | 0.84073 | 1.0109 | 0.98867 | 0.79424 | 0.68538 | 0.62749 | 0.61829 | 0.65271
43602.4285 | 0.8468 | 1.0128 | 0.98872 | 0.79352 | 0.68519 | 0.62741 | 0.61732 | 0.65263
43602.4285 | 0.83694 | 1.0102 | 0.98925 | 0.79379 | 0.68485 | 0.62761 | 0.61696 | 0.65268
43602.4285 | 0.8363 | 1.0124 | 0.98964 | 0.79558 | 0.68556 | 0.62782 | 0.61958 | 0.6531
43602.4286 | 0.84339 | 1.0131 | 0.98986 | 0.79535 | 0.68597 | 0.62809 | 0.61914 | 0.65299
43602.4286 | 0.841 | 1.0111 | 0.9878 | 0.79333 | 0.68529 | 0.62735 | 0.61904 | 0.65277
43602.4286 | 0.8296 | 1.006 | 0.98813 | 0.79327 | 0.68456 | 0.62693 | 0.61648 | 0.65248
43602.4286 | 0.83851 | 1.0081 | 0.98622 | 0.7931 | 0.68403 | 0.62673 | 0.61635 | 0.65262
43602.4286 | 0.8411 | 1.0089 | 0.98637 | 0.79261 | 0.68442 | 0.62658 | 0.62509 | 0.65272
43602.4286 | 0.84044 | 1.0075 | 0.9857 | 0.79148 | 0.68336 | 0.6259 | 0.61934 | 0.65223
43602.4286 | 0.83369 | 1.0047 | 0.98493 | 0.79105 | 0.68242 | 0.62541 | 0.61809 | 0.652
43602.4286 | 0.83942 | 1.0076 | 0.98512 | 0.79213 | 0.68277 | 0.62575 | 0.61671 | 0.65226
43602.4286 | 0.83552 | 1.0065 | 0.98561 | 0.79167 | 0.68268 | 0.62551 | 0.61585 | 0.65216
43602.4287 | 0.83642 | 1.0073 | 0.98507 | 0.79129 | 0.68235 | 0.62523 | 0.61464 | 0.65213
43602.4287 | 0.84177 | 1.0078 | 0.98455 | 0.79148 | 0.68263 | 0.62515 | 0.61703 | 0.65194
43602.4287 | 0.8368 | 1.0072 | 0.98523 | 0.79124 | 0.68208 | 0.62502 | 0.6162 | 0.65184
43602.4287 | 0.83546 | 1.0068 | 0.98458 | 0.79048 | 0.68168 | 0.62472 | 0.61537 | 0.65172
43602.4287 | 0.84066 | 1.009 | 0.98455 | 0.79072 | 0.68161 | 0.62435 | 0.62199 | 0.65156
43602.4287 | 0.83439 | 1.0049 | 0.985 | 0.79071 | 0.68189 | 0.62449 | 0.61797 | 0.65148
43602.4287 | 0.83686 | 1.007 | 0.98568 | 0.78993 | 0.68163 | 0.62451 | 0.6172 | 0.6513
43602.4287 | 0.8334 | 1.0068 | 0.98738 | 0.79122 | 0.6815 | 0.62432 | 0.61509 | 0.6512
43602.4287 | 0.84283 | 1.0113 | 0.98721 | 0.79188 | 0.68222 | 0.62469 | 0.61455 | 0.65141
43602.4288 | 0.83776 | 1.0099 | 0.98813 | 0.79221 | 0.68283 | 0.62454 | 0.61372 | 0.65111
43602.4288 | 0.84299 | 1.0114 | 0.9882 | 0.79197 | 0.68234 | 0.62463 | 0.61662 | 0.65121
43602.4288 | 0.83333 | 1.008 | 0.98822 | 0.79133 | 0.6821 | 0.62451 | 0.61534 | 0.65074
43602.4288 | 0.84126 | 1.0125 | 0.98912 | 0.79183 | 0.68222 | 0.6242 | 0.61419 | 0.65065
43602.4288 | 0.83979 | 1.0131 | 0.99052 | 0.79318 | 0.68268 | 0.62431 | 0.61731 | 0.65069
43602.4288 | 0.84109 | 1.0134 | 0.99086 | 0.79328 | 0.68292 | 0.62464 | 0.61583 | 0.65055
43602.4288 | 0.84286 | 1.0154 | 0.99222 | 0.79377 | 0.68287 | 0.62457 | 0.61601 | 0.65041
43602.4288 | 0.85436 | 1.0212 | 0.99374 | 0.7946 | 0.68379 | 0.62496 | 0.61474 | 0.65049
43602.4288 | 0.84791 | 1.0185 | 0.99399 | 0.79482 | 0.68397 | 0.62519 | 0.6178 | 0.65031
43602.4289 | 0.85404 | 1.0221 | 0.99604 | 0.79572 | 0.68473 | 0.6255 | 0.61973 | 0.6502
43602.4289 | 0.85272 | 1.0223 | 0.99685 | 0.79641 | 0.68469 | 0.62542 | 0.61701 | 0.65
43602.4289 | 0.86103 | 1.0267 | 0.99774 | 0.79685 | 0.68524 | 0.62557 | 0.61621 | 0.65002
43602.4289 | 0.85849 | 1.0258 | 0.99931 | 0.79779 | 0.68537 | 0.62556 | 0.61473 | 0.64963
43602.4289 | 0.85334 | 1.0257 | 1.0007 | 0.79802 | 0.68614 | 0.62614 | 0.61494 | 0.64996
43602.4289 | 0.85782 | 1.0283 | 1.0016 | 0.79858 | 0.68653 | 0.6265 | 0.61857 | 0.64994
43602.4289 | 0.8553 | 1.0269 | 1.0019 | 0.79914 | 0.68652 | 0.62643 | 0.61718 | 0.64969
43602.4289 | 0.85999 | 1.0289 | 1.0038 | 0.7995 | 0.68718 | 0.6271 | 0.61776 | 0.64997
43602.4289 | 0.86282 | 1.033 | 1.0051 | 0.80059 | 0.68724 | 0.62696 | 0.61569 | 0.64972
43602.429 | 0.86206 | 1.0343 | 1.0078 | 0.80215 | 0.68817 | 0.62738 | 0.62335 | 0.64938
43602.429 | 0.86804 | 1.0385 | 1.0106 | 0.80397 | 0.69019 | 0.62886 | 0.62092 | 0.64996
43602.429 | 0.87179 | 1.0394 | 1.0101 | 0.80506 | 0.6907 | 0.62914 | 0.62038 | 0.65014
43602.429 | 0.87535 | 1.043 | 1.0133 | 0.80544 | 0.69152 | 0.62963 | 0.61962 | 0.64966
43602.429 | 0.86917 | 1.0429 | 1.0141 | 0.80695 | 0.69202 | 0.63028 | 0.61819 | 0.6499
43602.429 | 0.86812 | 1.044 | 1.0158 | 0.8076 | 0.69282 | 0.63071 | 0.61912 | 0.64997
43602.429 | 0.87729 | 1.0484 | 1.0177 | 0.80915 | 0.69368 | 0.63118 | 0.62038 | 0.64998
43602.429 | 0.88645 | 1.0533 | 1.0185 | 0.81164 | 0.69584 | 0.63236 | 0.62229 | 0.65041
43602.429 | 0.87761 | 1.0512 | 1.0211 | 0.81011 | 0.6963 | 0.63276 | 0.62203 | 0.65014
43602.4291 | 0.87701 | 1.053 | 1.0212 | 0.81118 | 0.69611 | 0.63299 | 0.62829 | 0.65007
43602.4291 | 0.88479 | 1.0572 | 1.0225 | 0.81302 | 0.6975 | 0.63402 | 0.62376 | 0.65059
43602.4291 | 0.88938 | 1.0603 | 1.0239 | 0.81411 | 0.69806 | 0.63454 | 0.62339 | 0.65035
43602.4291 | 0.88567 | 1.0609 | 1.0263 | 0.81543 | 0.69933 | 0.63509 | 0.62343 | 0.65051
43602.4291 | 0.8911 | 1.0619 | 1.0261 | 0.81494 | 0.69961 | 0.63556 | 0.62426 | 0.65055
43602.4291 | 0.89204 | 1.0627 | 1.0261 | 0.81521 | 0.69993 | 0.63595 | 0.62424 | 0.65061
43602.4291 | 0.89581 | 1.0634 | 1.0251 | 0.81637 | 0.70007 | 0.636 | 0.62514 | 0.65082
43602.4291 | 0.88845 | 1.0601 | 1.0261 | 0.81517 | 0.70031 | 0.63636 | 0.62377 | 0.65102
43602.4291 | 0.89008 | 1.0645 | 1.0281 | 0.81756 | 0.69996 | 0.63677 | 0.62602 | 0.65127
43602.4292 | 0.90034 | 1.0704 | 1.0296 | 0.82109 | 0.70382 | 0.63871 | 0.62721 | 0.65189
43602.4292 | 0.8985 | 1.0667 | 1.0279 | 0.81877 | 0.70314 | 0.6382 | 0.63147 | 0.65154
43602.4292 | 0.89663 | 1.0655 | 1.0277 | 0.81784 | 0.70143 | 0.63772 | 0.62697 | 0.65117
43602.4292 | 0.90243 | 1.0708 | 1.029 | 0.82152 | 0.7035 | 0.63903 | 0.62741 | 0.65193
43602.4292 | 0.89379 | 1.0646 | 1.0268 | 0.81665 | 0.70354 | 0.63896 | 0.62744 | 0.65183
43602.4292 | 0.89759 | 1.0644 | 1.0263 | 0.81721 | 0.70126 | 0.63792 | 0.62665 | 0.65145
43602.4292 | 0.89981 | 1.0689 | 1.028 | 0.81972 | 0.70298 | 0.63851 | 0.62664 | 0.65189
43602.4292 | 0.90129 | 1.0682 | 1.0267 | 0.81928 | 0.70333 | 0.63872 | 0.62773 | 0.65171
43602.4292 | 0.89618 | 1.0641 | 1.026 | 0.81797 | 0.7038 | 0.63923 | 0.62928 | 0.6523
43602.4293 | 0.88856 | 1.0613 | 1.0251 | 0.81563 | 0.70154 | 0.63833 | 0.62771 | 0.65223
43602.4293 | 0.89196 | 1.0621 | 1.0238 | 0.81717 | 0.70162 | 0.63857 | 0.6278 | 0.65236
43602.4293 | 0.89425 | 1.0602 | 1.0223 | 0.81496 | 0.7014 | 0.63787 | 0.62585 | 0.65219
43602.4293 | 0.89554 | 1.0604 | 1.0218 | 0.81472 | 0.70053 | 0.63759 | 0.62912 | 0.65231
43602.4293 | 0.89068 | 1.0607 | 1.0223 | 0.81597 | 0.70095 | 0.63782 | 0.6316 | 0.65248
43602.4293 | 0.89436 | 1.0612 | 1.0214 | 0.81627 | 0.7013 | 0.63806 | 0.6278 | 0.65276
43602.4293 | 0.88919 | 1.0596 | 1.022 | 0.8155 | 0.70149 | 0.63844 | 0.62746 | 0.65309
43602.4293 | 0.89097 | 1.0571 | 1.0188 | 0.81361 | 0.69984 | 0.6372 | 0.62618 | 0.65264
43602.4293 | 0.88915 | 1.0562 | 1.0194 | 0.812 | 0.69946 | 0.63723 | 0.62465 | 0.65288
43602.4294 | 0.88928 | 1.059 | 1.0204 | 0.81593 | 0.70044 | 0.63791 | 0.62661 | 0.65317
43602.4294 | 0.89115 | 1.0587 | 1.0203 | 0.81653 | 0.70225 | 0.63914 | 0.63293 | 0.6539
43602.4294 | 0.89266 | 1.0583 | 1.0209 | 0.8137 | 0.70147 | 0.63895 | 0.63043 | 0.65395
43602.4294 | 0.88849 | 1.0571 | 1.0191 | 0.81469 | 0.70041 | 0.63807 | 0.62752 | 0.6536
43602.4294 | 0.88306 | 1.0562 | 1.0213 | 0.81594 | 0.70188 | 0.63904 | 0.62805 | 0.65418
43602.4294 | 0.88521 | 1.0551 | 1.0197 | 0.81488 | 0.70139 | 0.63907 | 0.62677 | 0.65421
43602.4294 | 0.88981 | 1.0571 | 1.0199 | 0.81518 | 0.70184 | 0.63895 | 0.62832 | 0.65443
43602.4294 | 0.88173 | 1.052 | 1.0182 | 0.81241 | 0.70071 | 0.63861 | 0.62783 | 0.65405
43602.4294 | 0.88537 | 1.055 | 1.0182 | 0.81316 | 0.69985 | 0.63795 | 0.62658 | 0.65418
43602.4295 | 0.8833 | 1.0538 | 1.0179 | 0.81317 | 0.70022 | 0.63814 | 0.62933 | 0.65453
43602.4295 | 0.88491 | 1.0556 | 1.0193 | 0.81338 | 0.70091 | 0.63841 | 0.6318 | 0.65469
43602.4295 | 0.8834 | 1.0545 | 1.0179 | 0.81456 | 0.70146 | 0.63886 | 0.62959 | 0.6547
43602.4295 | 0.88102 | 1.0535 | 1.0193 | 0.81346 | 0.70152 | 0.63921 | 0.62893 | 0.65521
43602.4295 | 0.88118 | 1.0519 | 1.017 | 0.81215 | 0.70022 | 0.63832 | 0.62685 | 0.65451
43602.4295 | 0.88649 | 1.0545 | 1.0173 | 0.81341 | 0.70006 | 0.63821 | 0.62769 | 0.65457
43602.4295 | 0.87954 | 1.0522 | 1.0183 | 0.81234 | 0.69987 | 0.63793 | 0.62718 | 0.65434
43602.4295 | 0.88761 | 1.0557 | 1.0174 | 0.8143 | 0.70047 | 0.6383 | 0.62792 | 0.65503
43602.4295 | 0.88552 | 1.0516 | 1.0168 | 0.81139 | 0.70045 | 0.63832 | 0.6286 | 0.65462
43602.4296 | 0.87959 | 1.0504 | 1.0161 | 0.81085 | 0.69927 | 0.63771 | 0.62694 | 0.65459
43602.4296 | 0.8824 | 1.0522 | 1.0172 | 0.81164 | 0.69934 | 0.63772 | 0.62743 | 0.65475
43602.4296 | 0.88384 | 1.0529 | 1.0176 | 0.81313 | 0.69999 | 0.63811 | 0.62772 | 0.65493
43602.4296 | 0.88227 | 1.053 | 1.0189 | 0.81279 | 0.7006 | 0.63843 | 0.63413 | 0.65498
43602.4296 | 0.88397 | 1.0538 | 1.0181 | 0.81401 | 0.70054 | 0.63846 | 0.62928 | 0.65498
43602.4296 | 0.87901 | 1.0522 | 1.0188 | 0.8124 | 0.70099 | 0.63894 | 0.62897 | 0.65537
43602.4296 | 0.87926 | 1.0511 | 1.0188 | 0.81194 | 0.70009 | 0.6385 | 0.62825 | 0.65503
43602.4296 | 0.87863 | 1.0536 | 1.0208 | 0.81378 | 0.70069 | 0.63885 | 0.6276 | 0.65529
43602.4296 | 0.89076 | 1.0595 | 1.0213 | 0.81614 | 0.70195 | 0.63987 | 0.62709 | 0.65578
43602.4297 | 0.88776 | 1.0588 | 1.0223 | 0.81601 | 0.70297 | 0.64041 | 0.6294 | 0.6558
43602.4297 | 0.88605 | 1.0579 | 1.0233 | 0.8162 | 0.70353 | 0.64067 | 0.63034 | 0.65612
43602.4297 | 0.88366 | 1.0559 | 1.0223 | 0.81445 | 0.70256 | 0.64024 | 0.62766 | 0.65565
43602.4297 | 0.89052 | 1.0577 | 1.0222 | 0.81543 | 0.70242 | 0.63977 | 0.62752 | 0.6557
43602.4297 | 0.88886 | 1.0571 | 1.0222 | 0.81461 | 0.70263 | 0.63997 | 0.63505 | 0.65556
43602.4297 | 0.88235 | 1.0563 | 1.0227 | 0.81584 | 0.70299 | 0.6404 | 0.63206 | 0.65608
43602.4297 | 0.88394 | 1.057 | 1.0243 | 0.81522 | 0.70314 | 0.64048 | 0.63029 | 0.65606
43602.4297 | 0.88528 | 1.0571 | 1.0229 | 0.81559 | 0.70284 | 0.64024 | 0.62927 | 0.6559
43602.4297 | 0.88675 | 1.0594 | 1.0246 | 0.81622 | 0.70377 | 0.6408 | 0.6293 | 0.65635
43602.4298 | 0.88442 | 1.0592 | 1.024 | 0.81621 | 0.70355 | 0.64079 | 0.6282 | 0.65605
43602.4298 | 0.88152 | 1.0572 | 1.0248 | 0.81553 | 0.70371 | 0.64087 | 0.63123 | 0.65624
43602.4298 | 0.89202 | 1.0609 | 1.0258 | 0.8166 | 0.70371 | 0.64102 | 0.63454 | 0.65629
43602.4298 | 0.8876 | 1.0611 | 1.0249 | 0.81777 | 0.70395 | 0.64102 | 0.63082 | 0.6561
43602.4298 | 0.89059 | 1.0625 | 1.0259 | 0.81779 | 0.705 | 0.64158 | 0.63046 | 0.65645
43602.4298 | 0.8828 | 1.0573 | 1.0249 | 0.8159 | 0.70388 | 0.64106 | 0.62943 | 0.65616
43602.4298 | 0.88751 | 1.0586 | 1.0237 | 0.81535 | 0.70337 | 0.64078 | 0.62916 | 0.65627
43602.4298 | 0.88521 | 1.0579 | 1.0236 | 0.81541 | 0.70322 | 0.64046 | 0.62909 | 0.65619
43602.4299 | 0.88441 | 1.0565 | 1.0228 | 0.81427 | 0.70282 | 0.64049 | 0.63131 | 0.6562
43602.4299 | 0.88985 | 1.0572 | 1.0228 | 0.81377 | 0.70221 | 0.64006 | 0.63491 | 0.65603
43602.4299 | 0.88675 | 1.0587 | 1.0226 | 0.81588 | 0.70284 | 0.63994 | 0.62973 | 0.65599
43602.4299 | 0.88063 | 1.0565 | 1.0225 | 0.81643 | 0.70382 | 0.64106 | 0.63021 | 0.65651
43602.4299 | 0.88646 | 1.0553 | 1.0205 | 0.81295 | 0.70263 | 0.64034 | 0.62815 | 0.65617
43602.4299 | 0.88254 | 1.0534 | 1.0195 | 0.81274 | 0.70103 | 0.63927 | 0.62803 | 0.65587
43602.4299 | 0.88496 | 1.0542 | 1.0201 | 0.81308 | 0.7016 | 0.63944 | 0.62891 | 0.65624
43602.4299 | 0.88098 | 1.0543 | 1.0208 | 0.81281 | 0.70173 | 0.63989 | 0.62923 | 0.65604
43602.4299 | 0.8756 | 1.0531 | 1.0211 | 0.81365 | 0.70205 | 0.63963 | 0.63251 | 0.65613
43602.43 | 0.8813 | 1.0537 | 1.0208 | 0.81341 | 0.70127 | 0.63929 | 0.63076 | 0.65605
43602.43 | 0.88189 | 1.0541 | 1.0207 | 0.81316 | 0.70151 | 0.63942 | 0.62926 | 0.65623
43602.43 | 0.88146 | 1.054 | 1.0219 | 0.81358 | 0.70155 | 0.63928 | 0.62899 | 0.65603
43602.43 | 0.8798 | 1.054 | 1.0217 | 0.81396 | 0.70188 | 0.63967 | 0.62743 | 0.65587
43602.43 | 0.88275 | 1.0566 | 1.0228 | 0.81508 | 0.70186 | 0.63963 | 0.62806 | 0.65609
43602.43 | 0.88595 | 1.0567 | 1.023 | 0.8153 | 0.70264 | 0.63971 | 0.62944 | 0.65599
43602.43 | 0.88446 | 1.0586 | 1.0247 | 0.81623 | 0.70271 | 0.63986 | 0.62906 | 0.65582
43602.43 | 0.88835 | 1.0621 | 1.0266 | 0.81747 | 0.70383 | 0.64065 | 0.63056 | 0.65601
43602.43 | 0.88776 | 1.0639 | 1.0274 | 0.81967 | 0.70477 | 0.64125 | 0.63471 | 0.65618
43602.4301 | 0.89035 | 1.0641 | 1.0295 | 0.81839 | 0.70534 | 0.64162 | 0.63092 | 0.65614
43602.4301 | 0.88928 | 1.0656 | 1.0309 | 0.8199 | 0.70593 | 0.64236 | 0.63145 | 0.65604
43602.4301 | 0.90099 | 1.0714 | 1.0324 | 0.82217 | 0.70732 | 0.64299 | 0.63078 | 0.65637
43602.4301 | 0.90138 | 1.0736 | 1.035 | 0.82391 | 0.70878 | 0.64358 | 0.63226 | 0.65645
43602.4301 | 0.90204 | 1.0746 | 1.0361 | 0.82341 | 0.70861 | 0.64399 | 0.63159 | 0.6562
43602.4301 | 0.9026 | 1.0765 | 1.0379 | 0.82466 | 0.7096 | 0.64463 | 0.63264 | 0.65631
43602.4301 | 0.90676 | 1.0808 | 1.0405 | 0.82627 | 0.7103 | 0.64533 | 0.63304 | 0.65645
43602.4301 | 0.91275 | 1.0855 | 1.0425 | 0.82893 | 0.71232 | 0.64668 | 0.6404 | 0.65686
43602.4301 | 0.91258 | 1.0872 | 1.0445 | 0.83099 | 0.71395 | 0.64774 | 0.63714 | 0.65724
43602.4302 | 0.91273 | 1.0871 | 1.0462 | 0.83001 | 0.71469 | 0.64814 | 0.63625 | 0.65701
43602.4302 | 0.9114 | 1.0902 | 1.0484 | 0.83293 | 0.71457 | 0.64835 | 0.63541 | 0.65717
43602.4302 | 0.92343 | 1.0973 | 1.0508 | 0.83626 | 0.71742 | 0.64985 | 0.6362 | 0.65756
43602.4302 | 0.92847 | 1.0999 | 1.0531 | 0.83904 | 0.71973 | 0.65124 | 0.63743 | 0.65769
43602.4302 | 0.9186 | 1.0956 | 1.054 | 0.83516 | 0.7196 | 0.65156 | 0.64086 | 0.65768
43602.4302 | 0.92553 | 1.0995 | 1.0548 | 0.83737 | 0.71871 | 0.65156 | 0.64235 | 0.65773
43602.4302 | 0.92708 | 1.1009 | 1.0556 | 0.8378 | 0.72047 | 0.6526 | 0.64057 | 0.65817
43602.4302 | 0.93582 | 1.1054 | 1.0584 | 0.84135 | 0.72144 | 0.65291 | 0.63969 | 0.65793
43602.4302 | 0.93126 | 1.1062 | 1.0616 | 0.84133 | 0.72339 | 0.65431 | 0.64082 | 0.65815
43602.4303 | 0.93475 | 1.1072 | 1.0611 | 0.84214 | 0.72383 | 0.65527 | 0.64053 | 0.65868
43602.4303 | 0.93335 | 1.1053 | 1.0609 | 0.84059 | 0.72252 | 0.65463 | 0.64107 | 0.65822
43602.4303 | 0.93516 | 1.1078 | 1.0625 | 0.84244 | 0.72444 | 0.65585 | 0.64751 | 0.65926
43602.4303 | 0.927 | 1.1051 | 1.062 | 0.84144 | 0.72362 | 0.6558 | 0.64469 | 0.6591
43602.4303 | 0.93101 | 1.1061 | 1.0619 | 0.84157 | 0.72382 | 0.6558 | 0.64277 | 0.65936
43602.4303 | 0.93658 | 1.1088 | 1.0625 | 0.84236 | 0.72434 | 0.65592 | 0.6427 | 0.6595
43602.4303 | 0.93237 | 1.1091 | 1.0646 | 0.84316 | 0.72499 | 0.65659 | 0.64242 | 0.65953
43602.4303 | 0.9316 | 1.1081 | 1.0649 | 0.84304 | 0.72505 | 0.65708 | 0.64359 | 0.66009
43602.4303 | 0.94137 | 1.1133 | 1.0667 | 0.84652 | 0.72704 | 0.65817 | 0.64531 | 0.66071
43602.4304 | 0.93902 | 1.1114 | 1.0665 | 0.84536 | 0.72873 | 0.65934 | 0.64553 | 0.66118
43602.4304 | 0.934 | 1.1056 | 1.0644 | 0.84092 | 0.72575 | 0.65787 | 0.6445 | 0.66054
43602.4304 | 0.93654 | 1.1063 | 1.0634 | 0.84134 | 0.72494 | 0.65756 | 0.64687 | 0.66106
43602.4304 | 0.93258 | 1.1048 | 1.0639 | 0.8415 | 0.72512 | 0.6577 | 0.64506 | 0.66114
43602.4304 | 0.92936 | 1.1055 | 1.064 | 0.84158 | 0.72522 | 0.65762 | 0.64418 | 0.66125
43602.4304 | 0.92926 | 1.1055 | 1.0643 | 0.84185 | 0.72568 | 0.6584 | 0.64441 | 0.66178
43602.4304 | 0.93026 | 1.1036 | 1.0635 | 0.84015 | 0.72525 | 0.65824 | 0.64584 | 0.66186
43602.4304 | 0.92242 | 1.0997 | 1.0616 | 0.83943 | 0.72394 | 0.65722 | 0.64468 | 0.66162
43602.4304 | 0.92133 | 1.0967 | 1.061 | 0.83667 | 0.72415 | 0.6577 | 0.64458 | 0.6623
43602.4305 | 0.92489 | 1.0974 | 1.0596 | 0.83748 | 0.72265 | 0.65664 | 0.645 | 0.66198
43602.4305 | 0.927 | 1.0988 | 1.0599 | 0.8382 | 0.72338 | 0.65725 | 0.65137 | 0.66239
43602.4305 | 0.91722 | 1.0953 | 1.0595 | 0.8376 | 0.72388 | 0.65737 | 0.64614 | 0.66297
43602.4305 | 0.90984 | 1.0888 | 1.0572 | 0.8335 | 0.72218 | 0.65656 | 0.64435 | 0.66282
43602.4305 | 0.90726 | 1.0875 | 1.0556 | 0.83264 | 0.72059 | 0.65569 | 0.64326 | 0.66274
43602.4305 | 0.91561 | 1.0903 | 1.0548 | 0.8331 | 0.72002 | 0.65543 | 0.64228 | 0.66309
43602.4305 | 0.91367 | 1.0882 | 1.0538 | 0.83157 | 0.71987 | 0.65508 | 0.64158 | 0.66284
43602.4305 | 0.90761 | 1.0849 | 1.0524 | 0.83019 | 0.71854 | 0.65421 | 0.64248 | 0.66253
43602.4305 | 0.90705 | 1.0842 | 1.0504 | 0.82896 | 0.71824 | 0.65429 | 0.64173 | 0.66291
43602.4306 | 0.90958 | 1.0823 | 1.0496 | 0.8285 | 0.71722 | 0.65338 | 0.64146 | 0.66275
43602.4306 | 0.90861 | 1.0819 | 1.0492 | 0.82789 | 0.71689 | 0.65287 | 0.64689 | 0.66271
43602.4306 | 0.90524 | 1.0821 | 1.0494 | 0.82855 | 0.71679 | 0.65289 | 0.64211 | 0.66284
43602.4306 | 0.90188 | 1.0813 | 1.0497 | 0.82909 | 0.71675 | 0.65299 | 0.64151 | 0.66287
43602.4306 | 0.89899 | 1.0796 | 1.0502 | 0.82894 | 0.71695 | 0.65291 | 0.64077 | 0.66297
43602.4306 | 0.90074 | 1.0801 | 1.0495 | 0.82846 | 0.7166 | 0.65292 | 0.63991 | 0.6629
43602.4306 | 0.904 | 1.0814 | 1.0493 | 0.82819 | 0.71672 | 0.6527 | 0.64064 | 0.66312
43602.4306 | 0.90109 | 1.0799 | 1.0501 | 0.82813 | 0.71675 | 0.65295 | 0.64089 | 0.663
43602.4306 | 0.90193 | 1.0793 | 1.049 | 0.82772 | 0.71641 | 0.65279 | 0.63997 | 0.66309
43602.4307 | 0.90235 | 1.0796 | 1.0492 | 0.82694 | 0.71593 | 0.65216 | 0.63904 | 0.66273
43602.4307 | 0.89921 | 1.0783 | 1.049 | 0.8263 | 0.71513 | 0.65154 | 0.64361 | 0.66237
43602.4307 | 0.90329 | 1.0801 | 1.0498 | 0.8265 | 0.71544 | 0.65177 | 0.64155 | 0.66255
43602.4307 | 0.89975 | 1.0806 | 1.0505 | 0.8278 | 0.71597 | 0.65218 | 0.64145 | 0.66239
43602.4307 | 0.90601 | 1.0833 | 1.0528 | 0.82881 | 0.71726 | 0.6528 | 0.64048 | 0.66259
43602.4307 | 0.90443 | 1.0833 | 1.0531 | 0.82913 | 0.71684 | 0.65283 | 0.64094 | 0.66245
43602.4307 | 0.90563 | 1.0854 | 1.0534 | 0.83065 | 0.71765 | 0.65291 | 0.64059 | 0.66264
43602.4307 | 0.90546 | 1.0866 | 1.055 | 0.83092 | 0.71792 | 0.65301 | 0.64105 | 0.6625
43602.4307 | 0.91181 | 1.0878 | 1.0556 | 0.83049 | 0.71854 | 0.65371 | 0.64019 | 0.66292
43602.4308 | 0.91336 | 1.0892 | 1.0562 | 0.83178 | 0.71791 | 0.65318 | 0.64106 | 0.66235
43602.4308 | 0.90463 | 1.0879 | 1.0581 | 0.83263 | 0.71933 | 0.65428 | 0.6488 | 0.66273
43602.4308 | 0.90964 | 1.0903 | 1.0592 | 0.83222 | 0.7196 | 0.65431 | 0.64356 | 0.66275
43602.4308 | 0.9119 | 1.0922 | 1.0606 | 0.83274 | 0.71976 | 0.65459 | 0.64232 | 0.66285
43602.4308 | 0.91 | 1.0926 | 1.0625 | 0.83388 | 0.72083 | 0.65542 | 0.64247 | 0.6631
43602.4308 | 0.91314 | 1.0963 | 1.0657 | 0.83602 | 0.72195 | 0.65594 | 0.64271 | 0.66334
43602.4308 | 0.91868 | 1.0993 | 1.0661 | 0.83636 | 0.72255 | 0.65646 | 0.64189 | 0.66297
43602.4308 | 0.92006 | 1.1006 | 1.0675 | 0.83767 | 0.72295 | 0.65692 | 0.64342 | 0.66307
43602.4308 | 0.91667 | 1.1002 | 1.0694 | 0.8372 | 0.72386 | 0.65712 | 0.64434 | 0.66299
43602.4309 | 0.92619 | 1.1037 | 1.0702 | 0.83802 | 0.72384 | 0.6572 | 0.64261 | 0.66255
43602.4309 | 0.92915 | 1.1073 | 1.0719 | 0.83993 | 0.72556 | 0.65842 | 0.64546 | 0.66339
43602.4309 | 0.92418 | 1.1046 | 1.072 | 0.8393 | 0.72495 | 0.65765 | 0.64358 | 0.66229
43602.4309 | 0.91788 | 1.1037 | 1.0743 | 0.83988 | 0.72592 | 0.65876 | 0.6509 | 0.66313
43602.4309 | 0.9272 | 1.1082 | 1.0754 | 0.84045 | 0.72666 | 0.6595 | 0.6486 | 0.66367
43602.4309 | 0.92697 | 1.1107 | 1.0773 | 0.84365 | 0.72749 | 0.65982 | 0.64691 | 0.66354
43602.4309 | 0.93515 | 1.1151 | 1.0793 | 0.84455 | 0.72877 | 0.66053 | 0.64686 | 0.66352
43602.4309 | 0.93217 | 1.1141 | 1.0797 | 0.84454 | 0.72935 | 0.66083 | 0.64639 | 0.66341
43602.4309 | 0.93216 | 1.1147 | 1.0809 | 0.84374 | 0.72934 | 0.66066 | 0.64518 | 0.66302
43602.431 | 0.93216 | 1.1175 | 1.0836 | 0.84588 | 0.72998 | 0.66137 | 0.64735 | 0.6632
43602.431 | 0.93847 | 1.1233 | 1.0856 | 0.84885 | 0.73193 | 0.66271 | 0.64833 | 0.6639
43602.431 | 0.94106 | 1.1245 | 1.0877 | 0.84871 | 0.73266 | 0.66339 | 0.6511 | 0.66368
43602.431 | 0.94508 | 1.1256 | 1.0876 | 0.85002 | 0.73356 | 0.66418 | 0.6536 | 0.6643
43602.431 | 0.94125 | 1.1269 | 1.0898 | 0.85006 | 0.73351 | 0.66397 | 0.65007 | 0.66384
43602.431 | 0.95027 | 1.1312 | 1.0917 | 0.85093 | 0.73454 | 0.66465 | 0.6505 | 0.66374
43602.431 | 0.94768 | 1.1331 | 1.0932 | 0.8539 | 0.73563 | 0.66531 | 0.64944 | 0.66388
43602.431 | 0.9494 | 1.1329 | 1.0947 | 0.85359 | 0.73713 | 0.6665 | 0.6509 | 0.66447
43602.431 | 0.94742 | 1.1342 | 1.0959 | 0.85517 | 0.73671 | 0.66619 | 0.65059 | 0.66385
43602.4311 | 0.95642 | 1.1386 | 1.0985 | 0.85615 | 0.7392 | 0.66807 | 0.65359 | 0.66487
43602.4311 | 0.95857 | 1.1425 | 1.1001 | 0.85812 | 0.73972 | 0.66838 | 0.65282 | 0.66479
43602.4311 | 0.958 | 1.1406 | 1.1003 | 0.85792 | 0.7404 | 0.66865 | 0.65611 | 0.66452
43602.4311 | 0.95881 | 1.1436 | 1.1016 | 0.85973 | 0.74041 | 0.669 | 0.65462 | 0.66452
43602.4311 | 0.96484 | 1.1485 | 1.1045 | 0.86369 | 0.74321 | 0.67076 | 0.65511 | 0.66539
43602.4311 | 0.96578 | 1.1469 | 1.1042 | 0.86055 | 0.74418 | 0.67179 | 0.65559 | 0.66568
43602.4311 | 0.96756 | 1.1487 | 1.1051 | 0.86274 | 0.74285 | 0.67092 | 0.6546 | 0.66506
43602.4311 | 0.9714 | 1.1519 | 1.1061 | 0.86541 | 0.74493 | 0.67213 | 0.65626 | 0.66581
43602.4312 | 0.97046 | 1.15 | 1.1074 | 0.86358 | 0.74572 | 0.67307 | 0.65709 | 0.6662
43602.4312 | 0.97268 | 1.1524 | 1.1074 | 0.86511 | 0.74546 | 0.67287 | 0.6586 | 0.66604
43602.4312 | 0.97212 | 1.1529 | 1.1073 | 0.86617 | 0.74684 | 0.67369 | 0.65797 | 0.6666
43602.4312 | 0.96526 | 1.1476 | 1.1058 | 0.86247 | 0.7455 | 0.67277 | 0.65725 | 0.66578
43602.4312 | 0.97033 | 1.1513 | 1.1069 | 0.86485 | 0.74552 | 0.67373 | 0.65764 | 0.66682
43602.4312 | 0.97474 | 1.1548 | 1.1072 | 0.86767 | 0.74693 | 0.67416 | 0.66239 | 0.66705
43602.4312 | 0.97235 | 1.1515 | 1.1066 | 0.86472 | 0.74707 | 0.67435 | 0.65976 | 0.66701
43602.4312 | 0.97022 | 1.1499 | 1.1064 | 0.86409 | 0.74577 | 0.67379 | 0.65933 | 0.66665
43602.4312 | 0.97225 | 1.1524 | 1.1072 | 0.86635 | 0.74688 | 0.67429 | 0.6588 | 0.6673
43602.4313 | 0.97135 | 1.151 | 1.1073 | 0.8654 | 0.74687 | 0.67464 | 0.65916 | 0.66732
43602.4313 | 0.96889 | 1.1512 | 1.1077 | 0.86576 | 0.74661 | 0.67449 | 0.65711 | 0.66733
43602.4313 | 0.97344 | 1.1529 | 1.1069 | 0.86594 | 0.74715 | 0.67485 | 0.65897 | 0.66744
43602.4313 | 0.96778 | 1.1512 | 1.1079 | 0.86713 | 0.74796 | 0.6759 | 0.66212 | 0.66824
43602.4313 | 0.97439 | 1.1539 | 1.1082 | 0.86657 | 0.74904 | 0.67644 | 0.66501 | 0.66853
43602.4313 | 0.97356 | 1.1537 | 1.1083 | 0.86768 | 0.7484 | 0.67611 | 0.66063 | 0.66791
43602.4313 | 0.97806 | 1.1567 | 1.1103 | 0.87024 | 0.75029 | 0.67697 | 0.66117 | 0.66872
43602.4313 | 0.97195 | 1.1551 | 1.1099 | 0.86817 | 0.75018 | 0.67734 | 0.66065 | 0.66898
43602.4313 | 0.97486 | 1.154 | 1.1093 | 0.86745 | 0.74917 | 0.67669 | 0.6607 | 0.66858
43602.4314 | 0.9753 | 1.1565 | 1.1096 | 0.86805 | 0.74946 | 0.67686 | 0.66108 | 0.66878
43602.4314 | 0.9773 | 1.1568 | 1.1097 | 0.8687 | 0.74996 | 0.67701 | 0.66222 | 0.66893
43602.4314 | 0.97363 | 1.1561 | 1.1109 | 0.86881 | 0.75065 | 0.67801 | 0.66502 | 0.66976
43602.4314 | 0.97059 | 1.1583 | 1.1118 | 0.87202 | 0.75161 | 0.67879 | 0.66316 | 0.67021
43602.4314 | 0.97481 | 1.1581 | 1.1118 | 0.8703 | 0.75306 | 0.67938 | 0.66347 | 0.67027
43602.4314 | 0.97304 | 1.1565 | 1.1113 | 0.86819 | 0.75183 | 0.67916 | 0.6629 | 0.67
43602.4314 | 0.97718 | 1.1594 | 1.1123 | 0.87124 | 0.75201 | 0.67913 | 0.66597 | 0.67083
43602.4314 | 0.97304 | 1.1588 | 1.1136 | 0.87047 | 0.75287 | 0.67938 | 0.66364 | 0.67061
43602.4314 | 0.97415 | 1.1592 | 1.1126 | 0.8711 | 0.75297 | 0.67987 | 0.6639 | 0.67088
43602.4315 | 0.97551 | 1.1577 | 1.1127 | 0.87034 | 0.75317 | 0.67979 | 0.66282 | 0.67069
43602.4315 | 0.97381 | 1.1572 | 1.1135 | 0.8695 | 0.75201 | 0.67878 | 0.66576 | 0.67007
43602.4315 | 0.97829 | 1.1605 | 1.1133 | 0.87223 | 0.75324 | 0.6801 | 0.66455 | 0.67097
43602.4315 | 0.97819 | 1.1589 | 1.1139 | 0.87017 | 0.75368 | 0.68043 | 0.66569 | 0.6713
43602.4315 | 0.97578 | 1.1589 | 1.1137 | 0.8702 | 0.75313 | 0.6801 | 0.664 | 0.67116
43602.4315 | 0.97087 | 1.1609 | 1.1157 | 0.87252 | 0.75404 | 0.6809 | 0.66556 | 0.6715
43602.4315 | 0.9713 | 1.1578 | 1.1143 | 0.86949 | 0.75364 | 0.68065 | 0.66404 | 0.67128
43602.4315 | 0.97675 | 1.1599 | 1.1145 | 0.87125 | 0.7532 | 0.68044 | 0.66432 | 0.67139
43602.4315 | 0.97878 | 1.1587 | 1.1141 | 0.87035 | 0.7531 | 0.67987 | 0.66289 | 0.67124
43602.4316 | 0.97428 | 1.1569 | 1.1137 | 0.86894 | 0.75232 | 0.6798 | 0.66595 | 0.67112
43602.4316 | 0.97389 | 1.1603 | 1.1151 | 0.87096 | 0.75274 | 0.68008 | 0.67013 | 0.67108
43602.4316 | 0.97457 | 1.1602 | 1.1157 | 0.87152 | 0.75327 | 0.68057 | 0.66601 | 0.6712
43602.4316 | 0.97877 | 1.1615 | 1.1167 | 0.8714 | 0.75418 | 0.68078 | 0.66528 | 0.67121
43602.4316 | 0.97723 | 1.1607 | 1.117 | 0.87015 | 0.7541 | 0.68065 | 0.66481 | 0.67124
43602.4316 | 0.97925 | 1.1633 | 1.1186 | 0.87266 | 0.75474 | 0.68078 | 0.6633 | 0.67118
43602.4316 | 0.97572 | 1.1623 | 1.1184 | 0.87247 | 0.75501 | 0.68177 | 0.66568 | 0.6717
43602.4316 | 0.97631 | 1.1619 | 1.118 | 0.87198 | 0.75549 | 0.68192 | 0.66499 | 0.67192
43602.4316 | 0.97929 | 1.1628 | 1.12 | 0.87211 | 0.75497 | 0.6814 | 0.66512 | 0.67119
43602.4317 | 0.98336 | 1.1664 | 1.1209 | 0.87387 | 0.7558 | 0.68222 | 0.66522 | 0.67176
43602.4317 | 0.97991 | 1.1688 | 1.1233 | 0.87544 | 0.75688 | 0.68285 | 0.66771 | 0.67198
43602.4317 | 0.98104 | 1.169 | 1.1245 | 0.87578 | 0.75826 | 0.68385 | 0.67212 | 0.67243
43602.4317 | 0.98235 | 1.1697 | 1.1251 | 0.8759 | 0.75825 | 0.6838 | 0.66834 | 0.67232
43602.4317 | 0.98133 | 1.171 | 1.126 | 0.87682 | 0.75853 | 0.68419 | 0.6681 | 0.67251
43602.4317 | 0.98247 | 1.1695 | 1.1256 | 0.87577 | 0.75862 | 0.6841 | 0.66791 | 0.67243
43602.4317 | 0.98157 | 1.169 | 1.1257 | 0.87478 | 0.75857 | 0.68408 | 0.66767 | 0.67232
43602.4317 | 0.98498 | 1.1688 | 1.1247 | 0.87419 | 0.75719 | 0.68305 | 0.66566 | 0.67181
43602.4317 | 0.97695 | 1.1701 | 1.1271 | 0.87541 | 0.75759 | 0.6835 | 0.66678 | 0.67222
43602.4318 | 0.97996 | 1.1725 | 1.1273 | 0.87695 | 0.75856 | 0.68418 | 0.66964 | 0.67247
43602.4318 | 0.98445 | 1.1706 | 1.1265 | 0.87497 | 0.75864 | 0.6841 | 0.66814 | 0.67208
43602.4318 | 0.98207 | 1.1688 | 1.1265 | 0.87403 | 0.75711 | 0.68324 | 0.6672 | 0.67136
43602.4318 | 0.98224 | 1.1702 | 1.1271 | 0.87493 | 0.75777 | 0.68382 | 0.66703 | 0.67265
43602.4318 | 0.9793 | 1.1695 | 1.1275 | 0.87431 | 0.75746 | 0.68332 | 0.6694 | 0.67158
43602.4318 | 0.98012 | 1.1696 | 1.1274 | 0.87358 | 0.7567 | 0.6831 | 0.66585 | 0.67174
43602.4318 | 0.97955 | 1.1733 | 1.1285 | 0.87607 | 0.75771 | 0.68338 | 0.66588 | 0.67199
43602.4318 | 0.98125 | 1.1717 | 1.1297 | 0.87497 | 0.75818 | 0.68353 | 0.6653 | 0.6719
43602.4318 | 0.98535 | 1.1718 | 1.129 | 0.87407 | 0.75741 | 0.6835 | 0.66657 | 0.67168
43602.4319 | 0.98697 | 1.1746 | 1.1297 | 0.87478 | 0.75771 | 0.6834 | 0.66697 | 0.67137
43602.4319 | 0.98421 | 1.1737 | 1.1299 | 0.87433 | 0.75741 | 0.68309 | 0.66558 | 0.67129
43602.4319 | 0.98168 | 1.1711 | 1.1293 | 0.87248 | 0.75699 | 0.68288 | 0.66613 | 0.67117
43602.4319 | 0.98777 | 1.174 | 1.1295 | 0.87431 | 0.75635 | 0.68265 | 0.66487 | 0.671
43602.4319 | 0.98237 | 1.1744 | 1.1317 | 0.87516 | 0.75747 | 0.68307 | 0.67028 | 0.67141
43602.4319 | 0.98629 | 1.1735 | 1.1308 | 0.87501 | 0.75718 | 0.68322 | 0.66829 | 0.67148
43602.4319 | 0.98627 | 1.1745 | 1.1315 | 0.87527 | 0.75736 | 0.68324 | 0.66634 | 0.67147
43602.4319 | 0.98034 | 1.1733 | 1.1322 | 0.87466 | 0.75688 | 0.68303 | 0.66644 | 0.67114
43602.4319 | 0.98268 | 1.1743 | 1.1324 | 0.87511 | 0.75737 | 0.6837 | 0.66623 | 0.67168
43602.432 | 0.98559 | 1.1748 | 1.1328 | 0.87467 | 0.75715 | 0.68296 | 0.66529 | 0.67096
43602.432 | 0.9862 | 1.1746 | 1.1329 | 0.87467 | 0.75697 | 0.68286 | 0.66552 | 0.67113
43602.432 | 0.98836 | 1.1765 | 1.1332 | 0.87454 | 0.75704 | 0.68289 | 0.66488 | 0.67108
43602.432 | 0.98217 | 1.1736 | 1.1334 | 0.87461 | 0.7568 | 0.68267 | 0.66753 | 0.67086
43602.432 | 0.9863 | 1.1748 | 1.1342 | 0.87404 | 0.75733 | 0.68292 | 0.6658 | 0.67108
43602.432 | 0.98747 | 1.1766 | 1.1349 | 0.8756 | 0.75736 | 0.68314 | 0.66614 | 0.67085
43602.432 | 0.98616 | 1.1773 | 1.1372 | 0.8764 | 0.75834 | 0.68332 | 0.6655 | 0.67094
43602.432 | 0.9899 | 1.1789 | 1.1378 | 0.87686 | 0.75883 | 0.68407 | 0.66691 | 0.67132
43602.432 | 0.99226 | 1.1818 | 1.1392 | 0.87865 | 0.75938 | 0.68415 | 0.67225 | 0.67144
43602.4321 | 0.9919 | 1.1804 | 1.1391 | 0.87755 | 0.7595 | 0.68471 | 0.66767 | 0.67129
43602.4321 | 0.99099 | 1.1813 | 1.1397 | 0.8777 | 0.7593 | 0.6847 | 0.66702 | 0.67138
43602.4321 | 0.98959 | 1.1825 | 1.1419 | 0.87822 | 0.75999 | 0.68493 | 0.66673 | 0.67168
43602.4321 | 0.99047 | 1.1838 | 1.1433 | 0.87921 | 0.76076 | 0.68547 | 0.66737 | 0.67186
43602.4321 | 0.99642 | 1.1877 | 1.1457 | 0.8806 | 0.76153 | 0.68597 | 0.66791 | 0.67226
43602.4321 | 0.99512 | 1.1878 | 1.1461 | 0.88145 | 0.76237 | 0.68681 | 0.66858 | 0.67227
43602.4321 | 1.0003 | 1.1915 | 1.147 | 0.88333 | 0.76296 | 0.68708 | 0.66863 | 0.67228
43602.4321 | 0.99656 | 1.1907 | 1.1492 | 0.88233 | 0.76355 | 0.68758 | 0.67498 | 0.67237
43602.4321 | 1.0043 | 1.1938 | 1.1502 | 0.88242 | 0.7635 | 0.68757 | 0.67066 | 0.67271
43602.4322 | 1.0011 | 1.1957 | 1.152 | 0.88491 | 0.76402 | 0.68811 | 0.67085 | 0.67295
43602.4322 | 1.0045 | 1.198 | 1.1542 | 0.88627 | 0.76619 | 0.68922 | 0.67117 | 0.67299
43602.4322 | 1.0039 | 1.1987 | 1.155 | 0.88594 | 0.76677 | 0.68983 | 0.6706 | 0.67326
43602.4322 | 1.0042 | 1.1984 | 1.1563 | 0.88721 | 0.76716 | 0.6901 | 0.67073 | 0.67332
43602.4322 | 1.0057 | 1.1991 | 1.1564 | 0.88689 | 0.76729 | 0.69041 | 0.6716 | 0.67323
43602.4322 | 1.0059 | 1.2002 | 1.1577 | 0.88729 | 0.76787 | 0.69094 | 0.67501 | 0.67347
43602.4322 | 1.0071 | 1.2013 | 1.1592 | 0.88824 | 0.76832 | 0.69108 | 0.67311 | 0.6739
43602.4322 | 1.0066 | 1.2018 | 1.1605 | 0.88863 | 0.76874 | 0.69142 | 0.67245 | 0.674
43602.4322 | 1.0034 | 1.2025 | 1.1616 | 0.88943 | 0.76939 | 0.69192 | 0.67202 | 0.67407
43602.4323 | 1.0121 | 1.2071 | 1.1633 | 0.89099 | 0.77045 | 0.69281 | 0.67274 | 0.67433
43602.4323 | 1.007 | 1.2073 | 1.1645 | 0.89193 | 0.77127 | 0.69361 | 0.6796 | 0.67473
43602.4323 | 1.0125 | 1.2085 | 1.1654 | 0.89223 | 0.77186 | 0.69395 | 0.67642 | 0.67487
43602.4323 | 1.0139 | 1.2093 | 1.1659 | 0.89199 | 0.77197 | 0.69402 | 0.67596 | 0.67521
43602.4323 | 1.0126 | 1.2089 | 1.1662 | 0.89219 | 0.77211 | 0.6942 | 0.6755 | 0.67495
43602.4323 | 1.0122 | 1.2099 | 1.1675 | 0.89218 | 0.7725 | 0.6945 | 0.67475 | 0.67545
43602.4323 | 1.016 | 1.2104 | 1.1675 | 0.89183 | 0.77263 | 0.69478 | 0.67491 | 0.6752
43602.4323 | 1.016 | 1.2117 | 1.168 | 0.89221 | 0.7728 | 0.69513 | 0.6758 | 0.67532
43602.4323 | 1.0114 | 1.2119 | 1.1695 | 0.89445 | 0.77357 | 0.69533 | 0.67514 | 0.67553
43602.4324 | 1.0165 | 1.2125 | 1.1698 | 0.89465 | 0.7739 | 0.69549 | 0.67942 | 0.67579
43602.4324 | 1.0084 | 1.2114 | 1.1706 | 0.89397 | 0.77418 | 0.69581 | 0.6771 | 0.67568
43602.4324 | 1.0149 | 1.2126 | 1.1709 | 0.89487 | 0.77471 | 0.6963 | 0.67713 | 0.67606
43602.4324 | 1.0149 | 1.2132 | 1.1712 | 0.89444 | 0.77482 | 0.6964 | 0.6766 | 0.67604
43602.4324 | 1.0154 | 1.212 | 1.1714 | 0.89251 | 0.77419 | 0.6964 | 0.67688 | 0.67593
43602.4324 | 1.017 | 1.2131 | 1.1716 | 0.89431 | 0.7742 | 0.6962 | 0.68084 | 0.67594
43602.4324 | 1.0174 | 1.2147 | 1.173 | 0.89475 | 0.77507 | 0.69665 | 0.67962 | 0.67635
43602.4324 | 1.0117 | 1.2134 | 1.1729 | 0.89397 | 0.77524 | 0.69714 | 0.67762 | 0.67639
43602.4324 | 1.0177 | 1.2158 | 1.1738 | 0.89532 | 0.77607 | 0.69732 | 0.67776 | 0.67655
43602.4325 | 1.0212 | 1.2148 | 1.1732 | 0.89475 | 0.77549 | 0.69705 | 0.67756 | 0.6763
43602.4325 | 1.0098 | 1.2128 | 1.1729 | 0.89444 | 0.77553 | 0.6974 | 0.67763 | 0.67638
43602.4325 | 1.016 | 1.2145 | 1.1734 | 0.89523 | 0.77509 | 0.6969 | 0.67936 | 0.67636
43602.4325 | 1.0084 | 1.2118 | 1.1726 | 0.89379 | 0.77549 | 0.69732 | 0.67978 | 0.67679
43602.4325 | 1.0177 | 1.2144 | 1.1733 | 0.89506 | 0.77505 | 0.69689 | 0.67737 | 0.67653
43602.4325 | 1.0135 | 1.2147 | 1.1733 | 0.89546 | 0.77576 | 0.69739 | 0.67731 | 0.67685
43602.4325 | 1.0139 | 1.2129 | 1.1725 | 0.89421 | 0.77541 | 0.69701 | 0.67638 | 0.67656
43602.4325 | 1.0166 | 1.2127 | 1.1721 | 0.89285 | 0.7744 | 0.69629 | 0.67982 | 0.67624
43602.4326 | 1.0135 | 1.2115 | 1.172 | 0.89294 | 0.77395 | 0.69601 | 0.67956 | 0.67612
43602.4326 | 1.0144 | 1.2124 | 1.1717 | 0.894 | 0.77424 | 0.69622 | 0.67791 | 0.67645
43602.4326 | 1.0107 | 1.2096 | 1.1706 | 0.89315 | 0.77416 | 0.69584 | 0.67712 | 0.6762
43602.4326 | 1.0084 | 1.2089 | 1.1704 | 0.89243 | 0.77324 | 0.69558 | 0.676 | 0.67608
43602.4326 | 1.0097 | 1.2101 | 1.1709 | 0.89259 | 0.77395 | 0.69589 | 0.67662 | 0.67621
43602.4326 | 1.0152 | 1.211 | 1.1701 | 0.89132 | 0.77345 | 0.69538 | 0.6754 | 0.6759
43602.4326 | 1.0149 | 1.2122 | 1.1715 | 0.89321 | 0.77356 | 0.6954 | 0.67532 | 0.67576
43602.4326 | 1.0143 | 1.2126 | 1.172 | 0.89347 | 0.77429 | 0.69609 | 0.67864 | 0.67633
43602.4326 | 1.0099 | 1.2116 | 1.1718 | 0.89326 | 0.77411 | 0.69596 | 0.68126 | 0.67621
43602.4327 | 1.0152 | 1.2119 | 1.1723 | 0.89298 | 0.77404 | 0.69592 | 0.67816 | 0.67625
43602.4327 | 1.0145 | 1.2127 | 1.1729 | 0.89296 | 0.77433 | 0.69596 | 0.67756 | 0.67598
43602.4327 | 1.0144 | 1.2142 | 1.1739 | 0.89418 | 0.77453 | 0.69611 | 0.67675 | 0.6762
43602.4327 | 1.0137 | 1.2145 | 1.1742 | 0.89441 | 0.77523 | 0.6965 | 0.6767 | 0.67625
43602.4327 | 1.0096 | 1.2153 | 1.1757 | 0.89501 | 0.77537 | 0.69679 | 0.67609 | 0.67634
43602.4327 | 1.0193 | 1.2194 | 1.1778 | 0.89621 | 0.77624 | 0.69788 | 0.67781 | 0.67654
43602.4327 | 1.0212 | 1.2213 | 1.1783 | 0.89737 | 0.77743 | 0.69815 | 0.67783 | 0.67688
43602.4327 | 1.0213 | 1.2225 | 1.1802 | 0.8982 | 0.77831 | 0.6987 | 0.67846 | 0.67685
43602.4327 | 1.0234 | 1.222 | 1.1805 | 0.89854 | 0.77835 | 0.69891 | 0.68277 | 0.67679
43602.4328 | 1.0218 | 1.225 | 1.1823 | 0.89964 | 0.77899 | 0.69919 | 0.67953 | 0.67706
43602.4328 | 1.0268 | 1.2268 | 1.1828 | 0.90025 | 0.77933 | 0.69948 | 0.679 | 0.67675
43602.4328 | 1.0251 | 1.2255 | 1.1838 | 0.90032 | 0.77998 | 0.69989 | 0.6796 | 0.67694
43602.4328 | 1.0297 | 1.228 | 1.1843 | 0.90089 | 0.77981 | 0.70012 | 0.67969 | 0.67691
43602.4328 | 1.0294 | 1.2267 | 1.1838 | 0.90043 | 0.7802 | 0.70003 | 0.685 | 0.67671
43602.4328 | 1.0276 | 1.2282 | 1.1853 | 0.90138 | 0.78019 | 0.6998 | 0.68058 | 0.67646
43602.4328 | 1.0271 | 1.2295 | 1.1864 | 0.90253 | 0.78118 | 0.70064 | 0.68072 | 0.67664
43602.4328 | 1.0301 | 1.2323 | 1.1871 | 0.90404 | 0.78157 | 0.70069 | 0.68071 | 0.67657
43602.4328 | 1.0273 | 1.2314 | 1.1874 | 0.90322 | 0.78203 | 0.70127 | 0.68073 | 0.67676
43602.4329 | 1.0338 | 1.233 | 1.1884 | 0.90346 | 0.78225 | 0.70188 | 0.68011 | 0.67666
43602.4329 | 1.0341 | 1.2349 | 1.1896 | 0.90583 | 0.78304 | 0.70212 | 0.68073 | 0.67701
43602.4329 | 1.037 | 1.2363 | 1.1906 | 0.90659 | 0.78386 | 0.7026 | 0.68315 | 0.67684
43602.4329 | 1.0382 | 1.2378 | 1.1912 | 0.90643 | 0.78404 | 0.70275 | 0.68487 | 0.67686
43602.4329 | 1.0374 | 1.236 | 1.1896 | 0.90587 | 0.78407 | 0.70276 | 0.68166 | 0.67687
43602.4329 | 1.0395 | 1.2384 | 1.1917 | 0.90727 | 0.78446 | 0.70309 | 0.68225 | 0.67713
43602.4329 | 1.0374 | 1.2403 | 1.1935 | 0.90875 | 0.78567 | 0.70398 | 0.68316 | 0.67711
43602.4329 | 1.0444 | 1.2424 | 1.1943 | 0.91051 | 0.78676 | 0.70478 | 0.68203 | 0.67731
43602.4329 | 1.0471 | 1.2432 | 1.1941 | 0.91097 | 0.78763 | 0.70534 | 0.6838 | 0.67788
43602.433 | 1.0422 | 1.2417 | 1.194 | 0.91084 | 0.78731 | 0.70501 | 0.68811 | 0.67731
43602.433 | 1.0487 | 1.2433 | 1.1945 | 0.91084 | 0.78721 | 0.70534 | 0.68505 | 0.67737
43602.433 | 1.0528 | 1.2448 | 1.1938 | 0.91188 | 0.78775 | 0.70531 | 0.68446 | 0.67768
43602.433 | 1.0481 | 1.2442 | 1.1949 | 0.91122 | 0.78756 | 0.7054 | 0.6839 | 0.67726
43602.433 | 1.0533 | 1.247 | 1.1959 | 0.91347 | 0.78789 | 0.70571 | 0.68418 | 0.67744
43602.433 | 1.0527 | 1.2476 | 1.1959 | 0.91489 | 0.7897 | 0.70647 | 0.68452 | 0.67787
43602.433 | 1.0485 | 1.2464 | 1.1965 | 0.91318 | 0.78964 | 0.70666 | 0.68516 | 0.67792
43602.433 | 1.0564 | 1.2493 | 1.197 | 0.91571 | 0.78989 | 0.70679 | 0.69033 | 0.67792
43602.433 | 1.0548 | 1.2508 | 1.1988 | 0.91689 | 0.7912 | 0.70762 | 0.68662 | 0.67827
43602.4331 | 1.0607 | 1.2516 | 1.1981 | 0.91702 | 0.79176 | 0.70811 | 0.68632 | 0.67835
43602.4331 | 1.0542 | 1.2487 | 1.1973 | 0.91489 | 0.79085 | 0.70772 | 0.6861 | 0.67797
43602.4331 | 1.0602 | 1.2515 | 1.1977 | 0.9178 | 0.79141 | 0.70777 | 0.68584 | 0.67797
43602.4331 | 1.0545 | 1.2499 | 1.1983 | 0.91651 | 0.7917 | 0.70833 | 0.68768 | 0.67859
43602.4331 | 1.0572 | 1.2504 | 1.1974 | 0.91719 | 0.79137 | 0.70807 | 0.68676 | 0.67842
43602.4331 | 1.0603 | 1.2501 | 1.1968 | 0.91661 | 0.79156 | 0.70807 | 0.68776 | 0.67851
43602.4331 | 1.0555 | 1.2513 | 1.1968 | 0.91809 | 0.79167 | 0.70795 | 0.69098 | 0.67819
43602.4331 | 1.0594 | 1.2505 | 1.1968 | 0.91797 | 0.79254 | 0.70869 | 0.68681 | 0.67837
43602.4331 | 1.0631 | 1.252 | 1.1971 | 0.91922 | 0.79257 | 0.70888 | 0.68738 | 0.67858
43602.4332 | 1.0622 | 1.2513 | 1.1959 | 0.91757 | 0.79214 | 0.70849 | 0.6865 | 0.67842
43602.4332 | 1.0607 | 1.2504 | 1.1963 | 0.91875 | 0.79334 | 0.70935 | 0.68807 | 0.67929
43602.4332 | 1.0452 | 1.2443 | 1.194 | 0.91463 | 0.79097 | 0.70804 | 0.68888 | 0.67853
43602.4332 | 1.0569 | 1.2504 | 1.1952 | 0.91889 | 0.79116 | 0.70819 | 0.68639 | 0.67832
43602.4332 | 1.0622 | 1.2489 | 1.1946 | 0.91717 | 0.79278 | 0.70866 | 0.68741 | 0.67861
43602.4332 | 1.0536 | 1.2472 | 1.1934 | 0.91581 | 0.79153 | 0.7081 | 0.68694 | 0.67844
43602.4332 | 1.0602 | 1.249 | 1.1938 | 0.91752 | 0.79175 | 0.70824 | 0.69051 | 0.6788
43602.4332 | 1.0608 | 1.2488 | 1.193 | 0.91754 | 0.79195 | 0.70825 | 0.68705 | 0.67856
43602.4332 | 1.0588 | 1.2469 | 1.1927 | 0.91639 | 0.79156 | 0.70835 | 0.68696 | 0.6787
43602.4333 | 1.0597 | 1.2477 | 1.1926 | 0.91729 | 0.79129 | 0.70767 | 0.68664 | 0.67838
43602.4333 | 1.0552 | 1.2466 | 1.1926 | 0.91667 | 0.79165 | 0.70823 | 0.68685 | 0.67856
43602.4333 | 1.0624 | 1.2482 | 1.1923 | 0.91731 | 0.79149 | 0.70804 | 0.69126 | 0.67863
43602.4333 | 1.0563 | 1.2479 | 1.193 | 0.91781 | 0.79229 | 0.70865 | 0.68867 | 0.6791
43602.4333 | 1.0578 | 1.2465 | 1.1913 | 0.91705 | 0.79223 | 0.70861 | 0.68723 | 0.67888
43602.4333 | 1.0567 | 1.2452 | 1.1914 | 0.91608 | 0.79161 | 0.70808 | 0.68671 | 0.67895
43602.4333 | 1.0587 | 1.2448 | 1.1899 | 0.91559 | 0.79043 | 0.70719 | 0.68646 | 0.67843
43602.4333 | 1.0563 | 1.2456 | 1.1904 | 0.91629 | 0.79113 | 0.70794 | 0.68827 | 0.67894
43602.4333 | 1.0554 | 1.2445 | 1.1893 | 0.91611 | 0.79105 | 0.70785 | 0.68869 | 0.67868
43602.4334 | 1.0546 | 1.2432 | 1.1887 | 0.91514 | 0.79072 | 0.70749 | 0.68665 | 0.67869
43602.4334 | 1.056 | 1.2454 | 1.1893 | 0.91602 | 0.79009 | 0.70691 | 0.68579 | 0.67857
43602.4334 | 1.0475 | 1.2415 | 1.1882 | 0.91425 | 0.7903 | 0.70725 | 0.6864 | 0.67868
43602.4334 | 1.0483 | 1.2407 | 1.1872 | 0.91337 | 0.78956 | 0.70663 | 0.6856 | 0.67881
43602.4334 | 1.0502 | 1.24 | 1.1861 | 0.91265 | 0.78854 | 0.70637 | 0.68526 | 0.6785
43602.4334 | 1.052 | 1.2413 | 1.1858 | 0.91284 | 0.78879 | 0.70628 | 0.69156 | 0.67864
43602.4334 | 1.0498 | 1.2385 | 1.1848 | 0.91167 | 0.7885 | 0.70615 | 0.68698 | 0.67851
43602.4334 | 1.0484 | 1.238 | 1.1841 | 0.91142 | 0.78727 | 0.70569 | 0.68509 | 0.67816
43602.4334 | 1.0495 | 1.2381 | 1.1835 | 0.9114 | 0.78725 | 0.70511 | 0.68463 | 0.678
43602.4335 | 1.0476 | 1.2391 | 1.1842 | 0.9122 | 0.78721 | 0.70542 | 0.6841 | 0.67825
43602.4335 | 1.0465 | 1.2369 | 1.1831 | 0.91087 | 0.78712 | 0.70531 | 0.68489 | 0.67836
43602.4335 | 1.0459 | 1.2363 | 1.1831 | 0.91093 | 0.78698 | 0.70539 | 0.68481 | 0.67831
43602.4335 | 1.0508 | 1.2396 | 1.1841 | 0.91261 | 0.78745 | 0.70547 | 0.68642 | 0.67878
43602.4335 | 1.0478 | 1.2357 | 1.182 | 0.91027 | 0.78727 | 0.7052 | 0.68973 | 0.67872
43602.4335 | 1.043 | 1.2331 | 1.1802 | 0.90749 | 0.78448 | 0.70349 | 0.68318 | 0.67746
43602.4335 | 1.0404 | 1.2328 | 1.1798 | 0.90847 | 0.78418 | 0.70359 | 0.68341 | 0.67782
43602.4335 | 1.0425 | 1.233 | 1.1797 | 0.90868 | 0.78477 | 0.70395 | 0.68298 | 0.67808
43602.4335 | 1.0457 | 1.2337 | 1.1791 | 0.9091 | 0.78465 | 0.70358 | 0.68386 | 0.67798
43602.4336 | 1.0395 | 1.23 | 1.1786 | 0.90656 | 0.78389 | 0.70307 | 0.68273 | 0.67755
43602.4336 | 1.0421 | 1.2346 | 1.1794 | 0.90929 | 0.78377 | 0.70295 | 0.68249 | 0.67744
43602.4336 | 1.0473 | 1.2325 | 1.1784 | 0.90747 | 0.78452 | 0.70338 | 0.68299 | 0.6774
43602.4336 | 1.045 | 1.2321 | 1.1772 | 0.90778 | 0.78378 | 0.70257 | 0.68668 | 0.67719
43602.4336 | 1.038 | 1.2281 | 1.1774 | 0.90523 | 0.78291 | 0.7023 | 0.68336 | 0.67711
43602.4336 | 1.0437 | 1.2311 | 1.1771 | 0.90672 | 0.78244 | 0.7021 | 0.68289 | 0.67721
43602.4336 | 1.0396 | 1.229 | 1.175 | 0.90503 | 0.783 | 0.70209 | 0.68185 | 0.67688
43602.4336 | 1.0329 | 1.2238 | 1.1733 | 0.90228 | 0.78038 | 0.70046 | 0.67946 | 0.67625
43602.4336 | 1.0354 | 1.2269 | 1.1741 | 0.90473 | 0.78007 | 0.70031 | 0.68073 | 0.67642
43602.4337 | 1.0388 | 1.2259 | 1.1728 | 0.90341 | 0.78118 | 0.70076 | 0.68053 | 0.67685
43602.4337 | 1.031 | 1.2222 | 1.171 | 0.90125 | 0.77948 | 0.69984 | 0.68149 | 0.676
43602.4337 | 1.0379 | 1.2237 | 1.1703 | 0.9019 | 0.77861 | 0.69905 | 0.68199 | 0.67609
43602.4337 | 1.0374 | 1.2227 | 1.17 | 0.90165 | 0.77976 | 0.69881 | 0.67886 | 0.67587
43602.4337 | 1.0338 | 1.2221 | 1.1686 | 0.90012 | 0.77793 | 0.69799 | 0.67849 | 0.67548
43602.4337 | 1.0378 | 1.2222 | 1.1691 | 0.90046 | 0.77814 | 0.69817 | 0.67825 | 0.67546
43602.4337 | 1.0395 | 1.222 | 1.1679 | 0.90073 | 0.77758 | 0.69744 | 0.68064 | 0.67492
43602.4337 | 1.0297 | 1.2195 | 1.1674 | 0.89989 | 0.77801 | 0.69793 | 0.67883 | 0.67515
43602.4337 | 1.0324 | 1.2207 | 1.1676 | 0.89979 | 0.77718 | 0.69723 | 0.67805 | 0.67514
43602.4338 | 1.0336 | 1.2205 | 1.1666 | 0.8995 | 0.77717 | 0.6971 | 0.67754 | 0.67495
43602.4338 | 1.0358 | 1.2192 | 1.1664 | 0.89831 | 0.77671 | 0.69665 | 0.67693 | 0.67476
43602.4338 | 1.0333 | 1.2198 | 1.1668 | 0.89928 | 0.7769 | 0.69686 | 0.68154 | 0.67469
43602.4338 | 1.0367 | 1.2206 | 1.1667 | 0.90017 | 0.77688 | 0.69694 | 0.6785 | 0.67462
43602.4338 | 1.0312 | 1.2205 | 1.1668 | 0.90033 | 0.77712 | 0.69695 | 0.67781 | 0.67471
43602.4338 | 1.0339 | 1.2203 | 1.1667 | 0.89994 | 0.77735 | 0.69726 | 0.67772 | 0.67476
43602.4338 | 1.0369 | 1.2208 | 1.1663 | 0.89977 | 0.77708 | 0.69699 | 0.6776 | 0.67491
43602.4338 | 1.0359 | 1.2218 | 1.1671 | 0.90064 | 0.77738 | 0.69719 | 0.6772 | 0.67462
43602.4338 | 1.0325 | 1.2204 | 1.1665 | 0.90036 | 0.7785 | 0.69755 | 0.6802 | 0.67468
43602.4339 | 1.0351 | 1.2207 | 1.1657 | 0.90035 | 0.77679 | 0.69657 | 0.67694 | 0.67454
43602.4339 | 1.0358 | 1.221 | 1.1659 | 0.90089 | 0.77792 | 0.69736 | 0.67711 | 0.67445
43602.4339 | 1.0377 | 1.2212 | 1.1657 | 0.90103 | 0.77894 | 0.69775 | 0.67876 | 0.67447
43602.4339 | 1.0334 | 1.22 | 1.1648 | 0.89989 | 0.77667 | 0.69672 | 0.67656 | 0.6742
43602.4339 | 1.0369 | 1.2215 | 1.1661 | 0.9016 | 0.77785 | 0.69717 | 0.67779 | 0.67453
43602.4339 | 1.0448 | 1.2213 | 1.1658 | 0.90115 | 0.77796 | 0.69701 | 0.68305 | 0.67404
43602.4339 | 1.0446 | 1.2223 | 1.1656 | 0.90294 | 0.7788 | 0.69753 | 0.67895 | 0.67439
43602.4339 | 1.0359 | 1.2182 | 1.164 | 0.89924 | 0.77723 | 0.69719 | 0.67782 | 0.67377
43602.434 | 1.037 | 1.2199 | 1.1651 | 0.90159 | 0.77804 | 0.69721 | 0.67743 | 0.67425
43602.434 | 1.0353 | 1.2211 | 1.1643 | 0.90098 | 0.77761 | 0.69719 | 0.67843 | 0.6742
43602.434 | 1.0395 | 1.2205 | 1.1638 | 0.90136 | 0.77756 | 0.69702 | 0.67762 | 0.67398
43602.434 | 1.0411 | 1.2213 | 1.1644 | 0.90274 | 0.7789 | 0.69763 | 0.67745 | 0.67408
43602.434 | 1.0397 | 1.2183 | 1.162 | 0.89981 | 0.77759 | 0.69687 | 0.67716 | 0.67372
43602.434 | 1.0378 | 1.2166 | 1.1611 | 0.89944 | 0.77678 | 0.69632 | 0.67672 | 0.67361
43602.434 | 1.0336 | 1.2182 | 1.1626 | 0.90053 | 0.77633 | 0.69594 | 0.67726 | 0.67364
43602.434 | 1.0402 | 1.2182 | 1.1615 | 0.90144 | 0.7776 | 0.69706 | 0.68112 | 0.67417
43602.434 | 1.0326 | 1.2144 | 1.1594 | 0.89865 | 0.77697 | 0.69613 | 0.6773 | 0.67349
43602.4341 | 1.0332 | 1.2162 | 1.1596 | 0.89988 | 0.77563 | 0.69546 | 0.6762 | 0.67308
43602.4341 | 1.0358 | 1.2141 | 1.1582 | 0.89894 | 0.77617 | 0.69558 | 0.67639 | 0.67302
43602.4341 | 1.0356 | 1.2139 | 1.1581 | 0.8991 | 0.77604 | 0.69576 | 0.67694 | 0.67329
43602.4341 | 1.0349 | 1.2113 | 1.1555 | 0.89713 | 0.77393 | 0.69447 | 0.67951 | 0.6726
43602.4341 | 1.0391 | 1.2158 | 1.1587 | 0.89989 | 0.77597 | 0.69528 | 0.67674 | 0.67339
43602.4341 | 1.0366 | 1.2131 | 1.1566 | 0.89811 | 0.77599 | 0.69543 | 0.6758 | 0.67292
43602.4341 | 1.0322 | 1.2127 | 1.1558 | 0.89756 | 0.77562 | 0.69501 | 0.67536 | 0.67286
43602.4341 | 1.0366 | 1.2134 | 1.1551 | 0.89814 | 0.77521 | 0.69481 | 0.67645 | 0.67269
43602.4341 | 1.03 | 1.2097 | 1.154 | 0.89642 | 0.7743 | 0.69425 | 0.6745 | 0.67258
43602.4342 | 1.0388 | 1.2126 | 1.1546 | 0.89832 | 0.77397 | 0.69427 | 0.67473 | 0.67257
43602.4342 | 1.0375 | 1.213 | 1.1552 | 0.89888 | 0.77554 | 0.69509 | 0.67503 | 0.67295
43602.4342 | 1.0271 | 1.2108 | 1.154 | 0.89684 | 0.77467 | 0.69452 | 0.67644 | 0.67244
43602.4342 | 1.0361 | 1.2096 | 1.1524 | 0.89666 | 0.77453 | 0.69479 | 0.67946 | 0.67252
43602.4342 | 1.0272 | 1.2078 | 1.1516 | 0.89554 | 0.77333 | 0.69334 | 0.67557 | 0.67239
43602.4342 | 1.0351 | 1.2091 | 1.1509 | 0.89582 | 0.77292 | 0.69296 | 0.67473 | 0.67236
43602.4342 | 1.0324 | 1.208 | 1.1507 | 0.89544 | 0.77318 | 0.69318 | 0.6744 | 0.67243
43602.4342 | 1.0335 | 1.2091 | 1.1513 | 0.8966 | 0.77352 | 0.69341 | 0.67332 | 0.67247
43602.4342 | 1.0269 | 1.2052 | 1.1489 | 0.89368 | 0.77313 | 0.69312 | 0.67493 | 0.67187
43602.4343 | 1.0356 | 1.2082 | 1.1494 | 0.89588 | 0.77141 | 0.69205 | 0.67279 | 0.67125
43602.4343 | 1.0307 | 1.2069 | 1.1495 | 0.89569 | 0.7746 | 0.69388 | 0.67429 | 0.67256
43602.4343 | 1.0348 | 1.2049 | 1.1475 | 0.8946 | 0.77153 | 0.69228 | 0.67293 | 0.672
43602.4343 | 1.0333 | 1.2075 | 1.1489 | 0.89563 | 0.77286 | 0.69295 | 0.67439 | 0.67232
43602.4343 | 1.0233 | 1.2035 | 1.1466 | 0.89317 | 0.77228 | 0.69307 | 0.68192 | 0.67202
43602.4343 | 1.0276 | 1.2024 | 1.1453 | 0.8923 | 0.77038 | 0.69167 | 0.67425 | 0.67168
43602.4343 | 1.0343 | 1.203 | 1.1449 | 0.89259 | 0.77003 | 0.69116 | 0.67319 | 0.67151
43602.4343 | 1.0298 | 1.2032 | 1.1452 | 0.89329 | 0.77057 | 0.69145 | 0.67357 | 0.67113
43602.4343 | 1.0364 | 1.2066 | 1.1473 | 0.89538 | 0.77117 | 0.69182 | 0.67319 | 0.67164
43602.4344 | 1.0332 | 1.2035 | 1.1456 | 0.89307 | 0.77286 | 0.69305 | 0.67368 | 0.67212
43602.4344 | 1.0401 | 1.2059 | 1.1462 | 0.89471 | 0.77051 | 0.69137 | 0.67099 | 0.67096
43602.4344 | 1.0333 | 1.2016 | 1.1437 | 0.89249 | 0.77148 | 0.69206 | 0.67374 | 0.67143
43602.4344 | 1.0341 | 1.2028 | 1.1446 | 0.8934 | 0.77107 | 0.69145 | 0.67236 | 0.67144
43602.4344 | 1.0385 | 1.2017 | 1.143 | 0.89187 | 0.76971 | 0.69074 | 0.67191 | 0.67085
43602.4344 | 1.0467 | 1.2108 | 1.1502 | 0.89877 | 0.7723 | 0.69246 | 0.67362 | 0.67209
43602.4344 | 1.031 | 1.2025 | 1.1454 | 0.8936 | 0.77516 | 0.69419 | 0.6761 | 0.67225
43602.4344 | 1.0204 | 1.2032 | 1.1456 | 0.89391 | 0.76961 | 0.69117 | 0.67753 | 0.67085
43602.4344 | 1.0402 | 1.2021 | 1.1436 | 0.89255 | 0.77149 | 0.69219 | 0.67383 | 0.67163
43602.4345 | 1.03 | 1.2042 | 1.1453 | 0.89388 | 0.77176 | 0.69205 | 0.67432 | 0.67126
43602.4345 | 1.0311 | 1.2039 | 1.1459 | 0.89479 | 0.77212 | 0.69248 | 0.67434 | 0.67156
43602.4345 | 1.0291 | 1.2044 | 1.1463 | 0.89468 | 0.77232 | 0.69294 | 0.67477 | 0.67189
43602.4345 | 1.0347 | 1.2053 | 1.1465 | 0.89571 | 0.77176 | 0.69257 | 0.67284 | 0.67158
43602.4345 | 1.0361 | 1.2044 | 1.1463 | 0.89563 | 0.77231 | 0.69281 | 0.67276 | 0.67181
43602.4345 | 1.0296 | 1.206 | 1.1478 | 0.89612 | 0.77462 | 0.69435 | 0.67745 | 0.672
43602.4345 | 1.051 | 1.2102 | 1.1493 | 0.89924 | 0.7745 | 0.69413 | 0.67521 | 0.6717
43602.4345 | 1.0458 | 1.2067 | 1.1472 | 0.89653 | 0.77591 | 0.69477 | 0.67611 | 0.67232
43602.4345 | 1.0398 | 1.2047 | 1.1455 | 0.89564 | 0.77382 | 0.69362 | 0.67417 | 0.67183
43602.4346 | 1.047 | 1.2102 | 1.1485 | 0.89813 | 0.77419 | 0.69357 | 0.67487 | 0.67184
43602.4346 | 1.0424 | 1.2088 | 1.1492 | 0.89843 | 0.77607 | 0.69481 | 0.67977 | 0.67222
43602.4346 | 1.0319 | 1.2059 | 1.1475 | 0.89619 | 0.77442 | 0.69416 | 0.67622 | 0.67211
43602.4346 | 1.047 | 1.2064 | 1.1468 | 0.8964 | 0.77418 | 0.69391 | 0.67562 | 0.67196
43602.4346 | 1.0538 | 1.2085 | 1.1482 | 0.89847 | 0.77482 | 0.69363 | 0.67465 | 0.67208
43602.4346 | 1.0469 | 1.208 | 1.1468 | 0.89705 | 0.77591 | 0.69469 | 0.67531 | 0.67214
43602.4346 | 1.0407 | 1.2058 | 1.1454 | 0.89586 | 0.7741 | 0.69365 | 0.67451 | 0.67185
43602.4346 | 1.0459 | 1.2107 | 1.1493 | 0.8993 | 0.77602 | 0.69486 | 0.67547 | 0.6726
43602.4346 | 1.0383 | 1.2104 | 1.1494 | 0.899 | 0.77546 | 0.6953 | 0.6793 | 0.67288
43602.4347 | 1.0454 | 1.2073 | 1.1464 | 0.89667 | 0.77549 | 0.69491 | 0.67588 | 0.67205
43602.4347 | 1.0446 | 1.2079 | 1.1475 | 0.89732 | 0.77486 | 0.69421 | 0.67566 | 0.67215
43602.4347 | 1.0489 | 1.2091 | 1.1485 | 0.89809 | 0.77407 | 0.69383 | 0.67535 | 0.67196
43602.4347 | 1.0384 | 1.2059 | 1.1468 | 0.8965 | 0.77718 | 0.69605 | 0.6777 | 0.67274
43602.4347 | 1.0455 | 1.2085 | 1.1487 | 0.89879 | 0.77395 | 0.69401 | 0.67643 | 0.67234
43602.4347 | 1.0494 | 1.2086 | 1.1486 | 0.89869 | 0.77511 | 0.69452 | 0.67475 | 0.6723
43602.4347 | 1.0395 | 1.2096 | 1.1496 | 0.89828 | 0.77562 | 0.69494 | 0.67558 | 0.67233
43602.4347 | 1.0445 | 1.2079 | 1.148 | 0.89729 | 0.7767 | 0.69557 | 0.67605 | 0.67253
43602.4347 | 1.0453 | 1.2056 | 1.146 | 0.89557 | 0.77329 | 0.69338 | 0.6735 | 0.67165
43602.4348 | 1.047 | 1.21 | 1.1491 | 0.89835 | 0.77502 | 0.69448 | 0.67908 | 0.67223
43602.4348 | 1.0489 | 1.2109 | 1.1501 | 0.89929 | 0.77585 | 0.69511 | 0.67632 | 0.67242
43602.4348 | 1.0511 | 1.2078 | 1.1477 | 0.89711 | 0.77487 | 0.6942 | 0.67568 | 0.67214
43602.4348 | 1.0483 | 1.2104 | 1.1498 | 0.89887 | 0.77615 | 0.695 | 0.67533 | 0.67204
43602.4348 | 1.0463 | 1.2108 | 1.1502 | 0.89955 | 0.77543 | 0.6946 | 0.67612 | 0.67235
43602.4348 | 1.0427 | 1.2088 | 1.1489 | 0.89728 | 0.77643 | 0.69552 | 0.67621 | 0.67264
43602.4348 | 1.0549 | 1.2168 | 1.1542 | 0.903 | 0.77723 | 0.69577 | 0.67577 | 0.6727
43602.4348 | 1.0509 | 1.212 | 1.1508 | 0.89949 | 0.77797 | 0.69637 | 0.67683 | 0.67296
43602.4348 | 1.0467 | 1.2111 | 1.1508 | 0.89954 | 0.77738 | 0.69612 | 0.67683 | 0.67309
43602.4349 | 1.0539 | 1.2114 | 1.1508 | 0.89927 | 0.7759 | 0.69503 | 0.6816 | 0.6724
43602.4349 | 1.0408 | 1.2132 | 1.1532 | 0.9008 | 0.77768 | 0.69653 | 0.67867 | 0.67321
43602.4349 | 1.0564 | 1.2134 | 1.1524 | 0.90091 | 0.77912 | 0.69751 | 0.67802 | 0.67354
43602.4349 | 1.0481 | 1.2095 | 1.1502 | 0.89843 | 0.77492 | 0.69449 | 0.67547 | 0.67178
43602.4349 | 1.046 | 1.2139 | 1.1531 | 0.90071 | 0.77807 | 0.69649 | 0.67621 | 0.67314
43602.4349 | 1.0516 | 1.2149 | 1.1539 | 0.90178 | 0.77691 | 0.69631 | 0.67616 | 0.67285
43602.4349 | 1.0353 | 1.2122 | 1.1528 | 0.89932 | 0.77802 | 0.69706 | 0.67893 | 0.67323
43602.4349 | 1.0516 | 1.215 | 1.154 | 0.90145 | 0.77735 | 0.69646 | 0.67738 | 0.67317
43602.4349 | 1.0521 | 1.2162 | 1.1551 | 0.90285 | 0.77895 | 0.69728 | 0.67865 | 0.67343
43602.435 | 1.0458 | 1.2117 | 1.1526 | 0.89993 | 0.77644 | 0.69592 | 0.67801 | 0.67312
43602.435 | 1.0426 | 1.2129 | 1.1528 | 0.89988 | 0.77723 | 0.69593 | 0.67684 | 0.67336
43602.435 | 1.0381 | 1.2155 | 1.1551 | 0.9019 | 0.77783 | 0.69715 | 0.67778 | 0.67361
43602.435 | 1.0493 | 1.2133 | 1.1524 | 0.89965 | 0.7768 | 0.69569 | 0.67587 | 0.67308
43602.435 | 1.0435 | 1.2129 | 1.1531 | 0.90006 | 0.77731 | 0.69612 | 0.68012 | 0.67347
43602.435 | 1.0405 | 1.2142 | 1.1536 | 0.89964 | 0.7771 | 0.69624 | 0.68015 | 0.67324
43602.435 | 1.0503 | 1.2165 | 1.1556 | 0.90171 | 0.77637 | 0.69633 | 0.67794 | 0.67364
43602.435 | 1.0494 | 1.2148 | 1.1551 | 0.90119 | 0.77955 | 0.69755 | 0.67806 | 0.67376
43602.435 | 1.0425 | 1.2126 | 1.1535 | 0.89937 | 0.7758 | 0.69565 | 0.67653 | 0.67335
43602.4351 | 1.0408 | 1.2181 | 1.1579 | 0.90305 | 0.77747 | 0.69645 | 0.67666 | 0.67394
43602.4351 | 1.0483 | 1.2172 | 1.1567 | 0.90192 | 0.77878 | 0.69708 | 0.67743 | 0.67431
43602.4351 | 1.0513 | 1.22 | 1.1589 | 0.90368 | 0.7796 | 0.6983 | 0.68132 | 0.67462
43602.4351 | 1.0321 | 1.2131 | 1.1552 | 0.8988 | 0.77886 | 0.69784 | 0.67973 | 0.6743
43602.4351 | 1.0386 | 1.2112 | 1.1528 | 0.89784 | 0.77501 | 0.69548 | 0.67642 | 0.67362
43602.4351 | 1.0345 | 1.2109 | 1.153 | 0.8976 | 0.77454 | 0.69496 | 0.67558 | 0.67365
43602.4351 | 1.0433 | 1.2157 | 1.1558 | 0.90089 | 0.77623 | 0.69557 | 0.67614 | 0.67414
43602.4351 | 1.0416 | 1.2131 | 1.1539 | 0.898 | 0.77658 | 0.69578 | 0.67944 | 0.67411
43602.4351 | 1.0363 | 1.2122 | 1.1541 | 0.8982 | 0.77501 | 0.69493 | 0.67612 | 0.67359
43602.4352 | 1.0381 | 1.2143 | 1.155 | 0.89972 | 0.77552 | 0.69545 | 0.67695 | 0.67426
43602.4352 | 1.0371 | 1.211 | 1.1531 | 0.89725 | 0.77577 | 0.6954 | 0.67702 | 0.67388
43602.4352 | 1.0351 | 1.2116 | 1.1535 | 0.89787 | 0.77516 | 0.69501 | 0.67479 | 0.67427
43602.4352 | 1.0283 | 1.2091 | 1.1526 | 0.89557 | 0.77353 | 0.69364 | 0.67522 | 0.67339
43602.4352 | 1.0343 | 1.212 | 1.1547 | 0.89768 | 0.77585 | 0.69553 | 0.67991 | 0.67495
43602.4352 | 1.0295 | 1.2089 | 1.1519 | 0.89506 | 0.77299 | 0.69386 | 0.676 | 0.67339
43602.4352 | 1.0283 | 1.2092 | 1.1527 | 0.89547 | 0.77441 | 0.69417 | 0.67539 | 0.67406
43602.4352 | 1.0268 | 1.2081 | 1.1524 | 0.89467 | 0.77305 | 0.69392 | 0.67497 | 0.67377
43602.4352 | 1.0319 | 1.208 | 1.1513 | 0.89487 | 0.77273 | 0.69313 | 0.67328 | 0.67371
43602.4353 | 1.0259 | 1.2081 | 1.1521 | 0.89479 | 0.77245 | 0.69304 | 0.67713 | 0.67352
43602.4353 | 1.0193 | 1.2051 | 1.1504 | 0.89242 | 0.77368 | 0.69372 | 0.67602 | 0.67408
43602.4353 | 1.0197 | 1.2041 | 1.1491 | 0.8915 | 0.77014 | 0.69152 | 0.67368 | 0.67333
43602.4353 | 1.0265 | 1.2041 | 1.1487 | 0.89188 | 0.77095 | 0.69205 | 0.6728 | 0.67348
43602.4353 | 1.0225 | 1.2018 | 1.147 | 0.88997 | 0.7696 | 0.69109 | 0.67108 | 0.67318
43602.4353 | 1.0196 | 1.2012 | 1.1468 | 0.88915 | 0.76934 | 0.69063 | 0.67654 | 0.67301
43602.4353 | 1.0172 | 1.1997 | 1.1453 | 0.88806 | 0.76766 | 0.68977 | 0.67285 | 0.67274
43602.4353 | 1.0171 | 1.2003 | 1.1456 | 0.88919 | 0.76841 | 0.68992 | 0.67251 | 0.67296
43602.4354 | 1.0113 | 1.1951 | 1.1426 | 0.88491 | 0.76654 | 0.68906 | 0.67131 | 0.67267
43602.4354 | 1.0083 | 1.1959 | 1.1425 | 0.88568 | 0.7654 | 0.68806 | 0.66954 | 0.67215
43602.4354 | 1.0071 | 1.1931 | 1.1406 | 0.88314 | 0.76472 | 0.68802 | 0.66929 | 0.67226
43602.4354 | 1.0113 | 1.1943 | 1.1399 | 0.88386 | 0.76343 | 0.68694 | 0.6729 | 0.67184
43602.4354 | 1.0064 | 1.1923 | 1.1391 | 0.88171 | 0.76399 | 0.6869 | 0.66954 | 0.67185
43602.4354 | 1.0051 | 1.1887 | 1.1366 | 0.8808 | 0.76138 | 0.68544 | 0.6678 | 0.67144
43602.4354 | 1.0046 | 1.1883 | 1.1373 | 0.88029 | 0.76158 | 0.68526 | 0.66743 | 0.67114
43602.4354 | 1.0024 | 1.1895 | 1.1366 | 0.88039 | 0.76081 | 0.68501 | 0.66688 | 0.67115
43602.4354 | 0.99854 | 1.1847 | 1.1345 | 0.87809 | 0.76007 | 0.68463 | 0.66731 | 0.67085
43602.4355 | 1.0015 | 1.186 | 1.1343 | 0.87846 | 0.75972 | 0.68383 | 0.66977 | 0.67088
43602.4355 | 0.99726 | 1.1843 | 1.1327 | 0.87689 | 0.75909 | 0.6834 | 0.66605 | 0.67056
43602.4355 | 1.0019 | 1.1844 | 1.1321 | 0.87631 | 0.75809 | 0.68268 | 0.66465 | 0.67043
43602.4355 | 0.99071 | 1.183 | 1.1323 | 0.87601 | 0.75746 | 0.68256 | 0.66481 | 0.67005
43602.4355 | 0.99707 | 1.1847 | 1.1319 | 0.87694 | 0.75796 | 0.68286 | 0.66341 | 0.67071
43602.4355 | 1.001 | 1.1852 | 1.1318 | 0.87635 | 0.75786 | 0.68256 | 0.66606 | 0.67012
43602.4355 | 0.99132 | 1.1827 | 1.1312 | 0.8756 | 0.75758 | 0.68229 | 0.66472 | 0.67017
43602.4355 | 0.99149 | 1.1794 | 1.1297 | 0.87407 | 0.75635 | 0.68168 | 0.66392 | 0.66995
43602.4355 | 0.99363 | 1.1816 | 1.1299 | 0.8759 | 0.75621 | 0.68134 | 0.6636 | 0.66994
43602.4356 | 0.99488 | 1.1817 | 1.1291 | 0.87538 | 0.7562 | 0.68115 | 0.66556 | 0.66996
43602.4356 | 0.99484 | 1.1796 | 1.1272 | 0.87386 | 0.75594 | 0.68089 | 0.66796 | 0.66971
43602.4356 | 0.98686 | 1.174 | 1.1253 | 0.87036 | 0.75389 | 0.67951 | 0.66312 | 0.66892
43602.4356 | 0.98728 | 1.1754 | 1.1244 | 0.87117 | 0.75224 | 0.67829 | 0.66143 | 0.66854
43602.4356 | 0.98627 | 1.1764 | 1.1245 | 0.87201 | 0.75375 | 0.67942 | 0.66176 | 0.66918
43602.4356 | 0.99007 | 1.177 | 1.1246 | 0.87222 | 0.75332 | 0.67917 | 0.66127 | 0.66879
43602.4356 | 0.99262 | 1.1772 | 1.1244 | 0.87238 | 0.75376 | 0.67871 | 0.66124 | 0.66848
43602.4356 | 0.98616 | 1.1742 | 1.1244 | 0.87005 | 0.75277 | 0.67833 | 0.65997 | 0.66824
43602.4356 | 0.98732 | 1.1775 | 1.1251 | 0.87281 | 0.75375 | 0.67908 | 0.66161 | 0.66877
43602.4357 | 0.99408 | 1.1776 | 1.1246 | 0.87238 | 0.75337 | 0.67864 | 0.66649 | 0.66827
43602.4357 | 0.99191 | 1.1794 | 1.1264 | 0.8734 | 0.75389 | 0.67895 | 0.66276 | 0.66865
43602.4357 | 1.0005 | 1.1818 | 1.1271 | 0.8749 | 0.75511 | 0.67946 | 0.6624 | 0.66867
43602.4357 | 1.002 | 1.186 | 1.1297 | 0.87721 | 0.75613 | 0.68009 | 0.66228 | 0.66887
43602.4357 | 0.99886 | 1.1862 | 1.1317 | 0.87951 | 0.75815 | 0.6815 | 0.66308 | 0.66945
43602.4357 | 1.0077 | 1.1878 | 1.132 | 0.87843 | 0.75923 | 0.68227 | 0.66347 | 0.66946
43602.4357 | 1.0056 | 1.191 | 1.135 | 0.88167 | 0.75884 | 0.68239 | 0.66668 | 0.66936
43602.4357 | 1.0124 | 1.1932 | 1.136 | 0.88272 | 0.76172 | 0.68424 | 0.6657 | 0.67023
43602.4357 | 1.02 | 1.1985 | 1.1395 | 0.887 | 0.76357 | 0.68535 | 0.66673 | 0.67018
43602.4358 | 1.0189 | 1.1998 | 1.1413 | 0.88741 | 0.76575 | 0.68683 | 0.66772 | 0.67117
43602.4358 | 1.0278 | 1.2019 | 1.1427 | 0.88933 | 0.76622 | 0.68735 | 0.66967 | 0.67065
43602.4358 | 1.0233 | 1.2029 | 1.1442 | 0.88965 | 0.76735 | 0.68841 | 0.67542 | 0.67096
43602.4358 | 1.0312 | 1.207 | 1.1476 | 0.89344 | 0.76943 | 0.69006 | 0.672 | 0.67164
43602.4358 | 1.0363 | 1.2066 | 1.1474 | 0.89305 | 0.77078 | 0.69107 | 0.67186 | 0.67204
43602.4358 | 1.0377 | 1.2086 | 1.1498 | 0.89495 | 0.77184 | 0.69162 | 0.6724 | 0.67239
43602.4358 | 1.038 | 1.2119 | 1.1525 | 0.8964 | 0.77409 | 0.69318 | 0.67265 | 0.67288
43602.4358 | 1.0424 | 1.2146 | 1.1539 | 0.89811 | 0.7742 | 0.69375 | 0.67441 | 0.67324
43602.4358 | 1.0411 | 1.2125 | 1.1528 | 0.89717 | 0.77597 | 0.69518 | 0.67518 | 0.67387
43602.4359 | 1.031 | 1.2115 | 1.1519 | 0.89523 | 0.77406 | 0.69373 | 0.67416 | 0.67326
43602.4359 | 1.0359 | 1.2129 | 1.1529 | 0.8968 | 0.77364 | 0.69341 | 0.67786 | 0.67308
43602.4359 | 1.0311 | 1.21 | 1.1511 | 0.89477 | 0.77364 | 0.69389 | 0.67466 | 0.67329
43602.4359 | 1.0398 | 1.2143 | 1.1533 | 0.8972 | 0.77472 | 0.69388 | 0.675 | 0.67346
43602.4359 | 1.029 | 1.2136 | 1.1539 | 0.89731 | 0.7744 | 0.69402 | 0.67485 | 0.67356
43602.4359 | 1.035 | 1.214 | 1.1543 | 0.8975 | 0.77578 | 0.69495 | 0.67605 | 0.67426
43602.4359 | 1.0404 | 1.2138 | 1.1536 | 0.89705 | 0.77458 | 0.69415 | 0.67489 | 0.67373
43602.4359 | 1.0324 | 1.2128 | 1.1531 | 0.89654 | 0.77465 | 0.69435 | 0.67435 | 0.67386
43602.4359 | 1.0329 | 1.2096 | 1.1511 | 0.89412 | 0.77437 | 0.69405 | 0.67502 | 0.67386
43602.436 | 1.0342 | 1.2119 | 1.1531 | 0.89628 | 0.77204 | 0.69266 | 0.6794 | 0.67354
43602.436 | 1.0259 | 1.2062 | 1.1489 | 0.8915 | 0.77296 | 0.69341 | 0.67636 | 0.6736
43602.436 | 1.0248 | 1.2063 | 1.1494 | 0.89164 | 0.7706 | 0.69237 | 0.67425 | 0.67363
43602.436 | 1.0246 | 1.2066 | 1.1491 | 0.89254 | 0.77075 | 0.69202 | 0.67329 | 0.67381
43602.436 | 1.0182 | 1.2053 | 1.1496 | 0.89134 | 0.76979 | 0.69175 | 0.67315 | 0.67331
43602.436 | 1.0216 | 1.2073 | 1.1492 | 0.89214 | 0.77072 | 0.69232 | 0.67252 | 0.67407
43602.436 | 1.0168 | 1.2013 | 1.1458 | 0.88802 | 0.76968 | 0.69117 | 0.67184 | 0.67331
43602.436 | 1.0127 | 1.199 | 1.1443 | 0.88556 | 0.76614 | 0.68914 | 0.67242 | 0.67259
43602.436 | 1.0198 | 1.202 | 1.1448 | 0.88789 | 0.7666 | 0.68932 | 0.67061 | 0.67289
43602.4361 | 1.0163 | 1.1986 | 1.1428 | 0.88508 | 0.76666 | 0.689 | 0.67054 | 0.67275
43602.4361 | 1.0168 | 1.1973 | 1.1414 | 0.88367 | 0.76443 | 0.68775 | 0.66941 | 0.67244
43602.4361 | 1.0118 | 1.1977 | 1.1417 | 0.88412 | 0.76405 | 0.68761 | 0.67257 | 0.6724
43602.4361 | 1.0082 | 1.1943 | 1.1396 | 0.88283 | 0.76392 | 0.68699 | 0.67306 | 0.67241
43602.4361 | 1.0044 | 1.1905 | 1.1376 | 0.87912 | 0.76177 | 0.68602 | 0.66863 | 0.67164
43602.4361 | 1.0035 | 1.1899 | 1.1369 | 0.87953 | 0.76042 | 0.68501 | 0.66829 | 0.67138
43602.4361 | 0.99979 | 1.1875 | 1.1358 | 0.87797 | 0.75982 | 0.68454 | 0.66733 | 0.67126
43602.4361 | 1.0023 | 1.187 | 1.135 | 0.87791 | 0.75889 | 0.6837 | 0.66593 | 0.67113
43602.4361 | 0.99723 | 1.1867 | 1.1352 | 0.8772 | 0.759 | 0.6838 | 0.66568 | 0.67138
43602.4362 | 0.99486 | 1.1837 | 1.1332 | 0.87513 | 0.75748 | 0.68276 | 0.66391 | 0.67083
43602.4362 | 0.99576 | 1.1843 | 1.1338 | 0.87545 | 0.75712 | 0.6827 | 0.66611 | 0.67078
43602.4362 | 0.9976 | 1.1847 | 1.1338 | 0.87488 | 0.7562 | 0.68175 | 0.66416 | 0.67059
43602.4362 | 0.99677 | 1.1828 | 1.1328 | 0.87333 | 0.75648 | 0.68214 | 0.6648 | 0.67055
43602.4362 | 0.99622 | 1.183 | 1.1325 | 0.87423 | 0.75626 | 0.68158 | 0.66502 | 0.67025
43602.4362 | 0.99099 | 1.1817 | 1.1336 | 0.87373 | 0.756 | 0.68156 | 0.66669 | 0.67044
43602.4362 | 0.99135 | 1.1808 | 1.1327 | 0.8723 | 0.75525 | 0.68165 | 0.66404 | 0.67042
43602.4362 | 0.99624 | 1.185 | 1.1346 | 0.87452 | 0.75571 | 0.68134 | 0.66412 | 0.6707
43602.4362 | 0.9914 | 1.1847 | 1.1358 | 0.87462 | 0.75704 | 0.68216 | 0.665 | 0.67084
43602.4363 | 0.99558 | 1.1852 | 1.1338 | 0.87457 | 0.75602 | 0.68168 | 0.66328 | 0.6702
43602.4363 | 0.99334 | 1.1825 | 1.1347 | 0.87224 | 0.75603 | 0.68157 | 0.66494 | 0.67021
43602.4363 | 0.99371 | 1.1847 | 1.135 | 0.87406 | 0.75571 | 0.68123 | 0.66241 | 0.67017
43602.4363 | 0.9926 | 1.1847 | 1.1359 | 0.87347 | 0.75638 | 0.68165 | 0.66423 | 0.67035
43602.4363 | 1.0002 | 1.1895 | 1.1377 | 0.8766 | 0.75691 | 0.68215 | 0.66411 | 0.67051
43602.4363 | 0.99413 | 1.1852 | 1.1362 | 0.87362 | 0.75723 | 0.68226 | 0.66596 | 0.6707
43602.4363 | 0.99217 | 1.1849 | 1.1368 | 0.87331 | 0.75611 | 0.68159 | 0.66823 | 0.67031
43602.4363 | 0.99455 | 1.1858 | 1.1367 | 0.87285 | 0.75559 | 0.68135 | 0.66389 | 0.67006
43602.4363 | 0.99713 | 1.1873 | 1.1386 | 0.87495 | 0.75685 | 0.68182 | 0.66445 | 0.67039
43602.4364 | 0.99996 | 1.1893 | 1.138 | 0.87581 | 0.75695 | 0.68196 | 0.66404 | 0.67017
43602.4364 | 0.992 | 1.1852 | 1.1379 | 0.87451 | 0.75707 | 0.68205 | 0.66222 | 0.67026
43602.4364 | 0.99232 | 1.1859 | 1.1383 | 0.87445 | 0.75633 | 0.68185 | 0.66546 | 0.67031
43602.4364 | 0.99509 | 1.186 | 1.1377 | 0.87353 | 0.75634 | 0.68162 | 0.66338 | 0.66996
43602.4364 | 0.99246 | 1.1873 | 1.1391 | 0.8749 | 0.75653 | 0.68156 | 0.66352 | 0.67019
43602.4364 | 0.99373 | 1.1868 | 1.1386 | 0.87406 | 0.75708 | 0.68181 | 0.66682 | 0.67006
43602.4364 | 0.99336 | 1.1869 | 1.1386 | 0.87381 | 0.75656 | 0.68171 | 0.6654 | 0.67003
43602.4364 | 0.99709 | 1.1876 | 1.1383 | 0.87428 | 0.75639 | 0.68135 | 0.66349 | 0.67016
43602.4364 | 0.9908 | 1.1867 | 1.1389 | 0.87394 | 0.75679 | 0.6816 | 0.66378 | 0.66999
43602.4365 | 0.99697 | 1.1885 | 1.1398 | 0.87478 | 0.75633 | 0.68138 | 0.6626 | 0.66995
43602.4365 | 0.9942 | 1.1893 | 1.1414 | 0.87513 | 0.7571 | 0.68203 | 0.66391 | 0.66995
43602.4365 | 1.0002 | 1.1924 | 1.1423 | 0.87767 | 0.75819 | 0.68255 | 0.66561 | 0.67044
43602.4365 | 0.99364 | 1.1881 | 1.1416 | 0.87413 | 0.7578 | 0.68248 | 0.66402 | 0.66988
43602.4365 | 1.0007 | 1.1911 | 1.1419 | 0.87508 | 0.75711 | 0.6819 | 0.66381 | 0.66997
43602.4365 | 1.0006 | 1.1921 | 1.1424 | 0.87694 | 0.75805 | 0.68229 | 0.6639 | 0.66995
43602.4365 | 0.99983 | 1.1932 | 1.143 | 0.87646 | 0.75854 | 0.68276 | 0.66926 | 0.66995
43602.4365 | 0.99825 | 1.1931 | 1.1444 | 0.87733 | 0.75875 | 0.68287 | 0.66559 | 0.67027
43602.4365 | 1.0019 | 1.195 | 1.1458 | 0.87814 | 0.75974 | 0.68348 | 0.66525 | 0.67043
43602.4366 | 1.0044 | 1.196 | 1.1465 | 0.8784 | 0.75957 | 0.6839 | 0.665 | 0.67052
43602.4366 | 1.007 | 1.1992 | 1.1485 | 0.88007 | 0.76072 | 0.68422 | 0.66514 | 0.6709
43602.4366 | 1.0021 | 1.1995 | 1.1488 | 0.88056 | 0.76177 | 0.6849 | 0.6666 | 0.67101
43602.4366 | 1.0047 | 1.1999 | 1.1498 | 0.88064 | 0.76263 | 0.68558 | 0.66894 | 0.67139
43602.4366 | 1.0085 | 1.2016 | 1.1508 | 0.8816 | 0.76253 | 0.68586 | 0.66837 | 0.67122
43602.4366 | 1.0054 | 1.2025 | 1.1528 | 0.88209 | 0.76297 | 0.68643 | 0.66756 | 0.67112
43602.4366 | 1.0103 | 1.2035 | 1.1529 | 0.88307 | 0.76382 | 0.68672 | 0.66781 | 0.67142
43602.4366 | 1.0084 | 1.2029 | 1.1524 | 0.88279 | 0.76411 | 0.68661 | 0.6669 | 0.67146
43602.4366 | 1.0093 | 1.2026 | 1.1529 | 0.88138 | 0.76337 | 0.68632 | 0.67114 | 0.67142
43602.4367 | 1.0125 | 1.2047 | 1.1534 | 0.88407 | 0.76427 | 0.68706 | 0.66985 | 0.67176
43602.4367 | 1.0073 | 1.2034 | 1.1542 | 0.88313 | 0.76455 | 0.68744 | 0.66891 | 0.67153
43602.4367 | 1.0069 | 1.2049 | 1.1544 | 0.8851 | 0.7645 | 0.68733 | 0.6685 | 0.67144
43602.4367 | 1.0132 | 1.2046 | 1.1539 | 0.8836 | 0.76516 | 0.688 | 0.66883 | 0.67193
43602.4367 | 1.0105 | 1.2042 | 1.154 | 0.88343 | 0.76475 | 0.68722 | 0.66725 | 0.67111
43602.4367 | 1.0159 | 1.2039 | 1.1535 | 0.88341 | 0.76455 | 0.68714 | 0.66851 | 0.6714
43602.4367 | 1.0038 | 1.1993 | 1.1522 | 0.8805 | 0.76435 | 0.68722 | 0.67139 | 0.67127
43602.4367 | 1.0035 | 1.1996 | 1.152 | 0.8804 | 0.76279 | 0.68641 | 0.66793 | 0.67165
43602.4368 | 1.0073 | 1.1998 | 1.1507 | 0.88065 | 0.76262 | 0.68605 | 0.66719 | 0.67128
43602.4368 | 1.0052 | 1.199 | 1.1513 | 0.88034 | 0.76277 | 0.68625 | 0.66665 | 0.67163
43602.4368 | 1.0082 | 1.1977 | 1.1493 | 0.8799 | 0.76197 | 0.68553 | 0.66785 | 0.67105
43602.4368 | 1.0032 | 1.1952 | 1.149 | 0.87785 | 0.76145 | 0.685 | 0.66676 | 0.6714
43602.4368 | 1.0023 | 1.1942 | 1.1473 | 0.87744 | 0.76027 | 0.68448 | 0.66632 | 0.67061
43602.4368 | 0.99868 | 1.1923 | 1.1468 | 0.87685 | 0.76003 | 0.68425 | 0.66598 | 0.67111
43602.4368 | 1.0015 | 1.1949 | 1.1478 | 0.87807 | 0.75977 | 0.68422 | 0.66556 | 0.67066
43602.4368 | 1.0016 | 1.194 | 1.147 | 0.87679 | 0.76069 | 0.68442 | 0.67025 | 0.67104
43602.4368 | 1.0001 | 1.1908 | 1.145 | 0.87508 | 0.75904 | 0.68371 | 0.66533 | 0.67095
43602.4369 | 0.99317 | 1.1885 | 1.1444 | 0.87502 | 0.75848 | 0.68323 | 0.66452 | 0.67079
43602.4369 | 0.99217 | 1.1863 | 1.1429 | 0.87267 | 0.75751 | 0.68252 | 0.66369 | 0.67054
43602.4369 | 1.0004 | 1.1889 | 1.1423 | 0.87413 | 0.75707 | 0.68213 | 0.66375 | 0.67055
43602.4369 | 0.99155 | 1.1873 | 1.1429 | 0.87357 | 0.75739 | 0.68224 | 0.66335 | 0.67039
43602.4369 | 0.99581 | 1.1888 | 1.1426 | 0.87274 | 0.75659 | 0.68177 | 0.6642 | 0.67022
43602.4369 | 0.99628 | 1.1887 | 1.1431 | 0.87326 | 0.75709 | 0.682 | 0.6656 | 0.67048
43602.4369 | 0.99411 | 1.1899 | 1.1441 | 0.87476 | 0.75667 | 0.6818 | 0.66257 | 0.67026
43602.4369 | 0.99825 | 1.1901 | 1.144 | 0.87432 | 0.75776 | 0.68238 | 0.66416 | 0.67054
43602.4369 | 0.99651 | 1.1882 | 1.1425 | 0.87333 | 0.7576 | 0.68225 | 0.66379 | 0.67037
43602.437 | 0.98735 | 1.1849 | 1.142 | 0.87322 | 0.75623 | 0.6816 | 0.66798 | 0.67021
43602.437 | 0.99007 | 1.1865 | 1.1424 | 0.87306 | 0.75662 | 0.68202 | 0.66519 | 0.67069
43602.437 | 0.99465 | 1.1885 | 1.1433 | 0.87377 | 0.75683 | 0.6818 | 0.66372 | 0.67034
43602.437 | 0.99642 | 1.1903 | 1.1438 | 0.87422 | 0.75731 | 0.68214 | 0.66424 | 0.6702
43602.437 | 1.0035 | 1.1915 | 1.1442 | 0.87493 | 0.75756 | 0.68187 | 0.66313 | 0.67032
43602.437 | 0.99437 | 1.1898 | 1.1448 | 0.8745 | 0.75791 | 0.68268 | 0.66432 | 0.67038
43602.437 | 1.0043 | 1.1933 | 1.1462 | 0.87604 | 0.75846 | 0.68276 | 0.66541 | 0.67066
43602.437 | 0.99755 | 1.1927 | 1.1457 | 0.87555 | 0.75863 | 0.68288 | 0.66442 | 0.6706
43602.437 | 0.99912 | 1.1926 | 1.1458 | 0.8759 | 0.75875 | 0.68304 | 0.66468 | 0.6705
43602.4371 | 0.99808 | 1.1904 | 1.1454 | 0.87451 | 0.75815 | 0.68292 | 0.66442 | 0.67055
43602.4371 | 0.9996 | 1.1926 | 1.1459 | 0.87569 | 0.75762 | 0.68275 | 0.66897 | 0.67031
43602.4371 | 1.0004 | 1.1921 | 1.1464 | 0.87509 | 0.75905 | 0.68315 | 0.66573 | 0.67069
43602.4371 | 0.99918 | 1.1921 | 1.1461 | 0.87472 | 0.75845 | 0.68312 | 0.66457 | 0.6705
43602.4371 | 1.0067 | 1.1952 | 1.1471 | 0.87709 | 0.75904 | 0.68335 | 0.66434 | 0.67106
43602.4371 | 1.0043 | 1.1943 | 1.147 | 0.87608 | 0.75929 | 0.68332 | 0.6642 | 0.67085
43602.4371 | 1.0024 | 1.1947 | 1.1475 | 0.87604 | 0.75911 | 0.6838 | 0.66529 | 0.67092
43602.4371 | 1.0042 | 1.1956 | 1.1478 | 0.87627 | 0.75958 | 0.68378 | 0.66514 | 0.67085
43602.4371 | 0.99997 | 1.1955 | 1.1482 | 0.87663 | 0.75933 | 0.68378 | 0.6677 | 0.67085
43602.4372 | 0.99987 | 1.1962 | 1.1492 | 0.87779 | 0.76014 | 0.68416 | 0.66901 | 0.67102
43602.4372 | 1.0002 | 1.1994 | 1.1512 | 0.87985 | 0.76159 | 0.68515 | 0.66609 | 0.6713
43602.4372 | 1.0096 | 1.2009 | 1.1525 | 0.88027 | 0.76222 | 0.68567 | 0.66673 | 0.67128
43602.4372 | 1.0092 | 1.2022 | 1.1523 | 0.88127 | 0.76246 | 0.68559 | 0.66641 | 0.67156
43602.4372 | 1.0076 | 1.2015 | 1.1536 | 0.8807 | 0.76249 | 0.6859 | 0.66746 | 0.67183
43602.4372 | 1.0051 | 1.2029 | 1.1543 | 0.88209 | 0.76321 | 0.68675 | 0.6672 | 0.67221
43602.4372 | 1.0117 | 1.2038 | 1.1539 | 0.88184 | 0.7634 | 0.68688 | 0.67016 | 0.67205
43602.4372 | 1.0123 | 1.2043 | 1.1543 | 0.88228 | 0.76394 | 0.68687 | 0.66875 | 0.672
43602.4372 | 1.0108 | 1.2037 | 1.1535 | 0.88181 | 0.76355 | 0.68671 | 0.66758 | 0.67182
43602.4373 | 1.0086 | 1.205 | 1.1552 | 0.88228 | 0.76368 | 0.68694 | 0.66811 | 0.672
43602.4373 | 1.011 | 1.2066 | 1.1559 | 0.88488 | 0.76489 | 0.68755 | 0.66806 | 0.67256
43602.4373 | 1.0121 | 1.2048 | 1.1553 | 0.8826 | 0.76499 | 0.68797 | 0.66893 | 0.67235
43602.4373 | 1.0137 | 1.2059 | 1.1558 | 0.88406 | 0.76485 | 0.6876 | 0.66906 | 0.67228
43602.4373 | 1.0159 | 1.2074 | 1.1566 | 0.88452 | 0.76506 | 0.68814 | 0.66961 | 0.67205
43602.4373 | 1.011 | 1.2066 | 1.1572 | 0.88398 | 0.76608 | 0.68846 | 0.6691 | 0.67251
43602.4373 | 1.0157 | 1.2081 | 1.1576 | 0.88517 | 0.76601 | 0.68862 | 0.6752 | 0.67285
43602.4373 | 1.0171 | 1.2057 | 1.1565 | 0.88394 | 0.76581 | 0.68871 | 0.67148 | 0.67265
43602.4373 | 1.0188 | 1.2078 | 1.1575 | 0.88509 | 0.76567 | 0.68861 | 0.67087 | 0.67256
43602.4374 | 1.0175 | 1.2075 | 1.1568 | 0.8846 | 0.76616 | 0.68876 | 0.67052 | 0.67294
43602.4374 | 1.0098 | 1.2033 | 1.1551 | 0.88206 | 0.76501 | 0.6884 | 0.66997 | 0.67273
43602.4374 | 1.0148 | 1.2063 | 1.1561 | 0.88455 | 0.76514 | 0.68815 | 0.66768 | 0.67278
43602.4374 | 1.0139 | 1.2071 | 1.1572 | 0.88487 | 0.76603 | 0.6885 | 0.66944 | 0.67315
43602.4374 | 1.0139 | 1.2073 | 1.1571 | 0.88556 | 0.76642 | 0.6887 | 0.669 | 0.67287
43602.4374 | 1.0154 | 1.2052 | 1.1557 | 0.88321 | 0.76565 | 0.68854 | 0.66951 | 0.67295
43602.4374 | 1.0162 | 1.2078 | 1.1575 | 0.88496 | 0.76548 | 0.68827 | 0.67294 | 0.67288
43602.4374 | 1.0147 | 1.2057 | 1.1558 | 0.88377 | 0.76571 | 0.68855 | 0.66995 | 0.67307
43602.4374 | 1.0144 | 1.2038 | 1.1546 | 0.88251 | 0.76455 | 0.68799 | 0.66963 | 0.67285
43602.4375 | 1.0111 | 1.2032 | 1.1552 | 0.88281 | 0.76467 | 0.68803 | 0.66858 | 0.6727
43602.4375 | 1.0137 | 1.2048 | 1.1546 | 0.88387 | 0.76447 | 0.6877 | 0.66874 | 0.67279
43602.4375 | 1.0122 | 1.2032 | 1.1543 | 0.88216 | 0.76502 | 0.68809 | 0.66902 | 0.67324
43602.4375 | 1.0115 | 1.2021 | 1.1533 | 0.88136 | 0.76343 | 0.68726 | 0.66852 | 0.67249
43602.4375 | 1.0101 | 1.2034 | 1.1543 | 0.88218 | 0.76425 | 0.68758 | 0.66858 | 0.67292
43602.4375 | 1.0092 | 1.2032 | 1.1546 | 0.88277 | 0.76451 | 0.68756 | 0.6741 | 0.67256
43602.4375 | 1.0134 | 1.2051 | 1.1545 | 0.88235 | 0.76429 | 0.68745 | 0.66955 | 0.67257
43602.4375 | 1.0149 | 1.2043 | 1.1544 | 0.88263 | 0.76452 | 0.68803 | 0.66892 | 0.67272
43602.4375 | 1.014 | 1.204 | 1.1552 | 0.88198 | 0.76449 | 0.68778 | 0.6695 | 0.67252
43602.4376 | 1.0191 | 1.2089 | 1.1574 | 0.88541 | 0.76519 | 0.68826 | 0.66841 | 0.67293
43602.4376 | 1.0156 | 1.2076 | 1.1568 | 0.88498 | 0.76634 | 0.68872 | 0.67051 | 0.67321
43602.4376 | 1.016 | 1.2064 | 1.1568 | 0.88351 | 0.76627 | 0.68878 | 0.67008 | 0.67327
43602.4376 | 1.0126 | 1.205 | 1.1563 | 0.88289 | 0.76504 | 0.68854 | 0.66931 | 0.67305
43602.4376 | 1.0081 | 1.2076 | 1.1577 | 0.88499 | 0.76572 | 0.68891 | 0.67048 | 0.67332
43602.4376 | 1.015 | 1.2082 | 1.1571 | 0.88477 | 0.76636 | 0.68907 | 0.67356 | 0.67348
43602.4376 | 1.0159 | 1.2068 | 1.157 | 0.88397 | 0.76618 | 0.68902 | 0.67086 | 0.67337
43602.4376 | 1.0162 | 1.209 | 1.1579 | 0.8858 | 0.76646 | 0.68918 | 0.6712 | 0.67317
43602.4376 | 1.0095 | 1.2077 | 1.1587 | 0.88484 | 0.76667 | 0.68958 | 0.67037 | 0.67354
43602.4377 | 1.016 | 1.2088 | 1.1585 | 0.88546 | 0.76617 | 0.68929 | 0.66958 | 0.67346
43602.4377 | 1.0082 | 1.207 | 1.159 | 0.88533 | 0.76699 | 0.69009 | 0.67213 | 0.67369
43602.4377 | 1.017 | 1.2089 | 1.1579 | 0.8852 | 0.7666 | 0.68966 | 0.67024 | 0.67343
43602.4377 | 1.0151 | 1.2075 | 1.158 | 0.88491 | 0.76678 | 0.68966 | 0.67037 | 0.67363
43602.4377 | 1.0064 | 1.2056 | 1.1575 | 0.88392 | 0.7662 | 0.68946 | 0.67278 | 0.67383
43602.4377 | 1.0114 | 1.205 | 1.1559 | 0.88289 | 0.7652 | 0.68882 | 0.67104 | 0.67343
43602.4377 | 1.0047 | 1.2062 | 1.158 | 0.88449 | 0.76583 | 0.68913 | 0.67038 | 0.67364
43602.4377 | 1.0124 | 1.2065 | 1.1566 | 0.88414 | 0.76574 | 0.68931 | 0.67093 | 0.6738
43602.4377 | 1.014 | 1.2056 | 1.1555 | 0.88232 | 0.76531 | 0.68863 | 0.6695 | 0.67342
43602.4378 | 1.0146 | 1.2071 | 1.1569 | 0.88377 | 0.7655 | 0.6885 | 0.66875 | 0.67314
43602.4378 | 1.0175 | 1.2079 | 1.1576 | 0.88475 | 0.76638 | 0.6889 | 0.67445 | 0.67347
43602.4378 | 1.0132 | 1.2063 | 1.1574 | 0.88363 | 0.76611 | 0.6891 | 0.67086 | 0.6736
43602.4378 | 1.0123 | 1.2066 | 1.1584 | 0.88396 | 0.76635 | 0.68942 | 0.67087 | 0.67364
43602.4378 | 1.0205 | 1.2103 | 1.1592 | 0.88636 | 0.76689 | 0.68964 | 0.67044 | 0.67363
43602.4378 | 1.0089 | 1.207 | 1.1591 | 0.88505 | 0.76764 | 0.69034 | 0.67014 | 0.67402
43602.4378 | 1.013 | 1.2085 | 1.1603 | 0.88581 | 0.76703 | 0.69015 | 0.67401 | 0.6739
43602.4378 | 1.016 | 1.2103 | 1.1598 | 0.88673 | 0.7683 | 0.69064 | 0.67158 | 0.67437
43602.4378 | 1.0185 | 1.2087 | 1.1592 | 0.88494 | 0.76805 | 0.69037 | 0.67128 | 0.67422
43602.4379 | 1.0109 | 1.2081 | 1.1603 | 0.88519 | 0.76745 | 0.69031 | 0.67126 | 0.67405
43602.4379 | 1.017 | 1.2107 | 1.16 | 0.88602 | 0.76774 | 0.69016 | 0.67123 | 0.67426
43602.4379 | 1.0125 | 1.2083 | 1.1599 | 0.88516 | 0.76845 | 0.69083 | 0.67178 | 0.67409
43602.4379 | 1.0194 | 1.2108 | 1.1604 | 0.88678 | 0.76785 | 0.6903 | 0.67604 | 0.67393
43602.4379 | 1.0094 | 1.2112 | 1.1621 | 0.88751 | 0.76898 | 0.69127 | 0.67324 | 0.67465
43602.4379 | 1.0205 | 1.2145 | 1.1647 | 0.88828 | 0.76983 | 0.69227 | 0.67325 | 0.67482
43602.4379 | 1.0245 | 1.2172 | 1.1664 | 0.89045 | 0.77081 | 0.69258 | 0.6734 | 0.67488
43602.4379 | 1.0266 | 1.2199 | 1.1685 | 0.89215 | 0.77234 | 0.69362 | 0.67488 | 0.67546
43602.4379 | 1.0283 | 1.2222 | 1.17 | 0.89292 | 0.77349 | 0.69437 | 0.67413 | 0.67564
43602.438 | 1.0295 | 1.2238 | 1.172 | 0.89446 | 0.77491 | 0.69556 | 0.67511 | 0.67605
43602.438 | 1.03 | 1.2238 | 1.1733 | 0.89463 | 0.77545 | 0.69619 | 0.6769 | 0.67648
43602.438 | 1.0333 | 1.2269 | 1.1747 | 0.89526 | 0.77583 | 0.69661 | 0.68086 | 0.67637
43602.438 | 1.0358 | 1.2295 | 1.177 | 0.89687 | 0.77714 | 0.69768 | 0.67869 | 0.67673
43602.438 | 1.0336 | 1.2314 | 1.1798 | 0.89856 | 0.77831 | 0.69879 | 0.67931 | 0.67769
43602.438 | 1.0401 | 1.2354 | 1.1819 | 0.90145 | 0.78001 | 0.70024 | 0.67951 | 0.67789
43602.438 | 1.0378 | 1.236 | 1.1834 | 0.90175 | 0.78138 | 0.70072 | 0.67946 | 0.67772
43602.438 | 1.0399 | 1.2388 | 1.1857 | 0.90342 | 0.78258 | 0.70201 | 0.6808 | 0.67848
43602.4381 | 1.0429 | 1.2425 | 1.1878 | 0.90561 | 0.78385 | 0.70298 | 0.68215 | 0.67876
43602.4381 | 1.0454 | 1.2417 | 1.188 | 0.90493 | 0.7848 | 0.704 | 0.68573 | 0.67913
43602.4381 | 1.0488 | 1.2441 | 1.1893 | 0.90675 | 0.78545 | 0.70425 | 0.68338 | 0.67942
43602.4381 | 1.0474 | 1.2447 | 1.1898 | 0.90627 | 0.78602 | 0.70483 | 0.68309 | 0.67959
43602.4381 | 1.0436 | 1.2422 | 1.1896 | 0.90479 | 0.78538 | 0.70426 | 0.68412 | 0.67951
43602.4381 | 1.0464 | 1.2412 | 1.189 | 0.90366 | 0.7846 | 0.70413 | 0.68267 | 0.67934
43602.4381 | 1.0437 | 1.2408 | 1.1888 | 0.90377 | 0.78503 | 0.70404 | 0.68335 | 0.67952
43602.4381 | 1.0412 | 1.241 | 1.1898 | 0.90457 | 0.78492 | 0.70437 | 0.68366 | 0.67981
43602.4381 | 1.0461 | 1.2421 | 1.1891 | 0.90485 | 0.7847 | 0.70417 | 0.68382 | 0.6797
43602.4382 | 1.0414 | 1.2391 | 1.1884 | 0.90281 | 0.78414 | 0.70379 | 0.68264 | 0.67976
43602.4382 | 1.0402 | 1.2395 | 1.1889 | 0.90301 | 0.78355 | 0.70374 | 0.68654 | 0.67978
43602.4382 | 1.0409 | 1.2412 | 1.1893 | 0.90422 | 0.78453 | 0.70395 | 0.68692 | 0.68013
43602.4382 | 1.0417 | 1.2399 | 1.1895 | 0.90368 | 0.78459 | 0.70422 | 0.68405 | 0.68028
43602.4382 | 1.0356 | 1.2372 | 1.1887 | 0.90177 | 0.78373 | 0.7039 | 0.68351 | 0.68022
43602.4382 | 1.036 | 1.2382 | 1.1892 | 0.90262 | 0.78313 | 0.70377 | 0.68312 | 0.68016
43602.4382 | 1.0375 | 1.2393 | 1.1903 | 0.9038 | 0.78386 | 0.70418 | 0.6828 | 0.68031
43602.4382 | 1.0395 | 1.2422 | 1.1924 | 0.90501 | 0.785 | 0.70476 | 0.68393 | 0.68038
43602.4382 | 1.046 | 1.2454 | 1.195 | 0.90675 | 0.78624 | 0.70588 | 0.68395 | 0.68118
43602.4383 | 1.0451 | 1.2476 | 1.1964 | 0.90773 | 0.78767 | 0.70738 | 0.68902 | 0.68178
43602.4383 | 1.045 | 1.2492 | 1.1984 | 0.90914 | 0.78821 | 0.70745 | 0.68697 | 0.68182
43602.4383 | 1.0463 | 1.2495 | 1.1997 | 0.90965 | 0.78944 | 0.70867 | 0.68756 | 0.68221
43602.4383 | 1.0463 | 1.2513 | 1.2015 | 0.91019 | 0.78981 | 0.70905 | 0.68772 | 0.68238
43602.4383 | 1.0559 | 1.2571 | 1.2044 | 0.91281 | 0.79134 | 0.7098 | 0.68768 | 0.68253
43602.4383 | 1.0558 | 1.2589 | 1.2072 | 0.91451 | 0.79369 | 0.71206 | 0.69326 | 0.68355
43602.4383 | 1.0582 | 1.2619 | 1.2101 | 0.91643 | 0.79516 | 0.71288 | 0.69242 | 0.68376
43602.4383 | 1.0564 | 1.2626 | 1.2108 | 0.9165 | 0.79575 | 0.7136 | 0.69156 | 0.68409
43602.4383 | 1.0585 | 1.2654 | 1.2138 | 0.91814 | 0.79659 | 0.71441 | 0.69219 | 0.68439
43602.4384 | 1.062 | 1.2677 | 1.2154 | 0.91949 | 0.79825 | 0.71542 | 0.69282 | 0.68466
43602.4384 | 1.0631 | 1.2704 | 1.2184 | 0.92138 | 0.80048 | 0.71719 | 0.69487 | 0.68557
43602.4384 | 1.0611 | 1.2721 | 1.2207 | 0.9217 | 0.80088 | 0.71763 | 0.69525 | 0.68553
43602.4384 | 1.062 | 1.2758 | 1.2245 | 0.92521 | 0.80287 | 0.71916 | 0.69585 | 0.6863
43602.4384 | 1.0688 | 1.2783 | 1.2257 | 0.92565 | 0.8037 | 0.71988 | 0.69652 | 0.68615
43602.4384 | 1.0661 | 1.2793 | 1.2274 | 0.92607 | 0.80498 | 0.72077 | 0.70161 | 0.68701
43602.4384 | 1.0575 | 1.2775 | 1.2289 | 0.92596 | 0.80543 | 0.72174 | 0.70127 | 0.68746
43602.4384 | 1.0744 | 1.284 | 1.2319 | 0.92823 | 0.8063 | 0.72233 | 0.69974 | 0.6872
43602.4384 | 1.0745 | 1.2859 | 1.2339 | 0.92946 | 0.80834 | 0.72351 | 0.7006 | 0.68796
43602.4385 | 1.0684 | 1.285 | 1.2346 | 0.92882 | 0.80858 | 0.72392 | 0.70041 | 0.68838
43602.4385 | 1.075 | 1.2888 | 1.2375 | 0.9305 | 0.80984 | 0.72516 | 0.70093 | 0.68863
43602.4385 | 1.0733 | 1.2884 | 1.2382 | 0.93037 | 0.81096 | 0.72578 | 0.70282 | 0.68891
43602.4385 | 1.0692 | 1.2882 | 1.2388 | 0.93112 | 0.81075 | 0.7259 | 0.7018 | 0.68913
43602.4385 | 1.0731 | 1.2902 | 1.2404 | 0.93175 | 0.81196 | 0.72664 | 0.70338 | 0.68974
43602.4385 | 1.065 | 1.2878 | 1.2395 | 0.93007 | 0.81152 | 0.72679 | 0.70779 | 0.68971
43602.4385 | 1.0652 | 1.2873 | 1.2398 | 0.9296 | 0.81136 | 0.72668 | 0.7036 | 0.6898
43602.4385 | 1.0673 | 1.2885 | 1.2405 | 0.93046 | 0.81087 | 0.72635 | 0.70311 | 0.68963
43602.4385 | 1.0707 | 1.2883 | 1.2405 | 0.93024 | 0.81196 | 0.72733 | 0.70394 | 0.69046
43602.4386 | 1.0639 | 1.288 | 1.2402 | 0.93036 | 0.81136 | 0.72714 | 0.70305 | 0.69023
43602.4386 | 1.0617 | 1.2871 | 1.2407 | 0.93012 | 0.81152 | 0.72751 | 0.70557 | 0.6906
43602.4386 | 1.0681 | 1.2877 | 1.2405 | 0.93023 | 0.81153 | 0.72716 | 0.70531 | 0.69081
43602.4386 | 1.0567 | 1.2857 | 1.2388 | 0.92852 | 0.81099 | 0.72711 | 0.70354 | 0.69092
43602.4386 | 1.0567 | 1.2823 | 1.2369 | 0.92731 | 0.81034 | 0.72643 | 0.70256 | 0.6907
43602.4386 | 1.0599 | 1.2824 | 1.2373 | 0.9271 | 0.80937 | 0.72596 | 0.70203 | 0.69082
43602.4386 | 1.0513 | 1.2792 | 1.2357 | 0.9261 | 0.80989 | 0.7262 | 0.7028 | 0.69122
43602.4386 | 1.0548 | 1.2781 | 1.2339 | 0.92466 | 0.80835 | 0.72524 | 0.7033 | 0.69042
43602.4386 | 1.055 | 1.2758 | 1.232 | 0.92236 | 0.80754 | 0.72485 | 0.70375 | 0.69135
43602.4387 | 1.0459 | 1.273 | 1.2306 | 0.92148 | 0.8065 | 0.72426 | 0.70156 | 0.69071
43602.4387 | 1.0508 | 1.2721 | 1.2296 | 0.92115 | 0.80594 | 0.72354 | 0.70169 | 0.69077
43602.4387 | 1.0489 | 1.2689 | 1.2257 | 0.91843 | 0.80471 | 0.72292 | 0.70091 | 0.69051
43602.4387 | 1.0359 | 1.2642 | 1.223 | 0.91759 | 0.80286 | 0.7214 | 0.70414 | 0.69001
43602.4387 | 1.0377 | 1.2622 | 1.2217 | 0.91523 | 0.80178 | 0.72085 | 0.7004 | 0.69024
43602.4387 | 1.0386 | 1.2616 | 1.2198 | 0.91429 | 0.80077 | 0.72014 | 0.69863 | 0.68997
43602.4387 | 1.0465 | 1.2609 | 1.219 | 0.91352 | 0.80025 | 0.71952 | 0.69795 | 0.69
43602.4387 | 1.0343 | 1.257 | 1.2166 | 0.91185 | 0.79952 | 0.71909 | 0.69738 | 0.68987
43602.4387 | 1.0306 | 1.2542 | 1.2149 | 0.91073 | 0.79791 | 0.71793 | 0.69582 | 0.68946
43602.4388 | 1.0338 | 1.2532 | 1.2139 | 0.90977 | 0.79709 | 0.71733 | 0.69586 | 0.68911
43602.4388 | 1.0388 | 1.2531 | 1.2146 | 0.90977 | 0.79688 | 0.71709 | 0.69936 | 0.68917
43602.4388 | 1.0339 | 1.252 | 1.2147 | 0.90951 | 0.79715 | 0.71675 | 0.69596 | 0.68889
43602.4388 | 1.0357 | 1.2532 | 1.2146 | 0.91005 | 0.79712 | 0.71705 | 0.69514 | 0.68893
43602.4388 | 1.0326 | 1.2542 | 1.2161 | 0.91115 | 0.79706 | 0.71688 | 0.69538 | 0.68879
43602.4388 | 1.0373 | 1.2576 | 1.2184 | 0.91262 | 0.79843 | 0.71788 | 0.69518 | 0.68922
43602.4388 | 1.035 | 1.2571 | 1.2188 | 0.91201 | 0.79871 | 0.71776 | 0.69542 | 0.6888
43602.4388 | 1.034 | 1.2563 | 1.2186 | 0.91176 | 0.79865 | 0.71817 | 0.69955 | 0.68876
43602.4388 | 1.0399 | 1.2606 | 1.2207 | 0.9132 | 0.79856 | 0.71803 | 0.69658 | 0.68883
43602.4389 | 1.0438 | 1.2636 | 1.2236 | 0.91503 | 0.80026 | 0.71917 | 0.69682 | 0.68923
43602.4389 | 1.0518 | 1.2674 | 1.2268 | 0.91727 | 0.80203 | 0.72043 | 0.6978 | 0.68969
43602.4389 | 1.0496 | 1.2698 | 1.2299 | 0.91844 | 0.80273 | 0.72065 | 0.69819 | 0.68923
43602.4389 | 1.0508 | 1.2738 | 1.2339 | 0.92167 | 0.80512 | 0.72253 | 0.69996 | 0.68977
43602.4389 | 1.0547 | 1.2765 | 1.2362 | 0.9227 | 0.80681 | 0.72393 | 0.70039 | 0.69031
43602.4389 | 1.06 | 1.2799 | 1.2386 | 0.92409 | 0.80786 | 0.72469 | 0.70071 | 0.69037
43602.4389 | 1.0672 | 1.2851 | 1.2433 | 0.92675 | 0.80949 | 0.72563 | 0.70479 | 0.69007
43602.4389 | 1.0674 | 1.2883 | 1.2455 | 0.92791 | 0.81124 | 0.72663 | 0.70522 | 0.69003
43602.4389 | 1.0636 | 1.2914 | 1.251 | 0.93075 | 0.81259 | 0.72759 | 0.70365 | 0.68977
43602.439 | 1.0757 | 1.2991 | 1.2546 | 0.93271 | 0.81536 | 0.72961 | 0.70534 | 0.69051
43602.439 | 1.0793 | 1.3043 | 1.2597 | 0.93566 | 0.81676 | 0.73021 | 0.70536 | 0.68981
43602.439 | 1.0814 | 1.3088 | 1.2642 | 0.93884 | 0.81972 | 0.73233 | 0.70738 | 0.69042
43602.439 | 1.0877 | 1.3148 | 1.2683 | 0.94211 | 0.82249 | 0.73467 | 0.71089 | 0.69171
43602.439 | 1.0912 | 1.319 | 1.2723 | 0.94501 | 0.8253 | 0.73664 | 0.71052 | 0.69185
43602.439 | 1.0937 | 1.3235 | 1.2763 | 0.94668 | 0.82623 | 0.73737 | 0.71141 | 0.69146
43602.439 | 1.1011 | 1.3275 | 1.2797 | 0.94926 | 0.82822 | 0.73867 | 0.71272 | 0.69173
43602.439 | 1.0997 | 1.3321 | 1.2831 | 0.95219 | 0.83031 | 0.74027 | 0.71331 | 0.69191
43602.439 | 1.1113 | 1.3377 | 1.2875 | 0.95479 | 0.83309 | 0.74298 | 0.71589 | 0.69306
43602.4391 | 1.1145 | 1.3409 | 1.2897 | 0.95608 | 0.83461 | 0.7438 | 0.72214 | 0.693
43602.4391 | 1.1198 | 1.3465 | 1.2945 | 0.95939 | 0.83679 | 0.74537 | 0.72009 | 0.69328
43602.4391 | 1.1145 | 1.35 | 1.298 | 0.96169 | 0.83863 | 0.74707 | 0.72 | 0.69398
43602.4391 | 1.13 | 1.3564 | 1.3022 | 0.96566 | 0.84158 | 0.74872 | 0.72187 | 0.69432
43602.4391 | 1.1287 | 1.3591 | 1.3055 | 0.9674 | 0.84359 | 0.75055 | 0.7231 | 0.69461
43602.4391 | 1.1329 | 1.3648 | 1.3093 | 0.971 | 0.84607 | 0.75232 | 0.72436 | 0.69515
43602.4391 | 1.1373 | 1.3698 | 1.3136 | 0.97333 | 0.84961 | 0.75457 | 0.72604 | 0.69589
43602.4391 | 1.1433 | 1.3753 | 1.3179 | 0.97755 | 0.85157 | 0.75647 | 0.72655 | 0.69656
43602.4391 | 1.1431 | 1.3781 | 1.3205 | 0.97968 | 0.85424 | 0.75861 | 0.72921 | 0.69734
43602.4392 | 1.1488 | 1.3832 | 1.3244 | 0.9831 | 0.85618 | 0.75994 | 0.73052 | 0.69757
43602.4392 | 1.1624 | 1.3899 | 1.3276 | 0.98658 | 0.85894 | 0.76192 | 0.73234 | 0.69816
43602.4392 | 1.1599 | 1.3921 | 1.3302 | 0.98872 | 0.86092 | 0.76355 | 0.73495 | 0.69822
43602.4392 | 1.1697 | 1.3957 | 1.3327 | 0.99139 | 0.86301 | 0.76501 | 0.73864 | 0.69904
43602.4392 | 1.1696 | 1.397 | 1.3342 | 0.99263 | 0.86423 | 0.76576 | 0.73685 | 0.69886
43602.4392 | 1.1662 | 1.4008 | 1.3372 | 0.99513 | 0.86706 | 0.76828 | 0.73787 | 0.70024
43602.4392 | 1.1811 | 1.4046 | 1.3395 | 0.99744 | 0.86844 | 0.76932 | 0.73908 | 0.70048
43602.4392 | 1.1821 | 1.4069 | 1.3416 | 1.0007 | 0.87004 | 0.7705 | 0.73979 | 0.70082
43602.4392 | 1.1835 | 1.409 | 1.3434 | 1.0018 | 0.87164 | 0.77207 | 0.74365 | 0.70132
43602.4393 | 1.1903 | 1.4138 | 1.3471 | 1.0051 | 0.87399 | 0.7737 | 0.74387 | 0.70234
43602.4393 | 1.1913 | 1.4172 | 1.3492 | 1.0082 | 0.87612 | 0.77534 | 0.74418 | 0.70302
43602.4393 | 1.1844 | 1.4144 | 1.3487 | 1.007 | 0.87675 | 0.77637 | 0.74511 | 0.7036
43602.4393 | 1.1901 | 1.4171 | 1.3509 | 1.0098 | 0.87789 | 0.77757 | 0.74621 | 0.70445
43602.4393 | 1.1947 | 1.4197 | 1.3525 | 1.0113 | 0.87912 | 0.77821 | 0.74775 | 0.7046
43602.4393 | 1.1987 | 1.4219 | 1.3536 | 1.0128 | 0.88138 | 0.78016 | 0.75139 | 0.70598
43602.4393 | 1.197 | 1.4226 | 1.3547 | 1.0143 | 0.88182 | 0.78027 | 0.74909 | 0.70574
43602.4393 | 1.2044 | 1.4251 | 1.3561 | 1.0159 | 0.88248 | 0.78098 | 0.74904 | 0.70591
43602.4393 | 1.2007 | 1.4264 | 1.3574 | 1.0171 | 0.88499 | 0.7834 | 0.75197 | 0.70774
43602.4394 | 1.2051 | 1.4277 | 1.3575 | 1.0173 | 0.88479 | 0.78283 | 0.7513 | 0.70717
43602.4394 | 1.2066 | 1.4279 | 1.358 | 1.019 | 0.88606 | 0.78387 | 0.75526 | 0.7082
43602.4394 | 1.2012 | 1.4265 | 1.3568 | 1.0181 | 0.88614 | 0.78375 | 0.75286 | 0.70779
43602.4394 | 1.2029 | 1.4245 | 1.3554 | 1.0161 | 0.88502 | 0.78372 | 0.75211 | 0.70854
43602.4394 | 1.2053 | 1.4234 | 1.355 | 1.0167 | 0.88526 | 0.78411 | 0.75256 | 0.70897
43602.4394 | 1.201 | 1.4246 | 1.3553 | 1.0172 | 0.8861 | 0.78415 | 0.75245 | 0.70935
43602.4394 | 1.2017 | 1.4211 | 1.3525 | 1.0157 | 0.88566 | 0.78418 | 0.75298 | 0.70956
43602.4394 | 1.1951 | 1.418 | 1.3494 | 1.0133 | 0.88354 | 0.78296 | 0.7516 | 0.70939
43602.4395 | 1.1929 | 1.4156 | 1.3474 | 1.0117 | 0.88236 | 0.78174 | 0.75567 | 0.70911
43602.4395 | 1.1901 | 1.4122 | 1.3443 | 1.0096 | 0.88071 | 0.78066 | 0.75225 | 0.70899
43602.4395 | 1.1853 | 1.4079 | 1.3415 | 1.0082 | 0.87945 | 0.78061 | 0.75106 | 0.70956
43602.4395 | 1.184 | 1.404 | 1.3376 | 1.0053 | 0.87703 | 0.77833 | 0.74863 | 0.70859
43602.4395 | 1.175 | 1.4004 | 1.3349 | 1.0025 | 0.87499 | 0.77698 | 0.74727 | 0.70842
43602.4395 | 1.1718 | 1.3967 | 1.3311 | 0.9993 | 0.87314 | 0.77539 | 0.74616 | 0.70766
43602.4395 | 1.1689 | 1.3906 | 1.3261 | 0.99702 | 0.87086 | 0.77416 | 0.74459 | 0.70773
43602.4395 | 1.1685 | 1.3859 | 1.3228 | 0.99274 | 0.8681 | 0.77207 | 0.74238 | 0.70738
43602.4395 | 1.1648 | 1.3841 | 1.3203 | 0.99143 | 0.86562 | 0.77005 | 0.74431 | 0.70659
43602.4396 | 1.1607 | 1.3798 | 1.3165 | 0.98897 | 0.86421 | 0.76899 | 0.74229 | 0.7064
43602.4396 | 1.1561 | 1.3744 | 1.3131 | 0.98476 | 0.86198 | 0.76674 | 0.73895 | 0.7052
43602.4396 | 1.1533 | 1.3721 | 1.3101 | 0.98371 | 0.85947 | 0.7653 | 0.73766 | 0.70503
43602.4396 | 1.1432 | 1.3676 | 1.3078 | 0.98133 | 0.8582 | 0.76418 | 0.73601 | 0.70439
43602.4396 | 1.1469 | 1.3663 | 1.3047 | 0.97863 | 0.85598 | 0.76259 | 0.73497 | 0.70432
43602.4396 | 1.149 | 1.3647 | 1.3039 | 0.97841 | 0.85409 | 0.76131 | 0.73334 | 0.70315
43602.4396 | 1.1442 | 1.3621 | 1.3017 | 0.97611 | 0.85428 | 0.76116 | 0.73341 | 0.70381
43602.4396 | 1.1373 | 1.3604 | 1.3 | 0.97527 | 0.85288 | 0.75997 | 0.73638 | 0.70306
43602.4396 | 1.143 | 1.3609 | 1.3004 | 0.97617 | 0.85219 | 0.75932 | 0.73489 | 0.7027
43602.4397 | 1.1406 | 1.3606 | 1.2997 | 0.97531 | 0.85252 | 0.75976 | 0.7332 | 0.70334
43602.4397 | 1.1412 | 1.3587 | 1.2988 | 0.97402 | 0.85126 | 0.75871 | 0.73169 | 0.70255
43602.4397 | 1.1344 | 1.3574 | 1.2985 | 0.97307 | 0.85051 | 0.7581 | 0.73117 | 0.70216
43602.4397 | 1.139 | 1.3586 | 1.2987 | 0.97368 | 0.85068 | 0.75826 | 0.73122 | 0.70236
43602.4397 | 1.1365 | 1.3597 | 1.2997 | 0.97444 | 0.85102 | 0.75813 | 0.73102 | 0.70202
43602.4397 | 1.1377 | 1.3606 | 1.3003 | 0.97447 | 0.85135 | 0.7585 | 0.73028 | 0.7024
43602.4397 | 1.144 | 1.3623 | 1.3002 | 0.97462 | 0.85133 | 0.75817 | 0.73034 | 0.70196
43602.4397 | 1.1417 | 1.3624 | 1.3012 | 0.97512 | 0.85204 | 0.75881 | 0.73601 | 0.70213
43602.4397 | 1.1426 | 1.3631 | 1.3017 | 0.97486 | 0.85152 | 0.75872 | 0.73224 | 0.70163
43602.4398 | 1.1414 | 1.3634 | 1.3014 | 0.97525 | 0.85184 | 0.75899 | 0.7322 | 0.70178
43602.4398 | 1.1475 | 1.3645 | 1.3026 | 0.97572 | 0.8519 | 0.75858 | 0.73207 | 0.70171
43602.4398 | 1.1457 | 1.3645 | 1.3031 | 0.97673 | 0.85182 | 0.75837 | 0.73128 | 0.70127
43602.4398 | 1.1455 | 1.3661 | 1.3039 | 0.97693 | 0.85297 | 0.75922 | 0.73144 | 0.7017
43602.4398 | 1.1461 | 1.3668 | 1.3051 | 0.97756 | 0.85297 | 0.75899 | 0.73012 | 0.70118
43602.4398 | 1.1461 | 1.3667 | 1.3053 | 0.97766 | 0.85402 | 0.76004 | 0.73326 | 0.70193
43602.4398 | 1.15 | 1.3686 | 1.3053 | 0.97774 | 0.85357 | 0.75941 | 0.73218 | 0.70142
43602.4398 | 1.1472 | 1.3687 | 1.3054 | 0.97774 | 0.8538 | 0.75989 | 0.73352 | 0.70155
43602.4398 | 1.1475 | 1.369 | 1.3059 | 0.97841 | 0.8536 | 0.7596 | 0.73267 | 0.70115
43602.4399 | 1.1512 | 1.3688 | 1.306 | 0.97859 | 0.85415 | 0.76011 | 0.73245 | 0.70176
43602.4399 | 1.145 | 1.3683 | 1.3057 | 0.97919 | 0.85379 | 0.75984 | 0.73203 | 0.70114
43602.4399 | 1.1464 | 1.3714 | 1.3078 | 0.98079 | 0.85516 | 0.76083 | 0.73626 | 0.70185
43602.4399 | 1.1544 | 1.372 | 1.3084 | 0.98179 | 0.85552 | 0.76081 | 0.73378 | 0.7012
43602.4399 | 1.1501 | 1.3724 | 1.3086 | 0.98233 | 0.85678 | 0.76191 | 0.73383 | 0.70208
43602.4399 | 1.1588 | 1.3743 | 1.3096 | 0.98371 | 0.85674 | 0.76169 | 0.73313 | 0.7019
43602.4399 | 1.1549 | 1.3747 | 1.309 | 0.98366 | 0.8566 | 0.7616 | 0.73288 | 0.7016
43602.4399 | 1.1498 | 1.3745 | 1.3105 | 0.98388 | 0.85718 | 0.76199 | 0.73372 | 0.70164
43602.4399 | 1.1632 | 1.3778 | 1.3124 | 0.98568 | 0.85861 | 0.76314 | 0.73399 | 0.70178
43602.44 | 1.1598 | 1.3778 | 1.3123 | 0.98598 | 0.85859 | 0.76236 | 0.73408 | 0.70138
43602.44 | 1.1591 | 1.3803 | 1.3138 | 0.98698 | 0.85964 | 0.76368 | 0.73853 | 0.70206
43602.44 | 1.1651 | 1.38 | 1.3136 | 0.98768 | 0.86094 | 0.76483 | 0.73737 | 0.70302
43602.44 | 1.1639 | 1.3818 | 1.3147 | 0.98912 | 0.86055 | 0.76452 | 0.73596 | 0.70257
43602.44 | 1.1678 | 1.382 | 1.3155 | 0.99031 | 0.86252 | 0.76563 | 0.7365 | 0.7031
43602.44 | 1.1675 | 1.3845 | 1.3166 | 0.99122 | 0.86288 | 0.76604 | 0.73692 | 0.70339
43602.44 | 1.1736 | 1.3853 | 1.3173 | 0.9923 | 0.8646 | 0.76715 | 0.73861 | 0.70373
43602.44 | 1.1718 | 1.3852 | 1.3171 | 0.99194 | 0.86325 | 0.76651 | 0.73742 | 0.70329
43602.44 | 1.1755 | 1.3857 | 1.3175 | 0.99284 | 0.86433 | 0.767 | 0.73862 | 0.70345
43602.4401 | 1.1776 | 1.3874 | 1.3191 | 0.9941 | 0.86529 | 0.76745 | 0.73895 | 0.7036
43602.4401 | 1.1798 | 1.3902 | 1.3202 | 0.99637 | 0.8663 | 0.76829 | 0.74199 | 0.70385
43602.4401 | 1.1737 | 1.3875 | 1.3195 | 0.99435 | 0.86677 | 0.76877 | 0.74265 | 0.70386
43602.4401 | 1.1798 | 1.3885 | 1.3198 | 0.99589 | 0.86672 | 0.7687 | 0.73998 | 0.70381
43602.4401 | 1.1796 | 1.3889 | 1.3192 | 0.99654 | 0.86678 | 0.76873 | 0.73989 | 0.704
43602.4401 | 1.1796 | 1.3895 | 1.3198 | 0.99602 | 0.86702 | 0.76892 | 0.74043 | 0.70398
43602.4401 | 1.1806 | 1.3895 | 1.3194 | 0.99661 | 0.86724 | 0.76928 | 0.74026 | 0.70409
43602.4401 | 1.1783 | 1.3882 | 1.3189 | 0.99552 | 0.86634 | 0.76864 | 0.73964 | 0.70381
43602.4401 | 1.1791 | 1.3885 | 1.3194 | 0.99626 | 0.8681 | 0.76981 | 0.73972 | 0.70442
43602.4402 | 1.181 | 1.3898 | 1.3201 | 0.9969 | 0.86759 | 0.76965 | 0.74209 | 0.70424
43602.4402 | 1.1807 | 1.3897 | 1.3189 | 0.99633 | 0.86706 | 0.76946 | 0.74253 | 0.70395
43602.4402 | 1.1799 | 1.3902 | 1.3201 | 0.99748 | 0.86764 | 0.76988 | 0.73985 | 0.70456
43602.4402 | 1.181 | 1.3895 | 1.3188 | 0.99771 | 0.86777 | 0.76928 | 0.74003 | 0.70405
43602.4402 | 1.1781 | 1.3892 | 1.3188 | 0.99725 | 0.86845 | 0.77065 | 0.74193 | 0.705
43602.4402 | 1.1786 | 1.3878 | 1.3173 | 0.99565 | 0.86658 | 0.76924 | 0.74028 | 0.70418
43602.4402 | 1.1835 | 1.3877 | 1.3181 | 0.99747 | 0.86739 | 0.76949 | 0.73995 | 0.70438
43602.4402 | 1.1805 | 1.3879 | 1.3179 | 0.99691 | 0.86739 | 0.76961 | 0.74008 | 0.70446
43602.4402 | 1.1757 | 1.3884 | 1.3183 | 0.99682 | 0.86741 | 0.76939 | 0.74131 | 0.70414
43602.4403 | 1.1806 | 1.3893 | 1.3181 | 0.99672 | 0.8673 | 0.76958 | 0.74609 | 0.70431
43602.4403 | 1.183 | 1.3885 | 1.3185 | 0.99752 | 0.86746 | 0.76988 | 0.74259 | 0.70454
43602.4403 | 1.1744 | 1.3877 | 1.3176 | 0.99726 | 0.86789 | 0.77023 | 0.7414 | 0.70461
43602.4403 | 1.1803 | 1.3874 | 1.318 | 0.99692 | 0.8675 | 0.76996 | 0.74105 | 0.7047
43602.4403 | 1.1802 | 1.3866 | 1.3167 | 0.99598 | 0.86689 | 0.76937 | 0.74013 | 0.70461
43602.4403 | 1.1773 | 1.385 | 1.3162 | 0.99622 | 0.86673 | 0.76921 | 0.73993 | 0.70444
43602.4403 | 1.176 | 1.3869 | 1.3171 | 0.99654 | 0.86671 | 0.76917 | 0.74004 | 0.70441
43602.4403 | 1.1822 | 1.3879 | 1.3172 | 0.99735 | 0.86745 | 0.7698 | 0.74024 | 0.70497
43602.4403 | 1.1767 | 1.3869 | 1.3168 | 0.99654 | 0.86713 | 0.76977 | 0.73998 | 0.7047
43602.4404 | 1.1747 | 1.3883 | 1.3188 | 0.99757 | 0.86741 | 0.76989 | 0.74498 | 0.70521
43602.4404 | 1.1712 | 1.3867 | 1.3172 | 0.99647 | 0.8679 | 0.7702 | 0.74213 | 0.70508
43602.4404 | 1.1745 | 1.3859 | 1.3169 | 0.99596 | 0.86628 | 0.76968 | 0.74066 | 0.70515
43602.4404 | 1.1705 | 1.3878 | 1.3181 | 0.9968 | 0.86711 | 0.77043 | 0.74138 | 0.70538
43602.4404 | 1.1815 | 1.3872 | 1.3173 | 0.99751 | 0.86679 | 0.76985 | 0.74131 | 0.70539
43602.4404 | 1.171 | 1.3852 | 1.3163 | 0.99545 | 0.86819 | 0.7708 | 0.74107 | 0.70551
43602.4404 | 1.1749 | 1.3831 | 1.3149 | 0.99318 | 0.86439 | 0.7684 | 0.74293 | 0.70432
43602.4404 | 1.1754 | 1.3841 | 1.3149 | 0.99469 | 0.86494 | 0.76829 | 0.74108 | 0.70469
43602.4404 | 1.1774 | 1.3832 | 1.3145 | 0.9935 | 0.86453 | 0.76796 | 0.73958 | 0.70468
43602.4405 | 1.1765 | 1.3849 | 1.3152 | 0.99452 | 0.86526 | 0.76887 | 0.74039 | 0.70546
43602.4405 | 1.1755 | 1.3817 | 1.3143 | 0.99306 | 0.86504 | 0.76883 | 0.74035 | 0.70511
43602.4405 | 1.1786 | 1.3823 | 1.3134 | 0.99318 | 0.86367 | 0.76746 | 0.73837 | 0.70474
43602.4405 | 1.1651 | 1.3794 | 1.3121 | 0.99106 | 0.86319 | 0.76694 | 0.73853 | 0.70438
43602.4405 | 1.1704 | 1.38 | 1.3125 | 0.99185 | 0.86315 | 0.76689 | 0.73759 | 0.70431
43602.4405 | 1.1711 | 1.3774 | 1.3107 | 0.99003 | 0.86233 | 0.7665 | 0.73995 | 0.70422
43602.4405 | 1.1692 | 1.3776 | 1.3102 | 0.98991 | 0.86193 | 0.7664 | 0.73784 | 0.70447
43602.4405 | 1.1659 | 1.376 | 1.3097 | 0.98913 | 0.86122 | 0.76601 | 0.73769 | 0.70481
43602.4405 | 1.1672 | 1.3754 | 1.3085 | 0.98841 | 0.86111 | 0.76576 | 0.73612 | 0.70458
43602.4406 | 1.1592 | 1.3737 | 1.3075 | 0.98653 | 0.85945 | 0.76412 | 0.73861 | 0.70356
43602.4406 | 1.1615 | 1.3737 | 1.3073 | 0.9867 | 0.86011 | 0.76504 | 0.73888 | 0.70405
43602.4406 | 1.1616 | 1.3724 | 1.3062 | 0.98565 | 0.8588 | 0.76393 | 0.73701 | 0.70384
43602.4406 | 1.1598 | 1.371 | 1.3054 | 0.9857 | 0.85789 | 0.76316 | 0.7359 | 0.70359
43602.4406 | 1.1553 | 1.3706 | 1.3051 | 0.98502 | 0.8579 | 0.76308 | 0.73644 | 0.70322
43602.4406 | 1.1611 | 1.3707 | 1.3045 | 0.98475 | 0.85747 | 0.76284 | 0.73443 | 0.70348
43602.4406 | 1.1593 | 1.3687 | 1.3024 | 0.98279 | 0.85615 | 0.76192 | 0.73427 | 0.70286
43602.4406 | 1.161 | 1.3687 | 1.3024 | 0.98353 | 0.8564 | 0.76194 | 0.73816 | 0.70298
43602.4406 | 1.1538 | 1.3661 | 1.301 | 0.98164 | 0.85605 | 0.76134 | 0.73602 | 0.70254
43602.4407 | 1.1592 | 1.367 | 1.3009 | 0.98127 | 0.85427 | 0.76019 | 0.73309 | 0.70236
43602.4407 | 1.1555 | 1.3654 | 1.2995 | 0.98023 | 0.8542 | 0.75958 | 0.73224 | 0.70195
43602.4407 | 1.1578 | 1.3659 | 1.2996 | 0.97984 | 0.85287 | 0.75897 | 0.73211 | 0.70165
43602.4407 | 1.1596 | 1.3668 | 1.2994 | 0.98106 | 0.85345 | 0.75909 | 0.73127 | 0.70151
43602.4407 | 1.158 | 1.3655 | 1.2991 | 0.97993 | 0.85403 | 0.75927 | 0.73111 | 0.70179
43602.4407 | 1.1509 | 1.3653 | 1.2989 | 0.97961 | 0.85367 | 0.75933 | 0.73097 | 0.70189
43602.4407 | 1.1574 | 1.3658 | 1.2992 | 0.9808 | 0.85348 | 0.75891 | 0.7315 | 0.70188
43602.4407 | 1.155 | 1.364 | 1.2984 | 0.97989 | 0.85361 | 0.75879 | 0.73658 | 0.70137
43602.4407 | 1.1522 | 1.3643 | 1.298 | 0.97953 | 0.85321 | 0.75878 | 0.73237 | 0.70148
43602.4408 | 1.1533 | 1.3628 | 1.2973 | 0.97849 | 0.85301 | 0.75879 | 0.73113 | 0.70158
43602.4408 | 1.154 | 1.3638 | 1.2974 | 0.9786 | 0.85216 | 0.75828 | 0.73075 | 0.70139
43602.4408 | 1.1566 | 1.365 | 1.2975 | 0.98013 | 0.85309 | 0.75844 | 0.73058 | 0.70122
43602.4408 | 1.151 | 1.3622 | 1.2961 | 0.97846 | 0.85228 | 0.75808 | 0.73069 | 0.70108
43602.4408 | 1.1521 | 1.3629 | 1.297 | 0.97959 | 0.85249 | 0.75793 | 0.73021 | 0.70108
43602.4408 | 1.1581 | 1.3634 | 1.2961 | 0.97891 | 0.85207 | 0.75756 | 0.73009 | 0.70081
43602.4408 | 1.1503 | 1.3621 | 1.2952 | 0.97756 | 0.85191 | 0.75706 | 0.72851 | 0.70039
43602.4408 | 1.1528 | 1.3611 | 1.2939 | 0.97748 | 0.85126 | 0.75686 | 0.73027 | 0.70073
43602.4409 | 1.1563 | 1.3608 | 1.2938 | 0.9773 | 0.85104 | 0.7565 | 0.733 | 0.70071
43602.4409 | 1.1502 | 1.3607 | 1.2938 | 0.97784 | 0.85132 | 0.75709 | 0.73078 | 0.70106
43602.4409 | 1.1546 | 1.3595 | 1.2926 | 0.97576 | 0.84999 | 0.75578 | 0.72965 | 0.69991
43602.4409 | 1.1517 | 1.3585 | 1.2916 | 0.97511 | 0.84954 | 0.75533 | 0.72781 | 0.69977
43602.4409 | 1.1479 | 1.3594 | 1.2919 | 0.97631 | 0.8494 | 0.75537 | 0.72736 | 0.69978
43602.4409 | 1.1545 | 1.3597 | 1.2923 | 0.97678 | 0.84996 | 0.75577 | 0.72772 | 0.70008
43602.4409 | 1.1549 | 1.3608 | 1.2931 | 0.97781 | 0.85077 | 0.75604 | 0.72864 | 0.70051
43602.4409 | 1.1532 | 1.3583 | 1.2915 | 0.97608 | 0.85035 | 0.75607 | 0.72912 | 0.69979
43602.4409 | 1.1524 | 1.3589 | 1.2915 | 0.97658 | 0.84952 | 0.75563 | 0.7276 | 0.69994
43602.441 | 1.1499 | 1.3608 | 1.2932 | 0.97832 | 0.85106 | 0.75617 | 0.72891 | 0.70019
43602.441 | 1.1501 | 1.3588 | 1.2913 | 0.97627 | 0.851 | 0.75624 | 0.73278 | 0.69989
43602.441 | 1.1532 | 1.358 | 1.2915 | 0.97593 | 0.84991 | 0.75553 | 0.72965 | 0.69986
43602.441 | 1.1545 | 1.3598 | 1.2919 | 0.97667 | 0.85029 | 0.75552 | 0.72854 | 0.6998
43602.441 | 1.1558 | 1.3614 | 1.293 | 0.97879 | 0.85061 | 0.75619 | 0.72976 | 0.70023
43602.441 | 1.1593 | 1.3611 | 1.2936 | 0.97817 | 0.85137 | 0.75647 | 0.73216 | 0.70037
43602.441 | 1.1587 | 1.3619 | 1.2937 | 0.97934 | 0.85186 | 0.7569 | 0.72943 | 0.70027
43602.441 | 1.153 | 1.3611 | 1.2932 | 0.97896 | 0.85198 | 0.75694 | 0.72819 | 0.70024
43602.441 | 1.1611 | 1.3658 | 1.2961 | 0.98232 | 0.8524 | 0.75709 | 0.72843 | 0.70023
43602.4411 | 1.1517 | 1.3607 | 1.2936 | 0.97868 | 0.85303 | 0.75745 | 0.72916 | 0.70009
43602.4411 | 1.16 | 1.364 | 1.2952 | 0.98108 | 0.8522 | 0.75707 | 0.72907 | 0.70019
43602.4411 | 1.1618 | 1.3664 | 1.2964 | 0.9823 | 0.85393 | 0.75804 | 0.7311 | 0.70057
43602.4411 | 1.1632 | 1.3669 | 1.2978 | 0.98312 | 0.85441 | 0.75853 | 0.7335 | 0.70057
43602.4411 | 1.1672 | 1.3686 | 1.2992 | 0.98517 | 0.85523 | 0.75901 | 0.73122 | 0.70073
43602.4411 | 1.1627 | 1.368 | 1.2989 | 0.98368 | 0.85617 | 0.75985 | 0.73151 | 0.70131
43602.4411 | 1.1661 | 1.3695 | 1.2999 | 0.98498 | 0.85537 | 0.7592 | 0.73345 | 0.70109
43602.4411 | 1.1695 | 1.3706 | 1.301 | 0.98516 | 0.85729 | 0.76096 | 0.73582 | 0.70138
43602.4411 | 1.1742 | 1.3755 | 1.304 | 0.98895 | 0.85775 | 0.76097 | 0.73324 | 0.70164
43602.4412 | 1.1721 | 1.3739 | 1.3034 | 0.98752 | 0.85861 | 0.76193 | 0.73321 | 0.70193
43602.4412 | 1.1735 | 1.375 | 1.3045 | 0.98871 | 0.85904 | 0.76204 | 0.73298 | 0.70172
43602.4412 | 1.1762 | 1.3752 | 1.3046 | 0.98794 | 0.85889 | 0.76197 | 0.73376 | 0.70156
43602.4412 | 1.1751 | 1.3765 | 1.3048 | 0.98907 | 0.85994 | 0.76288 | 0.73376 | 0.70179
43602.4412 | 1.1731 | 1.3762 | 1.3051 | 0.98886 | 0.85997 | 0.76327 | 0.73453 | 0.70222
43602.4412 | 1.1792 | 1.3759 | 1.3048 | 0.98966 | 0.85973 | 0.76292 | 0.73861 | 0.70165
43602.4412 | 1.1684 | 1.3775 | 1.3061 | 0.99 | 0.86048 | 0.76328 | 0.73666 | 0.70205
43602.4412 | 1.1714 | 1.3749 | 1.3039 | 0.98724 | 0.85984 | 0.76313 | 0.73477 | 0.70189
43602.4412 | 1.1749 | 1.3761 | 1.3047 | 0.98856 | 0.85886 | 0.76207 | 0.73393 | 0.70161
43602.4413 | 1.173 | 1.3764 | 1.305 | 0.98959 | 0.85994 | 0.76284 | 0.73438 | 0.70187
43602.4413 | 1.1708 | 1.3745 | 1.3038 | 0.98795 | 0.86022 | 0.76328 | 0.73545 | 0.70223
43602.4413 | 1.1721 | 1.374 | 1.3034 | 0.9878 | 0.85919 | 0.76234 | 0.73401 | 0.70209
43602.4413 | 1.1655 | 1.3737 | 1.303 | 0.98718 | 0.85909 | 0.76257 | 0.73308 | 0.70219
43602.4413 | 1.1714 | 1.372 | 1.3017 | 0.98595 | 0.85756 | 0.7616 | 0.73301 | 0.70195
43602.4413 | 1.1702 | 1.3736 | 1.3028 | 0.98737 | 0.8577 | 0.76138 | 0.73791 | 0.70174
43602.4413 | 1.1711 | 1.3719 | 1.3022 | 0.98624 | 0.85867 | 0.7621 | 0.73474 | 0.70192
43602.4413 | 1.1683 | 1.3716 | 1.301 | 0.98578 | 0.85754 | 0.76114 | 0.73277 | 0.70146
43602.4413 | 1.1738 | 1.3722 | 1.3016 | 0.98654 | 0.85812 | 0.76141 | 0.73315 | 0.70171
43602.4414 | 1.1706 | 1.3706 | 1.3007 | 0.98476 | 0.85699 | 0.76061 | 0.73221 | 0.70124
43602.4414 | 1.1708 | 1.3725 | 1.3018 | 0.98726 | 0.85799 | 0.76144 | 0.73306 | 0.70156
43602.4414 | 1.1695 | 1.3748 | 1.3029 | 0.98744 | 0.85769 | 0.76114 | 0.73242 | 0.70129
43602.4414 | 1.1667 | 1.375 | 1.3041 | 0.98791 | 0.85874 | 0.76208 | 0.73263 | 0.70156
43602.4414 | 1.167 | 1.3728 | 1.3025 | 0.98702 | 0.85863 | 0.76213 | 0.73449 | 0.7017
43602.4414 | 1.1689 | 1.3754 | 1.3039 | 0.98837 | 0.85784 | 0.76166 | 0.73642 | 0.70168
43602.4414 | 1.1743 | 1.3768 | 1.3053 | 0.98993 | 0.85945 | 0.76238 | 0.73464 | 0.7016
43602.4414 | 1.1754 | 1.3761 | 1.305 | 0.98884 | 0.85996 | 0.76321 | 0.73529 | 0.70209
43602.4414 | 1.1658 | 1.3754 | 1.3042 | 0.9885 | 0.85951 | 0.76297 | 0.73421 | 0.70183
43602.4415 | 1.1726 | 1.3761 | 1.3051 | 0.98929 | 0.85893 | 0.76275 | 0.73397 | 0.70152
43602.4415 | 1.1767 | 1.3774 | 1.3053 | 0.98948 | 0.86003 | 0.76319 | 0.73686 | 0.70195
43602.4415 | 1.1763 | 1.377 | 1.306 | 0.98969 | 0.86011 | 0.76307 | 0.73429 | 0.70161
43602.4415 | 1.1765 | 1.3781 | 1.3056 | 0.98957 | 0.85953 | 0.76275 | 0.73326 | 0.70161
43602.4415 | 1.1792 | 1.3781 | 1.3059 | 0.98972 | 0.85946 | 0.76297 | 0.73411 | 0.70153
43602.4415 | 1.1773 | 1.3793 | 1.307 | 0.99125 | 0.86114 | 0.76353 | 0.73909 | 0.70202
43602.4415 | 1.1676 | 1.3786 | 1.3065 | 0.99017 | 0.86057 | 0.7635 | 0.73595 | 0.70215
43602.4415 | 1.1656 | 1.375 | 1.3047 | 0.98798 | 0.86001 | 0.76379 | 0.73499 | 0.70188
43602.4415 | 1.1733 | 1.3787 | 1.3068 | 0.99124 | 0.8596 | 0.76281 | 0.7339 | 0.70151
43602.4416 | 1.1762 | 1.378 | 1.3062 | 0.99 | 0.86117 | 0.76377 | 0.73525 | 0.70218
43602.4416 | 1.1713 | 1.3813 | 1.3076 | 0.9914 | 0.86107 | 0.76366 | 0.73441 | 0.7023
43602.4416 | 1.1758 | 1.3796 | 1.3073 | 0.99083 | 0.86112 | 0.76404 | 0.73539 | 0.7023
43602.4416 | 1.1755 | 1.3797 | 1.308 | 0.99132 | 0.86131 | 0.76384 | 0.73843 | 0.70181
43602.4416 | 1.1799 | 1.3807 | 1.3091 | 0.99222 | 0.86197 | 0.76443 | 0.73682 | 0.70243
43602.4416 | 1.1806 | 1.3835 | 1.3104 | 0.99409 | 0.86222 | 0.76442 | 0.73637 | 0.70223
43602.4416 | 1.1801 | 1.3839 | 1.3112 | 0.9943 | 0.86376 | 0.76523 | 0.7361 | 0.70244
43602.4416 | 1.1869 | 1.3855 | 1.3115 | 0.9951 | 0.86454 | 0.76615 | 0.73692 | 0.70312
43602.4416 | 1.1851 | 1.3868 | 1.3132 | 0.99617 | 0.86471 | 0.76658 | 0.73952 | 0.70305
43602.4417 | 1.1809 | 1.3854 | 1.3123 | 0.99533 | 0.86529 | 0.76713 | 0.73716 | 0.70363
43602.4417 | 1.1867 | 1.3861 | 1.3136 | 0.99568 | 0.8653 | 0.76699 | 0.73875 | 0.70339
43602.4417 | 1.1821 | 1.3868 | 1.3138 | 0.99642 | 0.86546 | 0.76747 | 0.73977 | 0.70339
43602.4417 | 1.1881 | 1.3885 | 1.3147 | 0.99697 | 0.86597 | 0.76728 | 0.73874 | 0.70335
43602.4417 | 1.1807 | 1.3875 | 1.3146 | 0.99653 | 0.86613 | 0.76765 | 0.73877 | 0.70372
43602.4417 | 1.1894 | 1.3899 | 1.3161 | 0.99821 | 0.86628 | 0.76753 | 0.73923 | 0.70344
43602.4417 | 1.1837 | 1.3885 | 1.315 | 0.99677 | 0.86639 | 0.76758 | 0.7379 | 0.70353
43602.4417 | 1.1855 | 1.3894 | 1.316 | 0.99808 | 0.86725 | 0.76875 | 0.73963 | 0.70404
43602.4417 | 1.1794 | 1.3885 | 1.3155 | 0.99668 | 0.8651 | 0.76749 | 0.73718 | 0.70323
43602.4418 | 1.1874 | 1.3892 | 1.3153 | 0.99709 | 0.86628 | 0.76776 | 0.74064 | 0.70345
43602.4418 | 1.1794 | 1.387 | 1.3136 | 0.9955 | 0.8655 | 0.76726 | 0.74004 | 0.70337
43602.4418 | 1.1814 | 1.3881 | 1.3153 | 0.99693 | 0.86527 | 0.76705 | 0.73809 | 0.70342
43602.4418 | 1.1729 | 1.3871 | 1.314 | 0.99589 | 0.86596 | 0.76788 | 0.73934 | 0.704
43602.4418 | 1.1853 | 1.3887 | 1.315 | 0.99712 | 0.8657 | 0.76778 | 0.73905 | 0.70368
43602.4418 | 1.1779 | 1.3847 | 1.3116 | 0.99399 | 0.86445 | 0.76673 | 0.73973 | 0.70356
43602.4418 | 1.1747 | 1.3844 | 1.3115 | 0.99365 | 0.86355 | 0.76641 | 0.73712 | 0.70327
43602.4418 | 1.1848 | 1.3877 | 1.3147 | 0.99725 | 0.86482 | 0.7671 | 0.73754 | 0.70396
43602.4418 | 1.1833 | 1.3828 | 1.3115 | 0.99372 | 0.86498 | 0.76689 | 0.73847 | 0.70394
43602.4419 | 1.1827 | 1.3834 | 1.3114 | 0.99411 | 0.86321 | 0.76598 | 0.73716 | 0.7036
43602.4419 | 1.1847 | 1.3846 | 1.3123 | 0.99528 | 0.86455 | 0.76641 | 0.73814 | 0.70355
43602.4419 | 1.1769 | 1.3821 | 1.3106 | 0.99278 | 0.86401 | 0.76614 | 0.73694 | 0.70377
43602.4419 | 1.1812 | 1.3846 | 1.3119 | 0.99445 | 0.86372 | 0.76565 | 0.73687 | 0.70318
43602.4419 | 1.1759 | 1.3835 | 1.3114 | 0.99355 | 0.86258 | 0.76542 | 0.74085 | 0.70282
43602.4419 | 1.1776 | 1.3818 | 1.31 | 0.9928 | 0.86276 | 0.7652 | 0.73798 | 0.70324
43602.4419 | 1.1674 | 1.3809 | 1.3096 | 0.99085 | 0.86153 | 0.76419 | 0.73655 | 0.7028
43602.4419 | 1.1704 | 1.3814 | 1.3094 | 0.99138 | 0.86144 | 0.76494 | 0.73887 | 0.70279
43602.4419 | 1.1727 | 1.3801 | 1.308 | 0.99087 | 0.86082 | 0.76379 | 0.73675 | 0.70256
43602.442 | 1.1737 | 1.3797 | 1.3081 | 0.99016 | 0.86132 | 0.76348 | 0.73496 | 0.70267
43602.442 | 1.1602 | 1.3771 | 1.3065 | 0.98847 | 0.85949 | 0.76306 | 0.73372 | 0.70254
43602.442 | 1.165 | 1.3773 | 1.3062 | 0.98827 | 0.85924 | 0.76289 | 0.73464 | 0.70244
43602.442 | 1.1728 | 1.379 | 1.3066 | 0.98931 | 0.86011 | 0.76318 | 0.73613 | 0.70264
43602.442 | 1.1627 | 1.3758 | 1.3041 | 0.98703 | 0.85826 | 0.76196 | 0.73311 | 0.70179
43602.442 | 1.1738 | 1.3781 | 1.3063 | 0.98906 | 0.85914 | 0.76236 | 0.73383 | 0.70228
43602.442 | 1.1639 | 1.3763 | 1.305 | 0.98818 | 0.85979 | 0.76311 | 0.73545 | 0.70242
43602.442 | 1.1659 | 1.3759 | 1.304 | 0.98746 | 0.85741 | 0.76165 | 0.73557 | 0.70217
43602.442 | 1.162 | 1.3749 | 1.3036 | 0.98632 | 0.85811 | 0.76225 | 0.73337 | 0.70191
43602.4421 | 1.1607 | 1.3757 | 1.3037 | 0.9856 | 0.85617 | 0.76045 | 0.73191 | 0.701
43602.4421 | 1.1634 | 1.3766 | 1.3056 | 0.98784 | 0.85844 | 0.76212 | 0.73362 | 0.70203
43602.4421 | 1.1708 | 1.3753 | 1.3041 | 0.98647 | 0.85714 | 0.76154 | 0.73339 | 0.70178
43602.4421 | 1.1642 | 1.3746 | 1.3043 | 0.98644 | 0.85819 | 0.76187 | 0.73335 | 0.70226
43602.4421 | 1.1683 | 1.3752 | 1.305 | 0.98723 | 0.85832 | 0.76193 | 0.73471 | 0.70196
43602.4421 | 1.1694 | 1.376 | 1.3051 | 0.98775 | 0.85877 | 0.76199 | 0.73618 | 0.70192
43602.4421 | 1.1611 | 1.3757 | 1.3058 | 0.98707 | 0.85806 | 0.76188 | 0.73309 | 0.70184
43602.4421 | 1.1733 | 1.3776 | 1.3072 | 0.98897 | 0.85873 | 0.76204 | 0.73385 | 0.70194
43602.4421 | 1.1661 | 1.3759 | 1.306 | 0.98718 | 0.85914 | 0.76235 | 0.73412 | 0.70185
43602.4422 | 1.1597 | 1.3769 | 1.307 | 0.98707 | 0.85737 | 0.76174 | 0.73481 | 0.70173
43602.4422 | 1.1735 | 1.3789 | 1.3085 | 0.98994 | 0.85963 | 0.76293 | 0.73829 | 0.70217
43602.4422 | 1.1656 | 1.3774 | 1.3077 | 0.98778 | 0.85951 | 0.76301 | 0.73485 | 0.70235
43602.4422 | 1.172 | 1.3796 | 1.3085 | 0.98947 | 0.85828 | 0.76217 | 0.73381 | 0.70199
43602.4422 | 1.1708 | 1.3785 | 1.3082 | 0.98858 | 0.86003 | 0.76339 | 0.73479 | 0.70239
43602.4422 | 1.1735 | 1.3805 | 1.3096 | 0.99006 | 0.85983 | 0.76321 | 0.7341 | 0.70227
43602.4422 | 1.178 | 1.3829 | 1.3114 | 0.99178 | 0.8608 | 0.76387 | 0.73563 | 0.70274
43602.4422 | 1.1734 | 1.3817 | 1.3108 | 0.99084 | 0.86172 | 0.76469 | 0.73499 | 0.70303
43602.4423 | 1.1756 | 1.3818 | 1.3105 | 0.99045 | 0.86203 | 0.76485 | 0.73547 | 0.7028
43602.4423 | 1.1625 | 1.3801 | 1.3099 | 0.98908 | 0.85928 | 0.76324 | 0.73825 | 0.70239
43602.4423 | 1.1718 | 1.3831 | 1.3116 | 0.99165 | 0.86195 | 0.76497 | 0.73593 | 0.7028
43602.4423 | 1.1759 | 1.3814 | 1.3107 | 0.99063 | 0.86069 | 0.76389 | 0.735 | 0.70295
43602.4423 | 1.1689 | 1.3808 | 1.3109 | 0.99059 | 0.86134 | 0.76447 | 0.73643 | 0.70274
43602.4423 | 1.1677 | 1.3822 | 1.3117 | 0.99059 | 0.86049 | 0.76418 | 0.73545 | 0.70276
43602.4423 | 1.1736 | 1.3823 | 1.3118 | 0.99063 | 0.86024 | 0.76427 | 0.73508 | 0.70252
43602.4423 | 1.1759 | 1.3827 | 1.3127 | 0.99149 | 0.86178 | 0.76505 | 0.73956 | 0.70344
43602.4423 | 1.1756 | 1.3815 | 1.3116 | 0.99026 | 0.86089 | 0.76443 | 0.73664 | 0.703
43602.4424 | 1.175 | 1.3826 | 1.3124 | 0.99094 | 0.86138 | 0.76498 | 0.73639 | 0.70347
43602.4424 | 1.1734 | 1.3827 | 1.3121 | 0.99023 | 0.86097 | 0.76429 | 0.73618 | 0.70253
43602.4424 | 1.1672 | 1.3797 | 1.3106 | 0.98805 | 0.8602 | 0.7642 | 0.73574 | 0.70283
43602.4424 | 1.1703 | 1.3827 | 1.3121 | 0.98949 | 0.85922 | 0.76335 | 0.73552 | 0.70255
43602.4424 | 1.1734 | 1.3823 | 1.3123 | 0.98993 | 0.86101 | 0.76443 | 0.73868 | 0.7032
43602.4424 | 1.1679 | 1.382 | 1.3116 | 0.98952 | 0.86032 | 0.76408 | 0.73592 | 0.70313
43602.4424 | 1.1697 | 1.3817 | 1.3123 | 0.98897 | 0.86002 | 0.7636 | 0.73505 | 0.7031
43602.4424 | 1.1735 | 1.3813 | 1.3114 | 0.9889 | 0.86018 | 0.76386 | 0.73554 | 0.70319
43602.4424 | 1.161 | 1.3799 | 1.3115 | 0.98763 | 0.85914 | 0.76316 | 0.73469 | 0.70232
43602.4425 | 1.1589 | 1.3809 | 1.3124 | 0.98857 | 0.85981 | 0.76372 | 0.73579 | 0.70265
43602.4425 | 1.1683 | 1.3809 | 1.3109 | 0.9883 | 0.85934 | 0.76312 | 0.73345 | 0.70232
43602.4425 | 1.1612 | 1.3776 | 1.3102 | 0.9863 | 0.85863 | 0.76248 | 0.73331 | 0.70223
43602.4425 | 1.1612 | 1.379 | 1.3102 | 0.98715 | 0.85864 | 0.76279 | 0.73409 | 0.70258
43602.4425 | 1.1672 | 1.3794 | 1.3108 | 0.98711 | 0.85864 | 0.76276 | 0.73627 | 0.70289
43602.4425 | 1.1645 | 1.3799 | 1.3112 | 0.98633 | 0.8579 | 0.76217 | 0.73826 | 0.70208
43602.4425 | 1.1523 | 1.3763 | 1.3089 | 0.98416 | 0.85749 | 0.76169 | 0.7346 | 0.7019
43602.4425 | 1.1675 | 1.3797 | 1.3098 | 0.98598 | 0.85667 | 0.76124 | 0.73326 | 0.70208
43602.4425 | 1.1626 | 1.3782 | 1.3101 | 0.9854 | 0.85784 | 0.76175 | 0.7331 | 0.70168
43602.4426 | 1.1644 | 1.3797 | 1.3106 | 0.98615 | 0.85692 | 0.76154 | 0.73317 | 0.70161
43602.4426 | 1.1604 | 1.3802 | 1.3112 | 0.98695 | 0.85915 | 0.76264 | 0.73418 | 0.70278
43602.4426 | 1.1597 | 1.3779 | 1.3096 | 0.98467 | 0.85762 | 0.76167 | 0.73376 | 0.70218
43602.4426 | 1.1547 | 1.378 | 1.3095 | 0.98457 | 0.85696 | 0.76118 | 0.73475 | 0.70195
43602.4426 | 1.1551 | 1.3777 | 1.3095 | 0.98409 | 0.85721 | 0.76156 | 0.73364 | 0.70178
43602.4426 | 1.1572 | 1.3762 | 1.3088 | 0.98285 | 0.85614 | 0.76103 | 0.7329 | 0.70158
43602.4426 | 1.1599 | 1.3766 | 1.3085 | 0.98309 | 0.85555 | 0.76036 | 0.73271 | 0.70159
43602.4426 | 1.1532 | 1.3735 | 1.3062 | 0.98109 | 0.85515 | 0.75967 | 0.73113 | 0.70132
43602.4426 | 1.1519 | 1.3717 | 1.3052 | 0.98018 | 0.85346 | 0.7587 | 0.73293 | 0.70088
43602.4427 | 1.1553 | 1.373 | 1.3057 | 0.98063 | 0.85351 | 0.75882 | 0.73059 | 0.70118
43602.4427 | 1.1506 | 1.3727 | 1.305 | 0.97947 | 0.85349 | 0.75816 | 0.73024 | 0.70116
43602.4427 | 1.1505 | 1.3704 | 1.3042 | 0.97872 | 0.85256 | 0.75755 | 0.7296 | 0.70026
43602.4427 | 1.1531 | 1.3708 | 1.304 | 0.97905 | 0.85271 | 0.7579 | 0.73007 | 0.70077
43602.4427 | 1.1408 | 1.3671 | 1.3019 | 0.97693 | 0.85187 | 0.75747 | 0.72947 | 0.70076
43602.4427 | 1.1435 | 1.3671 | 1.3014 | 0.97619 | 0.85125 | 0.7567 | 0.73342 | 0.70028
43602.4427 | 1.1378 | 1.366 | 1.3007 | 0.97545 | 0.85051 | 0.75625 | 0.72998 | 0.69992
43602.4427 | 1.1426 | 1.3659 | 1.3008 | 0.97543 | 0.84997 | 0.75591 | 0.72849 | 0.7001
43602.4427 | 1.1432 | 1.3648 | 1.2985 | 0.97411 | 0.84966 | 0.7557 | 0.72819 | 0.70005
43602.4428 | 1.1432 | 1.3639 | 1.2982 | 0.97343 | 0.84848 | 0.75461 | 0.72749 | 0.69924
43602.4428 | 1.1527 | 1.3669 | 1.3005 | 0.97612 | 0.8491 | 0.75514 | 0.72693 | 0.70003
43602.4428 | 1.1419 | 1.3658 | 1.3004 | 0.97472 | 0.84997 | 0.75568 | 0.72805 | 0.69978
43602.4428 | 1.1482 | 1.3679 | 1.3009 | 0.97549 | 0.84862 | 0.75507 | 0.73111 | 0.69957
43602.4428 | 1.1429 | 1.3673 | 1.3018 | 0.97595 | 0.85041 | 0.75629 | 0.72917 | 0.69993
43602.4428 | 1.1446 | 1.367 | 1.3015 | 0.97507 | 0.84904 | 0.75513 | 0.72701 | 0.6989
43602.4428 | 1.1454 | 1.3692 | 1.3031 | 0.97658 | 0.85047 | 0.75616 | 0.72833 | 0.70007
43602.4428 | 1.1493 | 1.3699 | 1.3027 | 0.97735 | 0.85081 | 0.75624 | 0.72876 | 0.69964
43602.4428 | 1.1522 | 1.3708 | 1.3044 | 0.97813 | 0.85156 | 0.75686 | 0.72854 | 0.70015
43602.4429 | 1.1522 | 1.3733 | 1.3061 | 0.97872 | 0.85204 | 0.75654 | 0.72855 | 0.69924
43602.4429 | 1.1531 | 1.374 | 1.3061 | 0.98023 | 0.85342 | 0.75829 | 0.73292 | 0.70051
43602.4429 | 1.1501 | 1.3755 | 1.3078 | 0.98008 | 0.85292 | 0.75809 | 0.73025 | 0.69985
43602.4429 | 1.1572 | 1.3767 | 1.3088 | 0.98177 | 0.85426 | 0.75896 | 0.73001 | 0.70054
43602.4429 | 1.1527 | 1.3756 | 1.3083 | 0.98045 | 0.85367 | 0.75831 | 0.73001 | 0.69963
43602.4429 | 1.1578 | 1.3788 | 1.3108 | 0.98362 | 0.85472 | 0.75924 | 0.73204 | 0.70033
43602.4429 | 1.16 | 1.3795 | 1.3111 | 0.98327 | 0.85615 | 0.7605 | 0.73379 | 0.70089
43602.4429 | 1.1603 | 1.3809 | 1.3125 | 0.98465 | 0.85739 | 0.761 | 0.73234 | 0.70132
43602.4429 | 1.1622 | 1.3814 | 1.3134 | 0.9845 | 0.85764 | 0.76117 | 0.73196 | 0.70095
43602.443 | 1.1659 | 1.3821 | 1.3141 | 0.98546 | 0.85717 | 0.76089 | 0.73236 | 0.70053
43602.443 | 1.1589 | 1.3806 | 1.3132 | 0.98421 | 0.85721 | 0.76085 | 0.73198 | 0.70051
43602.443 | 1.1632 | 1.3842 | 1.3165 | 0.9869 | 0.85882 | 0.76239 | 0.73498 | 0.7017
43602.443 | 1.1591 | 1.3832 | 1.3156 | 0.98666 | 0.85888 | 0.76234 | 0.73889 | 0.70124
43602.443 | 1.1697 | 1.3875 | 1.3182 | 0.98952 | 0.86022 | 0.76304 | 0.73525 | 0.70188
43602.443 | 1.1669 | 1.3876 | 1.3188 | 0.98966 | 0.86122 | 0.76402 | 0.73552 | 0.70192
43602.443 | 1.1654 | 1.3881 | 1.3196 | 0.98981 | 0.86159 | 0.7647 | 0.73617 | 0.7025
43602.443 | 1.1687 | 1.3891 | 1.3196 | 0.98983 | 0.86103 | 0.76369 | 0.73503 | 0.70136
43602.443 | 1.172 | 1.389 | 1.3201 | 0.99043 | 0.86161 | 0.76481 | 0.73528 | 0.70224
43602.4431 | 1.1674 | 1.3889 | 1.3198 | 0.9895 | 0.86124 | 0.76427 | 0.73516 | 0.70145
43602.4431 | 1.1662 | 1.3902 | 1.3212 | 0.99078 | 0.86182 | 0.76467 | 0.73455 | 0.70223
43602.4431 | 1.174 | 1.3925 | 1.3225 | 0.99236 | 0.86251 | 0.76508 | 0.73473 | 0.70237
43602.4431 | 1.1677 | 1.3917 | 1.3231 | 0.99203 | 0.86409 | 0.76696 | 0.74055 | 0.70371
43602.4431 | 1.1684 | 1.3912 | 1.3224 | 0.99072 | 0.86289 | 0.76548 | 0.73809 | 0.70244
43602.4431 | 1.1672 | 1.3929 | 1.3241 | 0.99243 | 0.8631 | 0.76607 | 0.73749 | 0.70272
43602.4431 | 1.1744 | 1.3932 | 1.3232 | 0.99097 | 0.86281 | 0.76555 | 0.73674 | 0.7022
43602.4431 | 1.1673 | 1.3937 | 1.3235 | 0.99268 | 0.86271 | 0.76552 | 0.7362 | 0.70214
43602.4431 | 1.1653 | 1.3922 | 1.3236 | 0.99076 | 0.86368 | 0.76651 | 0.73777 | 0.70304
43602.4432 | 1.1695 | 1.3937 | 1.3241 | 0.9914 | 0.86338 | 0.76604 | 0.73638 | 0.70294
43602.4432 | 1.1717 | 1.3935 | 1.3246 | 0.99143 | 0.86373 | 0.76625 | 0.73658 | 0.70259
43602.4432 | 1.1662 | 1.3947 | 1.3252 | 0.99162 | 0.86265 | 0.76529 | 0.74016 | 0.70159
43602.4432 | 1.169 | 1.3953 | 1.3257 | 0.99328 | 0.86366 | 0.76642 | 0.7377 | 0.7024
43602.4432 | 1.1706 | 1.3948 | 1.3257 | 0.99188 | 0.86311 | 0.7665 | 0.7368 | 0.70265
43602.4432 | 1.1639 | 1.3961 | 1.3281 | 0.99311 | 0.86478 | 0.76706 | 0.73769 | 0.70283
43602.4432 | 1.1711 | 1.397 | 1.3275 | 0.99474 | 0.86498 | 0.76763 | 0.74192 | 0.70356
43602.4432 | 1.1665 | 1.3955 | 1.3268 | 0.9923 | 0.86464 | 0.76724 | 0.73933 | 0.70337
43602.4432 | 1.1675 | 1.3958 | 1.3266 | 0.9915 | 0.86389 | 0.76671 | 0.73718 | 0.70303
43602.4433 | 1.1693 | 1.3973 | 1.3288 | 0.9935 | 0.8649 | 0.76699 | 0.73723 | 0.70272
43602.4433 | 1.1673 | 1.3962 | 1.3278 | 0.99227 | 0.86469 | 0.76725 | 0.73722 | 0.7032
43602.4433 | 1.1666 | 1.3962 | 1.3277 | 0.99206 | 0.86408 | 0.76663 | 0.73696 | 0.70269
43602.4433 | 1.165 | 1.3969 | 1.3282 | 0.99346 | 0.86426 | 0.76691 | 0.73724 | 0.70309
43602.4433 | 1.1621 | 1.3953 | 1.3281 | 0.99126 | 0.86438 | 0.76743 | 0.73804 | 0.70372
43602.4433 | 1.1687 | 1.3968 | 1.3281 | 0.99269 | 0.86407 | 0.76692 | 0.7376 | 0.70346
43602.4433 | 1.1641 | 1.3955 | 1.328 | 0.99153 | 0.86419 | 0.76708 | 0.73738 | 0.70321
43602.4433 | 1.1664 | 1.3974 | 1.3296 | 0.99267 | 0.8645 | 0.76742 | 0.73938 | 0.7035
43602.4433 | 1.1632 | 1.3964 | 1.3292 | 0.99264 | 0.86492 | 0.76801 | 0.74232 | 0.70387
43602.4434 | 1.1593 | 1.3963 | 1.3294 | 0.99173 | 0.86364 | 0.76705 | 0.73796 | 0.70302
43602.4434 | 1.1684 | 1.3988 | 1.3302 | 0.99282 | 0.86478 | 0.76773 | 0.73827 | 0.70392
43602.4434 | 1.1651 | 1.3996 | 1.3312 | 0.9928 | 0.86526 | 0.76765 | 0.7381 | 0.70343
43602.4434 | 1.1651 | 1.3992 | 1.3311 | 0.99285 | 0.86462 | 0.76743 | 0.73702 | 0.70277
43602.4434 | 1.1627 | 1.3998 | 1.3315 | 0.9928 | 0.86571 | 0.76833 | 0.73911 | 0.704
43602.4434 | 1.1683 | 1.4003 | 1.3322 | 0.99172 | 0.8648 | 0.76736 | 0.73698 | 0.70308
43602.4434 | 1.1667 | 1.4007 | 1.3328 | 0.99315 | 0.8652 | 0.76792 | 0.73929 | 0.70324
43602.4434 | 1.1636 | 1.4011 | 1.3327 | 0.99267 | 0.86567 | 0.76856 | 0.74265 | 0.70349
43602.4434 | 1.1623 | 1.4026 | 1.3345 | 0.99455 | 0.86601 | 0.76864 | 0.73939 | 0.70349
43602.4435 | 1.1699 | 1.4045 | 1.3358 | 0.99582 | 0.86733 | 0.76967 | 0.73945 | 0.70382
43602.4435 | 1.1676 | 1.4049 | 1.3373 | 0.99603 | 0.86838 | 0.77046 | 0.74079 | 0.70444
43602.4435 | 1.168 | 1.4064 | 1.338 | 0.99691 | 0.86807 | 0.77004 | 0.74083 | 0.70375
43602.4435 | 1.1687 | 1.406 | 1.3384 | 0.99533 | 0.86852 | 0.77041 | 0.74052 | 0.70387
43602.4435 | 1.1682 | 1.4088 | 1.3408 | 0.99804 | 0.86891 | 0.77075 | 0.73917 | 0.70388
43602.4435 | 1.1715 | 1.41 | 1.3418 | 0.9988 | 0.87037 | 0.7717 | 0.74062 | 0.70411
43602.4435 | 1.1672 | 1.4097 | 1.3414 | 0.99725 | 0.87062 | 0.77208 | 0.74245 | 0.70459
43602.4435 | 1.1698 | 1.4101 | 1.3423 | 0.99815 | 0.87141 | 0.77311 | 0.74435 | 0.70571
43602.4436 | 1.1689 | 1.4107 | 1.3427 | 0.99727 | 0.87012 | 0.77183 | 0.74202 | 0.70397
43602.4436 | 1.1683 | 1.4134 | 1.3449 | 1.0004 | 0.87165 | 0.77313 | 0.74292 | 0.70482
43602.4436 | 1.1709 | 1.4132 | 1.3454 | 0.99954 | 0.87335 | 0.77436 | 0.74303 | 0.70553
43602.4436 | 1.1704 | 1.4127 | 1.3448 | 0.99906 | 0.87174 | 0.77326 | 0.74566 | 0.70491
43602.4436 | 1.1704 | 1.4127 | 1.3456 | 0.99971 | 0.87297 | 0.77421 | 0.74568 | 0.70569
43602.4436 | 1.1689 | 1.4121 | 1.3448 | 0.99891 | 0.87242 | 0.77364 | 0.74318 | 0.70508
43602.4436 | 1.1727 | 1.4133 | 1.3453 | 0.99938 | 0.87261 | 0.77368 | 0.74307 | 0.70481
43602.4436 | 1.1674 | 1.4118 | 1.3454 | 0.99889 | 0.87139 | 0.77277 | 0.74221 | 0.70451
43602.4436 | 1.1706 | 1.4125 | 1.346 | 0.9995 | 0.87157 | 0.77278 | 0.745 | 0.70464
43602.4437 | 1.1647 | 1.4129 | 1.3464 | 0.99942 | 0.87227 | 0.7733 | 0.74405 | 0.70483
43602.4437 | 1.162 | 1.4127 | 1.3458 | 0.9981 | 0.8719 | 0.77321 | 0.74233 | 0.70468
43602.4437 | 1.1631 | 1.4136 | 1.3476 | 0.9984 | 0.87187 | 0.77359 | 0.74278 | 0.70475
43602.4437 | 1.1759 | 1.4177 | 1.3494 | 1.0007 | 0.87296 | 0.77389 | 0.74257 | 0.70484
43602.4437 | 1.1685 | 1.4177 | 1.3509 | 1.0011 | 0.87404 | 0.77438 | 0.74362 | 0.70471
43602.4437 | 1.1738 | 1.4199 | 1.3519 | 1.0017 | 0.87432 | 0.77502 | 0.74367 | 0.70481
43602.4437 | 1.1721 | 1.4197 | 1.3515 | 1.0013 | 0.87438 | 0.77507 | 0.74281 | 0.7048
43602.4437 | 1.1693 | 1.4209 | 1.354 | 1.0023 | 0.87504 | 0.7752 | 0.74716 | 0.70492
43602.4437 | 1.1733 | 1.4212 | 1.3541 | 1.0028 | 0.87554 | 0.77624 | 0.74663 | 0.70541
43602.4438 | 1.1623 | 1.4213 | 1.3551 | 1.0024 | 0.87542 | 0.77631 | 0.74604 | 0.70512
43602.4438 | 1.1748 | 1.4249 | 1.3567 | 1.0035 | 0.87579 | 0.77649 | 0.74567 | 0.70532
43602.4438 | 1.1803 | 1.4263 | 1.3588 | 1.0058 | 0.87676 | 0.77675 | 0.74552 | 0.70515
43602.4438 | 1.1738 | 1.4262 | 1.3585 | 1.0051 | 0.87806 | 0.77792 | 0.74717 | 0.70555
43602.4438 | 1.1799 | 1.4285 | 1.3597 | 1.0054 | 0.87796 | 0.7779 | 0.7457 | 0.70529
43602.4438 | 1.1751 | 1.4282 | 1.3602 | 1.0049 | 0.87804 | 0.77781 | 0.74786 | 0.70527
43602.4438 | 1.1787 | 1.4295 | 1.3618 | 1.006 | 0.87881 | 0.77834 | 0.75028 | 0.70563
43602.4438 | 1.1739 | 1.4302 | 1.3627 | 1.0074 | 0.87869 | 0.77869 | 0.74787 | 0.70551
43602.4438 | 1.1775 | 1.4322 | 1.3636 | 1.0074 | 0.88028 | 0.77974 | 0.74831 | 0.70602
43602.4439 | 1.1789 | 1.4315 | 1.3626 | 1.0076 | 0.88015 | 0.77923 | 0.74804 | 0.70564
43602.4439 | 1.1713 | 1.4296 | 1.3617 | 1.0056 | 0.8793 | 0.77892 | 0.7474 | 0.70548
43602.4439 | 1.181 | 1.4324 | 1.3643 | 1.0074 | 0.87947 | 0.77928 | 0.7474 | 0.70581
43602.4439 | 1.1782 | 1.4332 | 1.3655 | 1.009 | 0.88015 | 0.77987 | 0.74712 | 0.70581
43602.4439 | 1.1825 | 1.4342 | 1.3663 | 1.0095 | 0.88129 | 0.78044 | 0.74739 | 0.706
43602.4439 | 1.1784 | 1.4339 | 1.3652 | 1.0082 | 0.88078 | 0.77983 | 0.74762 | 0.7054
43602.4439 | 1.1786 | 1.4343 | 1.3664 | 1.0086 | 0.8811 | 0.78035 | 0.74958 | 0.70566
43602.4439 | 1.1853 | 1.4369 | 1.3681 | 1.0101 | 0.88191 | 0.78047 | 0.75309 | 0.7058
43602.4439 | 1.1868 | 1.4382 | 1.3697 | 1.0109 | 0.88296 | 0.7817 | 0.75085 | 0.70627
43602.444 | 1.1798 | 1.4373 | 1.3698 | 1.0113 | 0.88323 | 0.78183 | 0.74996 | 0.70598
43602.444 | 1.1804 | 1.4358 | 1.3696 | 1.0097 | 0.88317 | 0.78216 | 0.74943 | 0.70645
43602.444 | 1.1813 | 1.4374 | 1.3705 | 1.0115 | 0.8828 | 0.78182 | 0.74926 | 0.70607
43602.444 | 1.1798 | 1.4383 | 1.3711 | 1.0118 | 0.88442 | 0.78277 | 0.75053 | 0.70656
43602.444 | 1.1827 | 1.4391 | 1.3712 | 1.0118 | 0.88381 | 0.78279 | 0.7506 | 0.70676
43602.444 | 1.1849 | 1.4378 | 1.3711 | 1.0122 | 0.88392 | 0.78248 | 0.74975 | 0.70638
43602.444 | 1.1782 | 1.4363 | 1.3698 | 1.0102 | 0.88363 | 0.78209 | 0.75182 | 0.70635
43602.444 | 1.183 | 1.4384 | 1.3713 | 1.0114 | 0.88328 | 0.78241 | 0.75411 | 0.70651
43602.444 | 1.1728 | 1.4373 | 1.3719 | 1.0115 | 0.88382 | 0.78293 | 0.75133 | 0.70678
43602.4441 | 1.1834 | 1.4389 | 1.3718 | 1.0116 | 0.88345 | 0.78285 | 0.75074 | 0.70648
43602.4441 | 1.1748 | 1.4379 | 1.3728 | 1.0122 | 0.88449 | 0.78349 | 0.75155 | 0.70666
43602.4441 | 1.1822 | 1.4408 | 1.3734 | 1.0129 | 0.88504 | 0.78372 | 0.75509 | 0.70702
43602.4441 | 1.1844 | 1.4407 | 1.3726 | 1.0123 | 0.88484 | 0.78343 | 0.75147 | 0.70664
43602.4441 | 1.1893 | 1.4411 | 1.3732 | 1.0136 | 0.88529 | 0.78358 | 0.75089 | 0.70653
43602.4441 | 1.1816 | 1.441 | 1.3737 | 1.0133 | 0.88542 | 0.78343 | 0.75023 | 0.70659
43602.4441 | 1.1835 | 1.4416 | 1.3754 | 1.0143 | 0.88551 | 0.78414 | 0.75104 | 0.70663
43602.4441 | 1.1847 | 1.4418 | 1.3749 | 1.0133 | 0.88622 | 0.78415 | 0.75131 | 0.70683
43602.4441 | 1.1868 | 1.4445 | 1.3761 | 1.0136 | 0.88575 | 0.78398 | 0.7518 | 0.70625
43602.4442 | 1.1936 | 1.4471 | 1.3779 | 1.017 | 0.88733 | 0.78528 | 0.75609 | 0.70679
43602.4442 | 1.1909 | 1.4458 | 1.3774 | 1.015 | 0.88759 | 0.78532 | 0.75363 | 0.7066
43602.4442 | 1.195 | 1.4478 | 1.3791 | 1.0169 | 0.88769 | 0.78553 | 0.75251 | 0.70676
43602.4442 | 1.1839 | 1.4465 | 1.3796 | 1.0165 | 0.88844 | 0.78613 | 0.7531 | 0.70673
43602.4442 | 1.1911 | 1.4498 | 1.3818 | 1.0178 | 0.88914 | 0.78649 | 0.75353 | 0.707
43602.4442 | 1.1889 | 1.4505 | 1.3833 | 1.0192 | 0.89048 | 0.78756 | 0.75489 | 0.70725
43602.4442 | 1.1922 | 1.4525 | 1.3843 | 1.0199 | 0.89064 | 0.78753 | 0.7583 | 0.70734
43602.4442 | 1.1966 | 1.4538 | 1.3846 | 1.0199 | 0.89129 | 0.78836 | 0.75675 | 0.70763
43602.4442 | 1.1998 | 1.4569 | 1.3866 | 1.0218 | 0.89241 | 0.78875 | 0.75545 | 0.70766
43602.4443 | 1.1967 | 1.457 | 1.3881 | 1.0226 | 0.89318 | 0.78936 | 0.75604 | 0.70813
43602.4443 | 1.2061 | 1.4604 | 1.3895 | 1.0244 | 0.89425 | 0.79033 | 0.75679 | 0.7081
43602.4443 | 1.2031 | 1.4622 | 1.391 | 1.026 | 0.89531 | 0.7911 | 0.75709 | 0.70816
43602.4443 | 1.206 | 1.4644 | 1.3926 | 1.0273 | 0.89661 | 0.79192 | 0.75758 | 0.70839
43602.4443 | 1.208 | 1.4638 | 1.3926 | 1.0271 | 0.89683 | 0.79261 | 0.75835 | 0.70893
43602.4443 | 1.2101 | 1.4659 | 1.3942 | 1.0281 | 0.89751 | 0.79302 | 0.75762 | 0.70928
43602.4443 | 1.2077 | 1.4675 | 1.3965 | 1.0298 | 0.8986 | 0.79387 | 0.75921 | 0.70963
43602.4443 | 1.2089 | 1.4689 | 1.3974 | 1.0305 | 0.89974 | 0.79466 | 0.76451 | 0.71005
43602.4443 | 1.2152 | 1.4708 | 1.3981 | 1.0307 | 0.90029 | 0.79503 | 0.76193 | 0.70987
43602.4444 | 1.2115 | 1.4705 | 1.3988 | 1.0315 | 0.90102 | 0.79534 | 0.76143 | 0.70978
43602.4444 | 1.2162 | 1.4714 | 1.3984 | 1.0311 | 0.9011 | 0.79562 | 0.76119 | 0.70973
43602.4444 | 1.2121 | 1.4706 | 1.3983 | 1.0312 | 0.90124 | 0.79563 | 0.76107 | 0.71002
43602.4444 | 1.2222 | 1.4726 | 1.3989 | 1.0326 | 0.90165 | 0.7958 | 0.76173 | 0.71011
43602.4444 | 1.2199 | 1.4718 | 1.3987 | 1.032 | 0.90186 | 0.79554 | 0.76075 | 0.70989
43602.4444 | 1.2128 | 1.4726 | 1.3998 | 1.0325 | 0.9025 | 0.79626 | 0.76387 | 0.71008
43602.4444 | 1.219 | 1.4738 | 1.4005 | 1.0339 | 0.90245 | 0.79678 | 0.76441 | 0.71057
43602.4444 | 1.2162 | 1.4742 | 1.4001 | 1.0338 | 0.9034 | 0.79695 | 0.76341 | 0.71066
43602.4444 | 1.2165 | 1.4741 | 1.4007 | 1.0343 | 0.9037 | 0.79771 | 0.7631 | 0.71099
43602.4445 | 1.2258 | 1.4768 | 1.4021 | 1.0367 | 0.90395 | 0.79775 | 0.76318 | 0.71079
43602.4445 | 1.2209 | 1.4766 | 1.4019 | 1.0358 | 0.90475 | 0.79805 | 0.76384 | 0.71095
43602.4445 | 1.2273 | 1.4762 | 1.4014 | 1.0357 | 0.90448 | 0.79802 | 0.76315 | 0.71068
43602.4445 | 1.2183 | 1.476 | 1.4008 | 1.035 | 0.90403 | 0.79799 | 0.76389 | 0.71088
43602.4445 | 1.2265 | 1.4785 | 1.4024 | 1.0369 | 0.90463 | 0.79817 | 0.76672 | 0.71125
43602.4445 | 1.2229 | 1.4774 | 1.4018 | 1.037 | 0.90553 | 0.79877 | 0.76499 | 0.71158
43602.4445 | 1.2253 | 1.4788 | 1.4016 | 1.0361 | 0.90461 | 0.79849 | 0.76377 | 0.71159
43602.4445 | 1.2231 | 1.4794 | 1.4037 | 1.0371 | 0.90545 | 0.79864 | 0.76384 | 0.71157
43602.4445 | 1.233 | 1.4809 | 1.4034 | 1.0382 | 0.9062 | 0.79972 | 0.76495 | 0.71181
43602.4446 | 1.2243 | 1.4796 | 1.4034 | 1.0378 | 0.9066 | 0.79982 | 0.76612 | 0.71212
43602.4446 | 1.229 | 1.4802 | 1.4042 | 1.0394 | 0.90684 | 0.80045 | 0.76996 | 0.71221
43602.4446 | 1.2263 | 1.479 | 1.4034 | 1.0381 | 0.90683 | 0.80023 | 0.7662 | 0.71242
43602.4446 | 1.2235 | 1.4769 | 1.4015 | 1.0369 | 0.90592 | 0.7994 | 0.76472 | 0.7119
43602.4446 | 1.2306 | 1.4789 | 1.4028 | 1.0387 | 0.90605 | 0.79979 | 0.76502 | 0.71239
43602.4446 | 1.2326 | 1.4803 | 1.4034 | 1.0399 | 0.90719 | 0.80055 | 0.76546 | 0.7125
43602.4446 | 1.2278 | 1.4796 | 1.4036 | 1.0391 | 0.907 | 0.80044 | 0.76579 | 0.71273
43602.4446 | 1.2293 | 1.4806 | 1.4043 | 1.0402 | 0.90761 | 0.80109 | 0.76585 | 0.71293
43602.4446 | 1.2292 | 1.4809 | 1.4048 | 1.0414 | 0.90819 | 0.80142 | 0.76603 | 0.71326
43602.4447 | 1.2355 | 1.4812 | 1.4035 | 1.0403 | 0.9083 | 0.80141 | 0.76621 | 0.71296
43602.4447 | 1.2335 | 1.4816 | 1.4038 | 1.0407 | 0.90831 | 0.80152 | 0.76643 | 0.71327
43602.4447 | 1.2406 | 1.4832 | 1.4044 | 1.0409 | 0.90817 | 0.8019 | 0.76621 | 0.71345
43602.4447 | 1.2365 | 1.4815 | 1.404 | 1.041 | 0.90817 | 0.80211 | 0.76783 | 0.71386
43602.4447 | 1.2356 | 1.4811 | 1.4039 | 1.0415 | 0.90947 | 0.80273 | 0.77241 | 0.71419
43602.4447 | 1.2367 | 1.482 | 1.4046 | 1.0419 | 0.90935 | 0.80262 | 0.76875 | 0.71447
43602.4447 | 1.233 | 1.4819 | 1.4047 | 1.0419 | 0.90931 | 0.80278 | 0.76797 | 0.71439
43602.4447 | 1.2401 | 1.4814 | 1.4043 | 1.0428 | 0.90995 | 0.80277 | 0.76805 | 0.71435
43602.4447 | 1.2359 | 1.4797 | 1.4029 | 1.0413 | 0.90864 | 0.80209 | 0.76807 | 0.71402
43602.4448 | 1.2365 | 1.4796 | 1.4028 | 1.0403 | 0.90889 | 0.80217 | 0.76839 | 0.71401
43602.4448 | 1.2375 | 1.4817 | 1.403 | 1.0412 | 0.90848 | 0.80191 | 0.76712 | 0.71402
43602.4448 | 1.2381 | 1.4815 | 1.4039 | 1.0419 | 0.90925 | 0.80243 | 0.76849 | 0.71433
43602.4448 | 1.241 | 1.4792 | 1.4019 | 1.0406 | 0.90782 | 0.80169 | 0.76855 | 0.71399
43602.4448 | 1.2348 | 1.4798 | 1.4028 | 1.0407 | 0.90797 | 0.80157 | 0.76697 | 0.71372
43602.4448 | 1.2386 | 1.4811 | 1.4027 | 1.0413 | 0.90765 | 0.80124 | 0.76636 | 0.71357
43602.4448 | 1.2354 | 1.4791 | 1.4014 | 1.0404 | 0.90783 | 0.80124 | 0.76681 | 0.71346
43602.4448 | 1.2356 | 1.4781 | 1.4015 | 1.0403 | 0.90753 | 0.80085 | 0.76688 | 0.71341
43602.4448 | 1.2377 | 1.479 | 1.4017 | 1.0406 | 0.90751 | 0.80079 | 0.76616 | 0.71333
43602.4449 | 1.2365 | 1.4788 | 1.4013 | 1.04 | 0.90728 | 0.80075 | 0.7665 | 0.71299
43602.4449 | 1.2366 | 1.4798 | 1.4022 | 1.04 | 0.90744 | 0.80085 | 0.77088 | 0.71329
43602.4449 | 1.2384 | 1.4806 | 1.4028 | 1.041 | 0.90754 | 0.80104 | 0.76753 | 0.71321
43602.4449 | 1.2343 | 1.4792 | 1.4015 | 1.0393 | 0.90703 | 0.80094 | 0.76654 | 0.71322
43602.4449 | 1.2386 | 1.4796 | 1.4019 | 1.0398 | 0.90683 | 0.80063 | 0.76606 | 0.71312
43602.4449 | 1.2395 | 1.4796 | 1.402 | 1.0406 | 0.9082 | 0.80125 | 0.76658 | 0.71345
43602.4449 | 1.2335 | 1.4791 | 1.4023 | 1.0403 | 0.90726 | 0.80083 | 0.76601 | 0.71314
43602.4449 | 1.234 | 1.4798 | 1.4024 | 1.041 | 0.90786 | 0.80151 | 0.76696 | 0.71383
43602.445 | 1.2387 | 1.4791 | 1.402 | 1.0403 | 0.90763 | 0.80114 | 0.76572 | 0.71351
43602.445 | 1.2383 | 1.4799 | 1.4027 | 1.041 | 0.90783 | 0.80151 | 0.76852 | 0.71378
43602.445 | 1.2398 | 1.4802 | 1.4027 | 1.0413 | 0.90769 | 0.80118 | 0.769 | 0.71326
43602.445 | 1.2356 | 1.4783 | 1.4026 | 1.0413 | 0.90846 | 0.80127 | 0.76719 | 0.71341
43602.445 | 1.2421 | 1.4782 | 1.4007 | 1.0402 | 0.90737 | 0.80092 | 0.76632 | 0.71339
43602.445 | 1.2379 | 1.4777 | 1.4002 | 1.0398 | 0.90681 | 0.80026 | 0.76534 | 0.71326
43602.445 | 1.2412 | 1.4772 | 1.3999 | 1.0395 | 0.9072 | 0.8005 | 0.7664 | 0.71293
43602.445 | 1.2355 | 1.4761 | 1.3989 | 1.0394 | 0.90556 | 0.79954 | 0.76536 | 0.71247
43602.445 | 1.2359 | 1.4744 | 1.3976 | 1.0377 | 0.90596 | 0.79967 | 0.76537 | 0.7126
43602.4451 | 1.2362 | 1.4737 | 1.3973 | 1.038 | 0.90502 | 0.79888 | 0.76703 | 0.71262
43602.4451 | 1.2294 | 1.4722 | 1.396 | 1.036 | 0.90492 | 0.79895 | 0.76477 | 0.71269
43602.4451 | 1.2344 | 1.4738 | 1.3969 | 1.0376 | 0.90435 | 0.79849 | 0.76376 | 0.71249
43602.4451 | 1.2289 | 1.4718 | 1.3952 | 1.0361 | 0.90443 | 0.79889 | 0.76383 | 0.71281
43602.4451 | 1.2305 | 1.4705 | 1.3949 | 1.0352 | 0.90348 | 0.79801 | 0.76426 | 0.71252
43602.4451 | 1.2297 | 1.4706 | 1.3943 | 1.0351 | 0.90307 | 0.79738 | 0.76609 | 0.71203
43602.4451 | 1.2282 | 1.4684 | 1.393 | 1.035 | 0.90253 | 0.79704 | 0.76308 | 0.7118
43602.4451 | 1.2305 | 1.469 | 1.3929 | 1.0341 | 0.90253 | 0.79694 | 0.76206 | 0.71166
43602.4451 | 1.2249 | 1.4688 | 1.3932 | 1.0343 | 0.90151 | 0.79627 | 0.76168 | 0.71168
43602.4452 | 1.2365 | 1.4707 | 1.3941 | 1.0358 | 0.90268 | 0.79713 | 0.76332 | 0.71191
43602.4452 | 1.2238 | 1.4679 | 1.392 | 1.0336 | 0.90319 | 0.79681 | 0.76261 | 0.71155
43602.4452 | 1.2259 | 1.4681 | 1.3919 | 1.0336 | 0.9008 | 0.79591 | 0.7616 | 0.71142
43602.4452 | 1.2239 | 1.4689 | 1.393 | 1.0345 | 0.90206 | 0.7964 | 0.76148 | 0.71154
43602.4452 | 1.2325 | 1.4683 | 1.3922 | 1.034 | 0.90206 | 0.79633 | 0.76233 | 0.71149
43602.4452 | 1.2303 | 1.469 | 1.3927 | 1.0343 | 0.90225 | 0.79651 | 0.76544 | 0.7114
43602.4452 | 1.2275 | 1.4677 | 1.3916 | 1.0336 | 0.90219 | 0.79653 | 0.76466 | 0.71191
43602.4452 | 1.2341 | 1.4683 | 1.3919 | 1.0339 | 0.90117 | 0.79579 | 0.76245 | 0.7116
43602.4452 | 1.2306 | 1.4687 | 1.3922 | 1.0346 | 0.90199 | 0.79624 | 0.76228 | 0.71134
43602.4453 | 1.2278 | 1.469 | 1.3924 | 1.0353 | 0.90134 | 0.79602 | 0.76178 | 0.7115
43602.4453 | 1.2324 | 1.4677 | 1.3915 | 1.0342 | 0.90198 | 0.79635 | 0.76195 | 0.71158
43602.4453 | 1.2354 | 1.4684 | 1.3922 | 1.0346 | 0.90148 | 0.79586 | 0.76317 | 0.71102
43602.4453 | 1.2324 | 1.4693 | 1.3928 | 1.0352 | 0.90224 | 0.79617 | 0.76278 | 0.71158
43602.4453 | 1.2347 | 1.4695 | 1.3924 | 1.0353 | 0.90228 | 0.7967 | 0.76191 | 0.71139
43602.4453 | 1.2322 | 1.4705 | 1.393 | 1.0357 | 0.90209 | 0.79696 | 0.76205 | 0.712
43602.4453 | 1.2265 | 1.4718 | 1.3948 | 1.037 | 0.90419 | 0.79807 | 0.76345 | 0.71249
43602.4453 | 1.2326 | 1.4702 | 1.3934 | 1.0359 | 0.90326 | 0.79805 | 0.76409 | 0.71236
43602.4453 | 1.2364 | 1.4709 | 1.3939 | 1.036 | 0.9027 | 0.79697 | 0.76788 | 0.71161
43602.4454 | 1.2308 | 1.4703 | 1.3932 | 1.0354 | 0.90291 | 0.79703 | 0.76462 | 0.71164
43602.4454 | 1.2394 | 1.4719 | 1.394 | 1.0367 | 0.9031 | 0.7973 | 0.76349 | 0.71203
43602.4454 | 1.2349 | 1.4715 | 1.3936 | 1.0367 | 0.90328 | 0.79719 | 0.76327 | 0.71171
43602.4454 | 1.2385 | 1.4719 | 1.394 | 1.0368 | 0.90377 | 0.79757 | 0.76365 | 0.71233
43602.4454 | 1.2386 | 1.4712 | 1.3927 | 1.0368 | 0.90409 | 0.7976 | 0.76326 | 0.71215
43602.4454 | 1.2293 | 1.4689 | 1.392 | 1.0354 | 0.90291 | 0.797 | 0.76287 | 0.71197
43602.4454 | 1.2325 | 1.4702 | 1.3929 | 1.0366 | 0.9027 | 0.79721 | 0.76273 | 0.71199
43602.4454 | 1.231 | 1.4698 | 1.3931 | 1.0363 | 0.90281 | 0.79722 | 0.76174 | 0.71183
43602.4454 | 1.2336 | 1.4685 | 1.3913 | 1.0349 | 0.90328 | 0.79764 | 0.76474 | 0.7122
43602.4455 | 1.24 | 1.4698 | 1.3919 | 1.0365 | 0.90298 | 0.79682 | 0.76415 | 0.71239
43602.4455 | 1.2277 | 1.4672 | 1.3899 | 1.0347 | 0.90268 | 0.79682 | 0.76176 | 0.7122
43602.4455 | 1.2366 | 1.4679 | 1.3899 | 1.0348 | 0.90173 | 0.7964 | 0.76309 | 0.71227
43602.4455 | 1.2319 | 1.4683 | 1.3905 | 1.0352 | 0.90243 | 0.79671 | 0.76531 | 0.71222
43602.4455 | 1.2344 | 1.4685 | 1.3896 | 1.0343 | 0.9015 | 0.79602 | 0.7625 | 0.71185
43602.4455 | 1.2304 | 1.4673 | 1.3887 | 1.0343 | 0.90197 | 0.79612 | 0.76194 | 0.71208
43602.4455 | 1.2337 | 1.4679 | 1.3895 | 1.0352 | 0.90131 | 0.79581 | 0.76113 | 0.712
43602.4455 | 1.2368 | 1.4682 | 1.3897 | 1.0348 | 0.90184 | 0.79638 | 0.76143 | 0.71203
43602.4455 | 1.2366 | 1.4682 | 1.3895 | 1.0353 | 0.90249 | 0.79624 | 0.76371 | 0.71174
43602.4456 | 1.2268 | 1.4671 | 1.3892 | 1.0345 | 0.90199 | 0.79592 | 0.76159 | 0.71169
43602.4456 | 1.2323 | 1.4695 | 1.391 | 1.036 | 0.90241 | 0.79668 | 0.76155 | 0.7122
43602.4456 | 1.2373 | 1.4688 | 1.3905 | 1.0353 | 0.90256 | 0.79674 | 0.76279 | 0.71218
43602.4456 | 1.2392 | 1.4709 | 1.3918 | 1.0375 | 0.9029 | 0.79644 | 0.76229 | 0.71199
43602.4456 | 1.2419 | 1.4724 | 1.3926 | 1.0373 | 0.90406 | 0.79788 | 0.76335 | 0.71253
43602.4456 | 1.2417 | 1.4722 | 1.3928 | 1.0382 | 0.90423 | 0.79756 | 0.76638 | 0.71268
43602.4456 | 1.2408 | 1.4744 | 1.3941 | 1.0402 | 0.90529 | 0.79828 | 0.76578 | 0.71297
43602.4456 | 1.2397 | 1.4749 | 1.3948 | 1.0395 | 0.90571 | 0.79887 | 0.76471 | 0.71308
43602.4456 | 1.244 | 1.475 | 1.3965 | 1.0411 | 0.90587 | 0.79947 | 0.7647 | 0.71306
43602.4457 | 1.2463 | 1.4755 | 1.3956 | 1.0411 | 0.90627 | 0.79949 | 0.76562 | 0.71337
43602.4457 | 1.2434 | 1.4763 | 1.3964 | 1.0416 | 0.90715 | 0.80025 | 0.76552 | 0.71379
43602.4457 | 1.2405 | 1.4763 | 1.3959 | 1.0407 | 0.90726 | 0.79991 | 0.76558 | 0.71355
43602.4457 | 1.2462 | 1.4762 | 1.3961 | 1.0411 | 0.90683 | 0.79979 | 0.76881 | 0.71352
43602.4457 | 1.2441 | 1.4764 | 1.3967 | 1.0415 | 0.90729 | 0.8001 | 0.7658 | 0.7138
43602.4457 | 1.2399 | 1.4747 | 1.3956 | 1.0401 | 0.90613 | 0.79943 | 0.76462 | 0.71341
43602.4457 | 1.2382 | 1.4756 | 1.3958 | 1.041 | 0.90619 | 0.7993 | 0.76441 | 0.71346
43602.4457 | 1.2381 | 1.4741 | 1.3944 | 1.0398 | 0.90667 | 0.80005 | 0.76661 | 0.71403
43602.4457 | 1.2345 | 1.4732 | 1.3939 | 1.0394 | 0.9053 | 0.79939 | 0.76518 | 0.71369
43602.4458 | 1.2426 | 1.4716 | 1.3927 | 1.0389 | 0.90529 | 0.79844 | 0.76419 | 0.71349
43602.4458 | 1.2336 | 1.4725 | 1.3926 | 1.0393 | 0.90519 | 0.79848 | 0.76345 | 0.71351
43602.4458 | 1.2425 | 1.4699 | 1.3909 | 1.0371 | 0.9046 | 0.79787 | 0.76322 | 0.71337
43602.4458 | 1.2374 | 1.4704 | 1.3911 | 1.0372 | 0.90441 | 0.79798 | 0.7649 | 0.71349
43602.4458 | 1.2374 | 1.4705 | 1.3913 | 1.0375 | 0.90439 | 0.79822 | 0.76686 | 0.71348
43602.4458 | 1.2286 | 1.4687 | 1.3897 | 1.0358 | 0.90409 | 0.79831 | 0.76467 | 0.7138
43602.4458 | 1.2312 | 1.4683 | 1.3893 | 1.0359 | 0.90286 | 0.79717 | 0.76364 | 0.71357
43602.4458 | 1.2294 | 1.4652 | 1.3873 | 1.0342 | 0.90218 | 0.79614 | 0.76235 | 0.71244
43602.4458 | 1.2301 | 1.4644 | 1.3864 | 1.0333 | 0.90033 | 0.7949 | 0.76112 | 0.71241
43602.4459 | 1.2334 | 1.4649 | 1.3861 | 1.0339 | 0.90129 | 0.79585 | 0.76167 | 0.71278
43602.4459 | 1.2273 | 1.463 | 1.3849 | 1.0328 | 0.90089 | 0.7953 | 0.76456 | 0.71273
43602.4459 | 1.2288 | 1.4631 | 1.3847 | 1.0325 | 0.89971 | 0.79464 | 0.76107 | 0.71254
43602.4459 | 1.2266 | 1.4612 | 1.3837 | 1.0312 | 0.89994 | 0.79474 | 0.76077 | 0.71262
43602.4459 | 1.2288 | 1.4621 | 1.3833 | 1.0321 | 0.89927 | 0.79409 | 0.76039 | 0.71214
43602.4459 | 1.2283 | 1.4615 | 1.3833 | 1.0314 | 0.89917 | 0.7937 | 0.75966 | 0.71187
43602.4459 | 1.2258 | 1.4604 | 1.3824 | 1.0309 | 0.89929 | 0.79407 | 0.76089 | 0.71233
43602.4459 | 1.2273 | 1.4586 | 1.3813 | 1.0295 | 0.89872 | 0.79333 | 0.76372 | 0.71233
43602.4459 | 1.2249 | 1.4587 | 1.381 | 1.0302 | 0.89831 | 0.79315 | 0.76042 | 0.71245
43602.446 | 1.2208 | 1.4576 | 1.3801 | 1.0288 | 0.89822 | 0.79343 | 0.76026 | 0.71272
43602.446 | 1.2312 | 1.4587 | 1.3809 | 1.0304 | 0.89802 | 0.79301 | 0.75995 | 0.7126
43602.446 | 1.2242 | 1.458 | 1.3801 | 1.0283 | 0.89741 | 0.79266 | 0.75882 | 0.71169
43602.446 | 1.2228 | 1.4575 | 1.38 | 1.0286 | 0.89733 | 0.79268 | 0.75872 | 0.71204
43602.446 | 1.2303 | 1.4599 | 1.3813 | 1.0308 | 0.89773 | 0.79332 | 0.76118 | 0.71252
43602.446 | 1.2282 | 1.4592 | 1.3808 | 1.0297 | 0.89894 | 0.79371 | 0.75965 | 0.71252
43602.446 | 1.2298 | 1.4593 | 1.3807 | 1.0298 | 0.89768 | 0.79307 | 0.75923 | 0.71196
43602.446 | 1.2259 | 1.459 | 1.3807 | 1.0305 | 0.89838 | 0.79363 | 0.75955 | 0.71211
43602.446 | 1.226 | 1.459 | 1.3809 | 1.0297 | 0.89813 | 0.79348 | 0.76017 | 0.71213
43602.4461 | 1.2273 | 1.4582 | 1.38 | 1.0288 | 0.89677 | 0.79253 | 0.76359 | 0.71183
43602.4461 | 1.2285 | 1.4597 | 1.3815 | 1.0303 | 0.89712 | 0.79257 | 0.75962 | 0.71172
43602.4461 | 1.2313 | 1.4615 | 1.382 | 1.0323 | 0.89855 | 0.79419 | 0.76073 | 0.71268
43602.4461 | 1.2307 | 1.4602 | 1.3813 | 1.0309 | 0.899 | 0.79456 | 0.76135 | 0.71259
43602.4461 | 1.2326 | 1.4616 | 1.382 | 1.0324 | 0.89881 | 0.79443 | 0.76137 | 0.71266
43602.4461 | 1.2354 | 1.4629 | 1.3837 | 1.0333 | 0.89946 | 0.79443 | 0.76097 | 0.71224
43602.4461 | 1.2319 | 1.4639 | 1.3847 | 1.0333 | 0.90014 | 0.79552 | 0.76116 | 0.71298
43602.4461 | 1.2367 | 1.4646 | 1.3846 | 1.034 | 0.9006 | 0.79588 | 0.76376 | 0.71289
43602.4461 | 1.2357 | 1.4646 | 1.3851 | 1.0339 | 0.90007 | 0.7953 | 0.76222 | 0.71289
43602.4462 | 1.2343 | 1.4673 | 1.388 | 1.0368 | 0.90246 | 0.7968 | 0.76304 | 0.71342
43602.4462 | 1.2341 | 1.4676 | 1.3876 | 1.0368 | 0.90251 | 0.79661 | 0.76267 | 0.71281
43602.4462 | 1.2334 | 1.4665 | 1.3873 | 1.0365 | 0.90248 | 0.79685 | 0.76294 | 0.71333
43602.4462 | 1.2355 | 1.4669 | 1.3874 | 1.036 | 0.90305 | 0.79749 | 0.76331 | 0.71393
43602.4462 | 1.2447 | 1.4694 | 1.3894 | 1.0384 | 0.90394 | 0.79801 | 0.76653 | 0.71426
43602.4462 | 1.2412 | 1.4694 | 1.3889 | 1.0377 | 0.90392 | 0.79818 | 0.76528 | 0.71368
43602.4462 | 1.2401 | 1.4706 | 1.3905 | 1.0384 | 0.90483 | 0.79869 | 0.76472 | 0.71423
43602.4462 | 1.242 | 1.4724 | 1.3921 | 1.0406 | 0.90587 | 0.79914 | 0.76528 | 0.71448
43602.4462 | 1.2406 | 1.4729 | 1.3923 | 1.0403 | 0.90519 | 0.79897 | 0.76519 | 0.71455
43602.4463 | 1.2426 | 1.4742 | 1.3935 | 1.0411 | 0.9068 | 0.80034 | 0.76876 | 0.71434
43602.4463 | 1.2448 | 1.4752 | 1.3942 | 1.0417 | 0.90687 | 0.80024 | 0.76635 | 0.71433
43602.4463 | 1.2408 | 1.4777 | 1.3963 | 1.0438 | 0.90766 | 0.80123 | 0.76662 | 0.71476
43602.4463 | 1.2491 | 1.478 | 1.397 | 1.0442 | 0.90853 | 0.80134 | 0.76656 | 0.71515
43602.4463 | 1.2453 | 1.4786 | 1.397 | 1.0441 | 0.90896 | 0.80241 | 0.7678 | 0.71561
43602.4463 | 1.249 | 1.4806 | 1.3991 | 1.0448 | 0.90955 | 0.80287 | 0.77092 | 0.71574
43602.4463 | 1.2495 | 1.4841 | 1.4019 | 1.0479 | 0.91091 | 0.80362 | 0.76932 | 0.71574
43602.4463 | 1.2519 | 1.4848 | 1.4031 | 1.0492 | 0.91302 | 0.80481 | 0.76953 | 0.71637
43602.4464 | 1.2511 | 1.4872 | 1.4042 | 1.0494 | 0.91331 | 0.80578 | 0.77023 | 0.7166
43602.4464 | 1.2579 | 1.4889 | 1.4057 | 1.0509 | 0.91438 | 0.80683 | 0.77118 | 0.71718
43602.4464 | 1.2569 | 1.4901 | 1.4076 | 1.0523 | 0.9155 | 0.80717 | 0.77258 | 0.71719
43602.4464 | 1.2565 | 1.4908 | 1.408 | 1.0515 | 0.91529 | 0.80704 | 0.77587 | 0.71732
43602.4464 | 1.2525 | 1.493 | 1.409 | 1.0523 | 0.91592 | 0.80762 | 0.77306 | 0.71748
43602.4464 | 1.263 | 1.4951 | 1.4109 | 1.0543 | 0.91724 | 0.80866 | 0.77328 | 0.71749
43602.4464 | 1.2542 | 1.4923 | 1.4093 | 1.0519 | 0.91685 | 0.80856 | 0.77285 | 0.71767
43602.4464 | 1.2617 | 1.4951 | 1.4121 | 1.0548 | 0.91713 | 0.80877 | 0.77311 | 0.71796
43602.4464 | 1.2632 | 1.4971 | 1.4131 | 1.0557 | 0.91887 | 0.80988 | 0.77411 | 0.71833
43602.4465 | 1.2616 | 1.4931 | 1.4114 | 1.0529 | 0.91783 | 0.80912 | 0.77386 | 0.71797
43602.4465 | 1.2604 | 1.4983 | 1.4139 | 1.0554 | 0.91835 | 0.8099 | 0.7734 | 0.71845
43602.4465 | 1.26 | 1.4978 | 1.4143 | 1.056 | 0.91939 | 0.81113 | 0.77504 | 0.71896
43602.4465 | 1.2591 | 1.4984 | 1.4141 | 1.0549 | 0.91952 | 0.81093 | 0.77875 | 0.71913
43602.4465 | 1.2531 | 1.4974 | 1.414 | 1.0556 | 0.91864 | 0.81051 | 0.776 | 0.71888
43602.4465 | 1.2566 | 1.4985 | 1.415 | 1.0559 | 0.91872 | 0.81044 | 0.77482 | 0.71892
43602.4465 | 1.263 | 1.5002 | 1.4164 | 1.0568 | 0.92038 | 0.81158 | 0.77578 | 0.71928
43602.4465 | 1.2576 | 1.498 | 1.4144 | 1.0548 | 0.9198 | 0.81092 | 0.77567 | 0.719
43602.4465 | 1.2613 | 1.4994 | 1.4161 | 1.0565 | 0.91913 | 0.8106 | 0.77475 | 0.71874
43602.4185 | 1.2567 | 1.499 | 1.416 | 1.0556 | 0.91917 | 0.8107 | 0.77496 | 0.71884
43602.4471 | 1.2549 | 1.4987 | 1.4152 | 1.0527 | 0.91691 | 0.80885 | 0.77572 | 0.71763
43602.4471 | 1.2471 | 1.4974 | 1.4148 | 1.0531 | 0.9171 | 0.8086 | 0.7737 | 0.71728
43602.4471 | 1.2535 | 1.4985 | 1.4158 | 1.0528 | 0.91653 | 0.80847 | 0.77319 | 0.71725
43602.4472 | 1.2484 | 1.4978 | 1.4157 | 1.0521 | 0.91787 | 0.80924 | 0.77352 | 0.71733
43602.4472 | 1.2491 | 1.4981 | 1.4149 | 1.0515 | 0.9169 | 0.80809 | 0.77239 | 0.71713
43602.4472 | 1.2528 | 1.4982 | 1.4152 | 1.0517 | 0.91612 | 0.80743 | 0.77214 | 0.71701
43602.4472 | 1.2514 | 1.4994 | 1.4159 | 1.0523 | 0.91803 | 0.80894 | 0.77594 | 0.7174
43602.4472 | 1.2525 | 1.4998 | 1.4156 | 1.0527 | 0.91693 | 0.80805 | 0.77249 | 0.71717
43602.4472 | 1.2473 | 1.4984 | 1.4155 | 1.052 | 0.91839 | 0.80892 | 0.77297 | 0.71776
43602.4472 | 1.2506 | 1.4991 | 1.4159 | 1.0512 | 0.91625 | 0.80782 | 0.77245 | 0.71701
43602.4472 | 1.2523 | 1.4998 | 1.4165 | 1.0522 | 0.91745 | 0.80801 | 0.77408 | 0.71681
43602.4472 | 1.2456 | 1.4996 | 1.417 | 1.0525 | 0.91812 | 0.80895 | 0.77595 | 0.71734
43602.4473 | 1.2525 | 1.5005 | 1.4176 | 1.0533 | 0.91725 | 0.8084 | 0.77347 | 0.71699
43602.4473 | 1.2458 | 1.4983 | 1.4161 | 1.0508 | 0.91736 | 0.80871 | 0.77278 | 0.71726
43602.4473 | 1.2472 | 1.4985 | 1.4166 | 1.0511 | 0.91705 | 0.80775 | 0.77202 | 0.71695
43602.4473 | 1.2478 | 1.5001 | 1.4178 | 1.052 | 0.91736 | 0.80863 | 0.77224 | 0.71736
43602.4473 | 1.249 | 1.4994 | 1.4167 | 1.0515 | 0.91712 | 0.80797 | 0.77447 | 0.71671
43602.4473 | 1.2407 | 1.4988 | 1.4167 | 1.051 | 0.91626 | 0.80776 | 0.77419 | 0.71653
43602.4473 | 1.2399 | 1.5 | 1.4189 | 1.052 | 0.91768 | 0.80916 | 0.77336 | 0.71735
43602.4473 | 1.25 | 1.5001 | 1.4181 | 1.0514 | 0.91768 | 0.80868 | 0.77287 | 0.71687
43602.4473 | 1.2445 | 1.4986 | 1.4175 | 1.0505 | 0.91671 | 0.80787 | 0.77204 | 0.71652
43602.4474 | 1.2342 | 1.4985 | 1.4178 | 1.05 | 0.91687 | 0.80797 | 0.77259 | 0.71672
43602.4474 | 1.2495 | 1.5005 | 1.4185 | 1.0524 | 0.91688 | 0.80837 | 0.77353 | 0.71668
43602.4474 | 1.2462 | 1.5004 | 1.4189 | 1.0513 | 0.91758 | 0.80885 | 0.77362 | 0.71674
43602.4474 | 1.2479 | 1.5 | 1.4187 | 1.0508 | 0.91729 | 0.80868 | 0.77245 | 0.71692
43602.4474 | 1.2478 | 1.5005 | 1.4195 | 1.0519 | 0.91739 | 0.80861 | 0.77263 | 0.71671
43602.4474 | 1.2431 | 1.4999 | 1.4194 | 1.0509 | 0.91788 | 0.80882 | 0.77627 | 0.71693
43602.4474 | 1.2458 | 1.4998 | 1.4197 | 1.0521 | 0.9175 | 0.80862 | 0.77486 | 0.7169
43602.4474 | 1.2463 | 1.4988 | 1.4189 | 1.0518 | 0.91765 | 0.80897 | 0.77366 | 0.7169
43602.4475 | 1.2439 | 1.4991 | 1.4189 | 1.0501 | 0.91682 | 0.80862 | 0.7729 | 0.717
43602.4475 | 1.2432 | 1.4989 | 1.4189 | 1.0509 | 0.91671 | 0.80845 | 0.77291 | 0.71692
43602.4475 | 1.246 | 1.5004 | 1.4203 | 1.0513 | 0.91715 | 0.80879 | 0.7728 | 0.71696
43602.4475 | 1.2427 | 1.4969 | 1.4182 | 1.0496 | 0.91595 | 0.80821 | 0.7721 | 0.71695
43602.4475 | 1.2385 | 1.4982 | 1.419 | 1.0501 | 0.91605 | 0.80756 | 0.77374 | 0.71631
43602.4475 | 1.2403 | 1.4994 | 1.4194 | 1.0509 | 0.91721 | 0.80861 | 0.77409 | 0.717
43602.4475 | 1.239 | 1.4989 | 1.4195 | 1.0504 | 0.91667 | 0.80784 | 0.77279 | 0.71659
43602.4475 | 1.2458 | 1.4997 | 1.4199 | 1.051 | 0.91681 | 0.8084 | 0.77285 | 0.71698
43602.4475 | 1.2449 | 1.5 | 1.4195 | 1.051 | 0.91712 | 0.80872 | 0.77269 | 0.71665
43602.4476 | 1.2387 | 1.4973 | 1.4179 | 1.0489 | 0.91625 | 0.80774 | 0.77211 | 0.71648
43602.4476 | 1.2429 | 1.4982 | 1.4184 | 1.0494 | 0.91538 | 0.80742 | 0.77367 | 0.71646
43602.4476 | 1.2397 | 1.4969 | 1.4183 | 1.0492 | 0.91632 | 0.80767 | 0.77496 | 0.71675
43602.4476 | 1.2505 | 1.4994 | 1.4194 | 1.0505 | 0.91629 | 0.80783 | 0.77262 | 0.71673
43602.4476 | 1.2363 | 1.4956 | 1.4181 | 1.0484 | 0.91591 | 0.80772 | 0.77265 | 0.71645
43602.4476 | 1.2448 | 1.4972 | 1.4187 | 1.0502 | 0.91582 | 0.80771 | 0.77227 | 0.71664
43602.4476 | 1.2388 | 1.4975 | 1.4185 | 1.0491 | 0.91603 | 0.80789 | 0.77268 | 0.7166
43602.4476 | 1.2416 | 1.4973 | 1.4183 | 1.0488 | 0.91462 | 0.80681 | 0.77159 | 0.71605
43602.4476 | 1.2362 | 1.4974 | 1.419 | 1.0487 | 0.91584 | 0.80757 | 0.77294 | 0.71626
43602.4477 | 1.2326 | 1.4967 | 1.4186 | 1.0493 | 0.91551 | 0.80773 | 0.77519 | 0.71632
43602.4477 | 1.2453 | 1.4982 | 1.4188 | 1.0498 | 0.91545 | 0.80787 | 0.7729 | 0.7166
43602.4477 | 1.2397 | 1.4957 | 1.4173 | 1.0482 | 0.91572 | 0.80747 | 0.7723 | 0.71623
43602.4477 | 1.2388 | 1.4944 | 1.4165 | 1.0474 | 0.91376 | 0.80638 | 0.7713 | 0.71618
43602.4477 | 1.2387 | 1.4954 | 1.4173 | 1.0472 | 0.9145 | 0.80648 | 0.77084 | 0.71579
43602.4477 | 1.2413 | 1.4955 | 1.4168 | 1.0472 | 0.9146 | 0.80677 | 0.77209 | 0.71611
43602.4477 | 1.2258 | 1.4947 | 1.4174 | 1.0472 | 0.91461 | 0.80654 | 0.77413 | 0.71625
43602.4477 | 1.2371 | 1.4939 | 1.4157 | 1.0466 | 0.91351 | 0.80668 | 0.77163 | 0.71603
43602.4477 | 1.2327 | 1.4917 | 1.4148 | 1.0453 | 0.91346 | 0.80603 | 0.77062 | 0.71572
43602.4478 | 1.2371 | 1.4908 | 1.413 | 1.0443 | 0.91231 | 0.80496 | 0.76971 | 0.71542
43602.4478 | 1.2339 | 1.4897 | 1.4125 | 1.0444 | 0.91264 | 0.80489 | 0.77091 | 0.71581
43602.4478 | 1.2325 | 1.4888 | 1.4116 | 1.0431 | 0.91206 | 0.80478 | 0.77157 | 0.71561
43602.4478 | 1.2376 | 1.4887 | 1.4112 | 1.0431 | 0.91146 | 0.80402 | 0.76914 | 0.71508
43602.4478 | 1.2323 | 1.4872 | 1.4101 | 1.0419 | 0.91095 | 0.80396 | 0.76868 | 0.71521
43602.4478 | 1.231 | 1.4862 | 1.409 | 1.0412 | 0.91082 | 0.80419 | 0.76922 | 0.71555
43602.4478 | 1.2351 | 1.4848 | 1.4079 | 1.0403 | 0.90949 | 0.80272 | 0.76991 | 0.71461
43602.4478 | 1.23 | 1.4852 | 1.4077 | 1.0405 | 0.90916 | 0.80276 | 0.77055 | 0.71493
43602.4478 | 1.2302 | 1.4844 | 1.4075 | 1.0409 | 0.90933 | 0.80302 | 0.76798 | 0.71504
43602.4479 | 1.2259 | 1.4837 | 1.4071 | 1.0403 | 0.90871 | 0.80236 | 0.76762 | 0.71478
43602.4479 | 1.2316 | 1.4837 | 1.4065 | 1.04 | 0.9087 | 0.80278 | 0.76766 | 0.71484
43602.4479 | 1.2346 | 1.4838 | 1.4071 | 1.04 | 0.909 | 0.8025 | 0.76737 | 0.7147
43602.4479 | 1.2282 | 1.4821 | 1.4052 | 1.0395 | 0.90856 | 0.80194 | 0.76872 | 0.71474
43602.4479 | 1.2264 | 1.4812 | 1.405 | 1.0387 | 0.90776 | 0.80167 | 0.76877 | 0.71476
43602.4479 | 1.2272 | 1.4822 | 1.4058 | 1.0399 | 0.90834 | 0.802 | 0.76733 | 0.71462
43602.4479 | 1.2249 | 1.4806 | 1.4048 | 1.0388 | 0.90788 | 0.80169 | 0.76689 | 0.71474
43602.4479 | 1.2277 | 1.4813 | 1.404 | 1.0381 | 0.90728 | 0.80137 | 0.76644 | 0.71435
43602.4479 | 1.2283 | 1.4819 | 1.405 | 1.0386 | 0.908 | 0.8018 | 0.7694 | 0.7149
43602.448 | 1.2259 | 1.4818 | 1.4052 | 1.0394 | 0.9072 | 0.80137 | 0.76852 | 0.71469
43602.448 | 1.2288 | 1.4833 | 1.4064 | 1.04 | 0.90816 | 0.80226 | 0.76756 | 0.71498
43602.448 | 1.2376 | 1.484 | 1.4059 | 1.0409 | 0.90948 | 0.80309 | 0.76798 | 0.71519
43602.4471 | 1.2257 | 1.4819 | 1.4058 | 1.0397 | 0.90907 | 0.80264 | 0.76757 | 0.71505
43602.4481 | 1.2339 | 1.4874 | 1.4084 | 1.043 | 0.91087 | 0.8045 | 0.7696 | 0.71616
43602.4481 | 1.2395 | 1.4883 | 1.41 | 1.0443 | 0.91233 | 0.80517 | 0.77324 | 0.7162
43602.4481 | 1.2359 | 1.4881 | 1.4103 | 1.0443 | 0.91202 | 0.80505 | 0.77167 | 0.71617
43602.4481 | 1.2423 | 1.4886 | 1.4102 | 1.0445 | 0.9123 | 0.80535 | 0.7709 | 0.71639
43602.4481 | 1.2388 | 1.4885 | 1.4105 | 1.0446 | 0.91292 | 0.80589 | 0.77103 | 0.71681
43602.4481 | 1.236 | 1.4891 | 1.4111 | 1.0451 | 0.91307 | 0.80642 | 0.77119 | 0.71713
43602.4482 | 1.2416 | 1.4887 | 1.4107 | 1.0453 | 0.9136 | 0.80688 | 0.77205 | 0.7174
43602.4482 | 1.2399 | 1.4885 | 1.41 | 1.0447 | 0.91331 | 0.80666 | 0.77466 | 0.71757
43602.4482 | 1.2416 | 1.4891 | 1.4098 | 1.0456 | 0.9133 | 0.80677 | 0.77255 | 0.71764
43602.4482 | 1.2386 | 1.4876 | 1.4102 | 1.0452 | 0.91342 | 0.80671 | 0.77158 | 0.71745
43602.4482 | 1.2429 | 1.4883 | 1.4094 | 1.045 | 0.91335 | 0.80627 | 0.77153 | 0.7175
43602.4482 | 1.2405 | 1.4892 | 1.4101 | 1.0461 | 0.91347 | 0.80651 | 0.77159 | 0.71733
43602.4482 | 1.2427 | 1.4881 | 1.4102 | 1.0462 | 0.9142 | 0.80682 | 0.77206 | 0.71745
43602.4482 | 1.2447 | 1.4885 | 1.4094 | 1.0445 | 0.91264 | 0.80584 | 0.77074 | 0.71688
43602.4482 | 1.2429 | 1.4885 | 1.4096 | 1.0452 | 0.91344 | 0.80643 | 0.77347 | 0.7171
43602.4483 | 1.241 | 1.4873 | 1.4086 | 1.0439 | 0.91255 | 0.80571 | 0.77228 | 0.71698
43602.4483 | 1.2378 | 1.486 | 1.4085 | 1.0436 | 0.91188 | 0.80525 | 0.77066 | 0.7164
43602.4483 | 1.2378 | 1.4858 | 1.4077 | 1.0426 | 0.91222 | 0.80492 | 0.77021 | 0.71616
43602.4483 | 1.2369 | 1.4862 | 1.4069 | 1.0431 | 0.91113 | 0.80445 | 0.7697 | 0.71604
43602.4483 | 1.2376 | 1.4854 | 1.4067 | 1.0425 | 0.91052 | 0.80418 | 0.76922 | 0.71559
43602.4483 | 1.2339 | 1.4851 | 1.4072 | 1.0422 | 0.91073 | 0.80423 | 0.77043 | 0.71596
43602.4483 | 1.2382 | 1.4842 | 1.4055 | 1.0425 | 0.9106 | 0.80406 | 0.77219 | 0.71582
43602.4483 | 1.235 | 1.4844 | 1.4052 | 1.0418 | 0.91027 | 0.8036 | 0.76935 | 0.71559
43602.4483 | 1.2296 | 1.4834 | 1.4052 | 1.0412 | 0.90928 | 0.80346 | 0.769 | 0.71565
43602.4484 | 1.2369 | 1.4841 | 1.405 | 1.0417 | 0.90983 | 0.80317 | 0.76863 | 0.71533
43602.4484 | 1.2371 | 1.4833 | 1.4044 | 1.0407 | 0.90952 | 0.80257 | 0.76798 | 0.71501
43602.4484 | 1.2317 | 1.4818 | 1.4044 | 1.0404 | 0.90919 | 0.80257 | 0.76749 | 0.71511
43602.4484 | 1.241 | 1.4848 | 1.4062 | 1.0426 | 0.90884 | 0.80292 | 0.76861 | 0.71473
43602.4484 | 1.2315 | 1.4845 | 1.4062 | 1.0418 | 0.90967 | 0.80302 | 0.77003 | 0.71506
43602.4484 | 1.2348 | 1.4849 | 1.4059 | 1.0412 | 0.91021 | 0.80403 | 0.76921 | 0.71549
43602.4484 | 1.2401 | 1.4861 | 1.407 | 1.0425 | 0.91017 | 0.80362 | 0.76861 | 0.71532
43602.4484 | 1.2387 | 1.4878 | 1.4078 | 1.043 | 0.91107 | 0.80432 | 0.77131 | 0.71559
43602.4484 | 1.238 | 1.4876 | 1.4077 | 1.0433 | 0.91177 | 0.80442 | 0.76941 | 0.71577
43602.4485 | 1.2379 | 1.4863 | 1.4069 | 1.0424 | 0.91163 | 0.80427 | 0.76935 | 0.71569
43602.4485 | 1.2363 | 1.4881 | 1.4087 | 1.0437 | 0.91152 | 0.80461 | 0.76919 | 0.71574
43602.4485 | 1.2386 | 1.4894 | 1.4097 | 1.0446 | 0.91222 | 0.80505 | 0.76955 | 0.7157
43602.4485 | 1.2424 | 1.4891 | 1.4083 | 1.0435 | 0.91263 | 0.80498 | 0.77275 | 0.71568
43602.4485 | 1.2425 | 1.4891 | 1.4082 | 1.0432 | 0.91142 | 0.80473 | 0.77069 | 0.71574
43602.4485 | 1.2404 | 1.4892 | 1.4084 | 1.0432 | 0.91114 | 0.80432 | 0.76944 | 0.71549
43602.4485 | 1.2414 | 1.4901 | 1.4088 | 1.0439 | 0.91132 | 0.804 | 0.76905 | 0.71518
43602.4485 | 1.2393 | 1.4881 | 1.4079 | 1.043 | 0.91148 | 0.80451 | 0.76952 | 0.71544
43602.4485 | 1.2456 | 1.4902 | 1.408 | 1.0448 | 0.91114 | 0.80402 | 0.76959 | 0.71523
43602.4486 | 1.2403 | 1.4891 | 1.4076 | 1.044 | 0.91222 | 0.80457 | 0.76945 | 0.71571
43602.4486 | 1.2375 | 1.488 | 1.4073 | 1.043 | 0.91066 | 0.80436 | 0.77209 | 0.71558
43602.4486 | 1.2309 | 1.4867 | 1.4069 | 1.0426 | 0.9106 | 0.80374 | 0.76994 | 0.71527
43602.4486 | 1.2388 | 1.4867 | 1.4057 | 1.0424 | 0.9096 | 0.80301 | 0.76819 | 0.71477
43602.4486 | 1.237 | 1.4863 | 1.4057 | 1.0421 | 0.90998 | 0.80319 | 0.76836 | 0.71492
43602.4486 | 1.2411 | 1.4869 | 1.4057 | 1.0417 | 0.90968 | 0.8028 | 0.76812 | 0.71519
43602.4486 | 1.2407 | 1.4864 | 1.406 | 1.042 | 0.91119 | 0.80342 | 0.76844 | 0.71511
43602.4486 | 1.2451 | 1.4867 | 1.406 | 1.0423 | 0.90975 | 0.80268 | 0.76781 | 0.71467
43602.4486 | 1.2345 | 1.485 | 1.4046 | 1.0413 | 0.90975 | 0.80269 | 0.76914 | 0.71486
43602.4487 | 1.2376 | 1.4838 | 1.4032 | 1.0399 | 0.90916 | 0.80275 | 0.77032 | 0.7151
43602.4487 | 1.231 | 1.4831 | 1.4028 | 1.0393 | 0.90745 | 0.80158 | 0.7677 | 0.71453
43602.4487 | 1.239 | 1.4853 | 1.404 | 1.0411 | 0.9078 | 0.80199 | 0.76626 | 0.71457
43602.4487 | 1.238 | 1.4837 | 1.4036 | 1.0406 | 0.90851 | 0.80208 | 0.76686 | 0.71484
43602.4487 | 1.2394 | 1.4837 | 1.4038 | 1.0412 | 0.90865 | 0.80239 | 0.76728 | 0.71464
43602.4487 | 1.2363 | 1.4817 | 1.402 | 1.0395 | 0.90768 | 0.80167 | 0.76956 | 0.71442
43602.4487 | 1.2389 | 1.4822 | 1.4015 | 1.0394 | 0.907 | 0.80112 | 0.7674 | 0.71428
43602.4481 | 1.235 | 1.483 | 1.4026 | 1.0399 | 0.90765 | 0.80179 | 0.76685 | 0.71451
43602.4488 | 1.2329 | 1.4798 | 1.4006 | 1.0376 | 0.90642 | 0.8016 | 0.76746 | 0.71501
43602.4488 | 1.2357 | 1.4793 | 1.3996 | 1.038 | 0.90624 | 0.80078 | 0.76644 | 0.71417
43602.4489 | 1.2339 | 1.4797 | 1.4005 | 1.0376 | 0.90624 | 0.80049 | 0.76558 | 0.71452
43602.4489 | 1.2317 | 1.4803 | 1.4006 | 1.0379 | 0.90638 | 0.80053 | 0.76546 | 0.71456
43602.4489 | 1.2365 | 1.4803 | 1.4007 | 1.0386 | 0.90652 | 0.80072 | 0.76746 | 0.71425
43602.4489 | 1.2337 | 1.4781 | 1.3986 | 1.036 | 0.90607 | 0.80052 | 0.76894 | 0.71442
43602.4489 | 1.2371 | 1.4788 | 1.399 | 1.0368 | 0.90536 | 0.79991 | 0.76547 | 0.71423
43602.4489 | 1.2364 | 1.4786 | 1.399 | 1.0375 | 0.90558 | 0.79969 | 0.76449 | 0.71408
43602.4489 | 1.2338 | 1.4781 | 1.3986 | 1.0371 | 0.9057 | 0.80008 | 0.765 | 0.71433
43602.4489 | 1.2248 | 1.4781 | 1.3989 | 1.0368 | 0.90566 | 0.80001 | 0.7653 | 0.71432
43602.4489 | 1.2371 | 1.4789 | 1.3991 | 1.0377 | 0.90539 | 0.79993 | 0.76553 | 0.71418
43602.449 | 1.231 | 1.4784 | 1.3988 | 1.0376 | 0.90603 | 0.79976 | 0.76786 | 0.71412
43602.449 | 1.2293 | 1.4766 | 1.3973 | 1.0363 | 0.905 | 0.7997 | 0.76505 | 0.71393
43602.449 | 1.2313 | 1.4771 | 1.3977 | 1.0364 | 0.90475 | 0.79957 | 0.76497 | 0.71409
43602.449 | 1.2316 | 1.4759 | 1.3973 | 1.0368 | 0.90469 | 0.79876 | 0.76468 | 0.71342
43602.449 | 1.2255 | 1.476 | 1.397 | 1.0355 | 0.90474 | 0.79958 | 0.76919 | 0.7142
43602.449 | 1.2367 | 1.4758 | 1.3967 | 1.0358 | 0.9044 | 0.79914 | 0.76674 | 0.71394
43602.449 | 1.2331 | 1.4751 | 1.3951 | 1.0347 | 0.9039 | 0.79854 | 0.76413 | 0.71396
43602.449 | 1.2302 | 1.4729 | 1.3945 | 1.0336 | 0.9035 | 0.79836 | 0.76374 | 0.71381
43602.449 | 1.2293 | 1.4728 | 1.3944 | 1.0339 | 0.90308 | 0.79838 | 0.76328 | 0.71349
43602.4491 | 1.2262 | 1.4726 | 1.3937 | 1.0335 | 0.90318 | 0.79808 | 0.76427 | 0.71352
43602.4491 | 1.226 | 1.4721 | 1.3936 | 1.0332 | 0.90261 | 0.7978 | 0.76348 | 0.71347
43602.4491 | 1.2251 | 1.4715 | 1.3932 | 1.0329 | 0.9024 | 0.79751 | 0.76332 | 0.71328
43602.4491 | 1.2263 | 1.4713 | 1.3918 | 1.033 | 0.90185 | 0.79716 | 0.76499 | 0.71324
43602.4491 | 1.2261 | 1.4703 | 1.3913 | 1.0325 | 0.90181 | 0.79702 | 0.76273 | 0.71336
43602.4491 | 1.232 | 1.4708 | 1.3916 | 1.0325 | 0.90151 | 0.79684 | 0.76275 | 0.71312
43602.4491 | 1.2228 | 1.4692 | 1.3909 | 1.0318 | 0.90085 | 0.79653 | 0.76174 | 0.71259
43602.4491 | 1.2286 | 1.4682 | 1.3903 | 1.0311 | 0.90087 | 0.79633 | 0.76167 | 0.71275
43602.4492 | 1.223 | 1.4689 | 1.3905 | 1.0319 | 0.90104 | 0.79631 | 0.76465 | 0.71303
43602.4492 | 1.2253 | 1.4678 | 1.39 | 1.0308 | 0.90021 | 0.79641 | 0.76381 | 0.71304
43602.4492 | 1.222 | 1.4678 | 1.3903 | 1.0309 | 0.90126 | 0.79647 | 0.76287 | 0.71315
43602.4492 | 1.2272 | 1.4677 | 1.3904 | 1.0316 | 0.90076 | 0.79609 | 0.76209 | 0.71281
43602.4492 | 1.2259 | 1.4672 | 1.3898 | 1.0315 | 0.90128 | 0.79665 | 0.76359 | 0.7133
43602.4492 | 1.2301 | 1.4671 | 1.3897 | 1.0306 | 0.90125 | 0.79645 | 0.76583 | 0.71325
43602.4492 | 1.2317 | 1.4667 | 1.389 | 1.031 | 0.90079 | 0.79595 | 0.76261 | 0.71307
43602.4492 | 1.2263 | 1.4665 | 1.3892 | 1.0312 | 0.90009 | 0.79579 | 0.76165 | 0.7128
43602.4492 | 1.2282 | 1.4652 | 1.3882 | 1.03 | 0.90098 | 0.79675 | 0.76226 | 0.71369
43602.4493 | 1.2226 | 1.4639 | 1.3875 | 1.0304 | 0.89927 | 0.79528 | 0.7606 | 0.71309
43602.4493 | 1.2277 | 1.4668 | 1.3892 | 1.0318 | 0.89989 | 0.79592 | 0.76351 | 0.71286
43602.4493 | 1.2274 | 1.4649 | 1.3876 | 1.0307 | 0.90128 | 0.79671 | 0.76307 | 0.71358
43602.4493 | 1.2247 | 1.4631 | 1.3859 | 1.0294 | 0.89901 | 0.79511 | 0.76105 | 0.71319
43602.4493 | 1.2247 | 1.4628 | 1.386 | 1.029 | 0.89882 | 0.79471 | 0.76053 | 0.713
43602.4493 | 1.2229 | 1.4626 | 1.385 | 1.0295 | 0.89875 | 0.79465 | 0.76008 | 0.71288
43602.4488 | 1.226 | 1.4634 | 1.3855 | 1.0297 | 0.89876 | 0.79471 | 0.76232 | 0.71301
43602.4494 | 1.2319 | 1.4671 | 1.3882 | 1.0323 | 0.90102 | 0.79631 | 0.76264 | 0.71362
43602.4494 | 1.2318 | 1.4671 | 1.3877 | 1.0314 | 0.90103 | 0.79636 | 0.76187 | 0.71338
43602.4494 | 1.235 | 1.4679 | 1.3884 | 1.0327 | 0.90123 | 0.79664 | 0.7625 | 0.71359
43602.4495 | 1.2317 | 1.4686 | 1.3894 | 1.0339 | 0.90165 | 0.79708 | 0.76318 | 0.71417
43602.4495 | 1.232 | 1.4679 | 1.3885 | 1.0333 | 0.90236 | 0.79724 | 0.76243 | 0.7139
43602.4495 | 1.2335 | 1.4694 | 1.3887 | 1.0335 | 0.90195 | 0.79696 | 0.76287 | 0.71399
43602.4495 | 1.2342 | 1.4681 | 1.3891 | 1.0341 | 0.90285 | 0.7977 | 0.76698 | 0.71438
43602.4495 | 1.2359 | 1.4673 | 1.3886 | 1.0339 | 0.90322 | 0.79756 | 0.76544 | 0.71412
43602.4495 | 1.2349 | 1.4688 | 1.3893 | 1.0343 | 0.90261 | 0.79738 | 0.76396 | 0.71382
43602.4495 | 1.2352 | 1.4705 | 1.3905 | 1.035 | 0.90323 | 0.79817 | 0.7639 | 0.71423
43602.4495 | 1.2394 | 1.4729 | 1.3916 | 1.0362 | 0.90466 | 0.79911 | 0.7646 | 0.71482
43602.4495 | 1.238 | 1.4701 | 1.3907 | 1.0349 | 0.90421 | 0.79881 | 0.76554 | 0.71448
43602.4496 | 1.2363 | 1.4702 | 1.3909 | 1.0354 | 0.90386 | 0.79852 | 0.76438 | 0.71417
43602.4496 | 1.2305 | 1.4696 | 1.3902 | 1.0348 | 0.90383 | 0.79856 | 0.76773 | 0.71451
43602.4496 | 1.2351 | 1.4709 | 1.3907 | 1.0353 | 0.90373 | 0.79882 | 0.76551 | 0.71501
43602.4496 | 1.2406 | 1.4713 | 1.391 | 1.0361 | 0.90435 | 0.79882 | 0.76476 | 0.71467
43602.4496 | 1.2389 | 1.471 | 1.3911 | 1.0362 | 0.90443 | 0.79922 | 0.76501 | 0.71486
43602.4496 | 1.2359 | 1.472 | 1.3921 | 1.0362 | 0.90477 | 0.79929 | 0.76451 | 0.71522
43602.4496 | 1.2382 | 1.4723 | 1.3921 | 1.036 | 0.90582 | 0.80003 | 0.76625 | 0.71525
43602.4496 | 1.2365 | 1.4727 | 1.3928 | 1.0365 | 0.90552 | 0.79989 | 0.76567 | 0.71549
43602.4496 | 1.24 | 1.4714 | 1.3908 | 1.0354 | 0.90483 | 0.79973 | 0.76654 | 0.71501
43602.4497 | 1.2439 | 1.4741 | 1.3928 | 1.0374 | 0.90527 | 0.79988 | 0.76538 | 0.71546
43602.4497 | 1.2368 | 1.4725 | 1.3922 | 1.0363 | 0.90527 | 0.7998 | 0.76529 | 0.71523
43602.4497 | 1.2351 | 1.4716 | 1.3917 | 1.0358 | 0.90533 | 0.80037 | 0.76974 | 0.71563
43602.4497 | 1.2397 | 1.4742 | 1.3931 | 1.0375 | 0.90508 | 0.79989 | 0.76716 | 0.71526
43602.4497 | 1.2372 | 1.4724 | 1.3922 | 1.0364 | 0.90609 | 0.80093 | 0.76642 | 0.71541
43602.4497 | 1.2405 | 1.4744 | 1.3931 | 1.038 | 0.90588 | 0.80084 | 0.76621 | 0.71591
43602.4497 | 1.2402 | 1.4748 | 1.3934 | 1.0374 | 0.9064 | 0.80064 | 0.76656 | 0.71545
43602.4497 | 1.2418 | 1.4738 | 1.3931 | 1.0381 | 0.90629 | 0.80055 | 0.76622 | 0.71546
43602.4497 | 1.2377 | 1.4741 | 1.393 | 1.0373 | 0.90576 | 0.80011 | 0.76559 | 0.71537
43602.4498 | 1.2326 | 1.4722 | 1.3918 | 1.0364 | 0.90521 | 0.80007 | 0.7665 | 0.71509
43602.4498 | 1.2378 | 1.4729 | 1.393 | 1.0372 | 0.9055 | 0.80004 | 0.76844 | 0.71519
43602.4498 | 1.2396 | 1.474 | 1.3931 | 1.0379 | 0.90616 | 0.80076 | 0.76762 | 0.716
43602.4498 | 1.2486 | 1.4752 | 1.3936 | 1.0388 | 0.90653 | 0.80066 | 0.76699 | 0.71593
43602.4498 | 1.2314 | 1.4733 | 1.3921 | 1.0367 | 0.90572 | 0.8 | 0.76572 | 0.7154
43602.4498 | 1.2377 | 1.4731 | 1.3923 | 1.0377 | 0.90606 | 0.80032 | 0.76643 | 0.71569
43602.4498 | 1.241 | 1.4737 | 1.3924 | 1.0374 | 0.90569 | 0.80009 | 0.76561 | 0.71525
43602.4498 | 1.2377 | 1.4731 | 1.3926 | 1.0369 | 0.90644 | 0.8007 | 0.76603 | 0.71576
43602.4498 | 1.2359 | 1.4744 | 1.3931 | 1.0378 | 0.90526 | 0.79937 | 0.76564 | 0.71477
43602.4499 | 1.2314 | 1.4736 | 1.393 | 1.0376 | 0.90526 | 0.80009 | 0.77031 | 0.71542
43602.4499 | 1.2405 | 1.4733 | 1.3927 | 1.0375 | 0.90579 | 0.80041 | 0.76789 | 0.7156
43602.4499 | 1.2434 | 1.4758 | 1.3943 | 1.0396 | 0.90649 | 0.80079 | 0.76681 | 0.71613
43602.4494 | 1.2395 | 1.4748 | 1.3928 | 1.038 | 0.90664 | 0.80111 | 0.76669 | 0.71604
43602.45 | 1.238 | 1.4727 | 1.392 | 1.038 | 0.90576 | 0.80027 | 0.76577 | 0.71619
43602.45 | 1.2339 | 1.4698 | 1.3897 | 1.035 | 0.90531 | 0.80031 | 0.76644 | 0.71612
43602.45 | 1.2416 | 1.471 | 1.39 | 1.0361 | 0.90371 | 0.79933 | 0.76462 | 0.71547
43602.45 | 1.2358 | 1.4693 | 1.3889 | 1.0347 | 0.90413 | 0.79949 | 0.76528 | 0.7156
43602.45 | 1.2322 | 1.468 | 1.3872 | 1.0338 | 0.90291 | 0.79812 | 0.76711 | 0.71515
43602.45 | 1.2283 | 1.4665 | 1.3864 | 1.0326 | 0.90285 | 0.79812 | 0.76464 | 0.71532
43602.4501 | 1.2325 | 1.465 | 1.385 | 1.0324 | 0.90078 | 0.79751 | 0.76347 | 0.71512
43602.4501 | 1.2326 | 1.4642 | 1.3846 | 1.0321 | 0.90121 | 0.79749 | 0.7635 | 0.71532
43602.4501 | 1.2304 | 1.4627 | 1.3834 | 1.0315 | 0.90115 | 0.79753 | 0.76379 | 0.71554
43602.4501 | 1.2303 | 1.4601 | 1.3808 | 1.0283 | 0.8998 | 0.79587 | 0.76465 | 0.71432
43602.4501 | 1.2326 | 1.4607 | 1.3803 | 1.0287 | 0.89855 | 0.79527 | 0.76514 | 0.71432
43602.4501 | 1.2298 | 1.4611 | 1.3807 | 1.0296 | 0.89876 | 0.79526 | 0.76202 | 0.71441
43602.4501 | 1.2258 | 1.4591 | 1.3799 | 1.029 | 0.89845 | 0.79568 | 0.76207 | 0.71431
43602.4501 | 1.2275 | 1.4594 | 1.3792 | 1.0286 | 0.89761 | 0.79495 | 0.76165 | 0.71415
43602.4501 | 1.227 | 1.4577 | 1.3774 | 1.0261 | 0.89756 | 0.79422 | 0.76106 | 0.71396
43602.4502 | 1.2264 | 1.4573 | 1.3774 | 1.0271 | 0.89641 | 0.79348 | 0.75995 | 0.7138
43602.4502 | 1.2305 | 1.458 | 1.3775 | 1.0276 | 0.89656 | 0.79355 | 0.7602 | 0.71344
43602.4502 | 1.2263 | 1.4563 | 1.3767 | 1.0269 | 0.89756 | 0.79489 | 0.76226 | 0.71445
43602.4502 | 1.2267 | 1.4564 | 1.3766 | 1.0264 | 0.89661 | 0.79402 | 0.76034 | 0.71433
43602.4502 | 1.2263 | 1.4562 | 1.3765 | 1.0264 | 0.89675 | 0.79308 | 0.76356 | 0.71336
43602.4502 | 1.2271 | 1.4566 | 1.3766 | 1.0276 | 0.89629 | 0.79337 | 0.76147 | 0.71371
43602.4502 | 1.2317 | 1.4595 | 1.3782 | 1.0281 | 0.89767 | 0.79456 | 0.76158 | 0.71456
43602.4502 | 1.2278 | 1.458 | 1.3777 | 1.0285 | 0.89845 | 0.79454 | 0.76125 | 0.71402
43602.4503 | 1.2288 | 1.4573 | 1.3778 | 1.0278 | 0.89687 | 0.79388 | 0.7608 | 0.71394
43602.4503 | 1.2326 | 1.4596 | 1.3799 | 1.0296 | 0.89869 | 0.79507 | 0.76194 | 0.71454
43602.4503 | 1.2321 | 1.46 | 1.3791 | 1.0297 | 0.89943 | 0.79609 | 0.76253 | 0.71518
43602.4503 | 1.2333 | 1.4615 | 1.3811 | 1.0313 | 0.89948 | 0.79569 | 0.76197 | 0.71444
43602.4503 | 1.236 | 1.4616 | 1.3813 | 1.0312 | 0.90046 | 0.7962 | 0.76688 | 0.71472
43602.4503 | 1.236 | 1.4612 | 1.3808 | 1.031 | 0.90021 | 0.7964 | 0.76429 | 0.71483
43602.45 | 1.2377 | 1.4641 | 1.3833 | 1.0345 | 0.90134 | 0.79744 | 0.76378 | 0.71575
43602.4504 | 1.243 | 1.4716 | 1.3892 | 1.0391 | 0.90599 | 0.80068 | 0.77037 | 0.71674
43602.4504 | 1.2373 | 1.472 | 1.3898 | 1.039 | 0.90746 | 0.80184 | 0.76778 | 0.71675
43602.4504 | 1.243 | 1.4744 | 1.3913 | 1.0396 | 0.90599 | 0.8012 | 0.76717 | 0.71654
43602.4505 | 1.245 | 1.4766 | 1.393 | 1.0425 | 0.90938 | 0.80336 | 0.76941 | 0.71761
43602.4505 | 1.2504 | 1.4755 | 1.3925 | 1.0415 | 0.90846 | 0.80312 | 0.76987 | 0.71769
43602.4505 | 1.248 | 1.4769 | 1.3936 | 1.0427 | 0.90966 | 0.80398 | 0.7699 | 0.71814
43602.4505 | 1.244 | 1.4753 | 1.3932 | 1.0409 | 0.9086 | 0.80288 | 0.76824 | 0.71698
43602.4505 | 1.2476 | 1.4785 | 1.3949 | 1.0429 | 0.90896 | 0.80347 | 0.76814 | 0.71738
43602.4505 | 1.2448 | 1.4778 | 1.395 | 1.0421 | 0.9096 | 0.80387 | 0.76857 | 0.71794
43602.4505 | 1.2477 | 1.4787 | 1.3953 | 1.0434 | 0.91065 | 0.80467 | 0.7719 | 0.71784
43602.4505 | 1.2485 | 1.479 | 1.3957 | 1.0442 | 0.91094 | 0.80466 | 0.77018 | 0.71794
43602.4505 | 1.2481 | 1.4803 | 1.3966 | 1.0446 | 0.91075 | 0.80484 | 0.76956 | 0.71808
43602.4506 | 1.2498 | 1.4786 | 1.3956 | 1.0429 | 0.91205 | 0.8058 | 0.77023 | 0.7184
43602.4506 | 1.2506 | 1.4793 | 1.3964 | 1.0427 | 0.91053 | 0.80451 | 0.76989 | 0.71815
43602.4506 | 1.2523 | 1.4812 | 1.3978 | 1.0449 | 0.91177 | 0.80574 | 0.77107 | 0.71903
43602.4506 | 1.2478 | 1.4802 | 1.3969 | 1.0442 | 0.91201 | 0.8056 | 0.77283 | 0.71853
43602.4506 | 1.2522 | 1.4807 | 1.3966 | 1.0436 | 0.91138 | 0.80505 | 0.7718 | 0.71852
43602.4506 | 1.242 | 1.4795 | 1.3963 | 1.0435 | 0.91084 | 0.80478 | 0.77019 | 0.71838
43602.4506 | 1.2512 | 1.4805 | 1.3973 | 1.0437 | 0.91082 | 0.80524 | 0.7702 | 0.71825
43602.4506 | 1.2523 | 1.4815 | 1.3977 | 1.0441 | 0.91252 | 0.80556 | 0.77063 | 0.71819
43602.4506 | 1.2506 | 1.4784 | 1.3956 | 1.0426 | 0.91069 | 0.80476 | 0.77013 | 0.71847
43602.4507 | 1.2425 | 1.4806 | 1.3977 | 1.0437 | 0.9107 | 0.80459 | 0.76964 | 0.71845
43602.4507 | 1.2405 | 1.4807 | 1.3979 | 1.0451 | 0.91181 | 0.80585 | 0.77293 | 0.71896
43602.4507 | 1.2516 | 1.481 | 1.3976 | 1.0442 | 0.91219 | 0.80612 | 0.77321 | 0.71895
43602.4507 | 1.2452 | 1.4815 | 1.3983 | 1.0445 | 0.91139 | 0.80522 | 0.77034 | 0.71865
43602.4507 | 1.245 | 1.4793 | 1.3966 | 1.0432 | 0.91163 | 0.80546 | 0.77016 | 0.7185
43602.4507 | 1.2508 | 1.4796 | 1.3963 | 1.0425 | 0.91026 | 0.80455 | 0.76966 | 0.71804
43602.4507 | 1.2482 | 1.479 | 1.3959 | 1.0425 | 0.91028 | 0.80448 | 0.77027 | 0.71825
43602.4507 | 1.2455 | 1.4764 | 1.3955 | 1.0414 | 0.91028 | 0.80432 | 0.76987 | 0.71826
43602.4507 | 1.2437 | 1.4781 | 1.3956 | 1.0421 | 0.90939 | 0.80405 | 0.77223 | 0.71826
43602.4508 | 1.2407 | 1.478 | 1.3955 | 1.0407 | 0.90981 | 0.80441 | 0.772 | 0.71829
43602.4508 | 1.2457 | 1.4772 | 1.3946 | 1.0407 | 0.90851 | 0.80297 | 0.76838 | 0.71704
43602.4508 | 1.2465 | 1.4767 | 1.3944 | 1.041 | 0.90888 | 0.80373 | 0.76914 | 0.71821
43602.4508 | 1.2445 | 1.4768 | 1.3948 | 1.0408 | 0.9093 | 0.80385 | 0.76922 | 0.71813
43602.4504 | 1.244 | 1.4773 | 1.3944 | 1.0409 | 0.90858 | 0.80293 | 0.76896 | 0.71775
43602.4509 | 1.2553 | 1.4837 | 1.4005 | 1.0448 | 0.91136 | 0.80523 | 0.77391 | 0.71859
43602.4509 | 1.2527 | 1.4836 | 1.4006 | 1.0446 | 0.91263 | 0.80625 | 0.77229 | 0.71919
43602.4509 | 1.2468 | 1.4847 | 1.4014 | 1.0455 | 0.91177 | 0.80552 | 0.77142 | 0.71818
43602.4509 | 1.2505 | 1.4847 | 1.402 | 1.0457 | 0.91265 | 0.80595 | 0.77143 | 0.71879
43602.451 | 1.2464 | 1.4856 | 1.4021 | 1.0452 | 0.91243 | 0.80675 | 0.77182 | 0.71942
43602.451 | 1.251 | 1.4858 | 1.4029 | 1.0463 | 0.91375 | 0.80763 | 0.77292 | 0.71984
43602.451 | 1.2612 | 1.4882 | 1.4041 | 1.048 | 0.91314 | 0.80654 | 0.77165 | 0.71878
43602.451 | 1.2455 | 1.4866 | 1.4036 | 1.0462 | 0.91445 | 0.80772 | 0.77389 | 0.71955
43602.451 | 1.2557 | 1.4878 | 1.404 | 1.0472 | 0.91392 | 0.80787 | 0.77612 | 0.71973
43602.451 | 1.2512 | 1.4888 | 1.4051 | 1.0484 | 0.9141 | 0.80746 | 0.77315 | 0.71948
43602.451 | 1.2565 | 1.4895 | 1.4058 | 1.048 | 0.91479 | 0.80826 | 0.77322 | 0.71982
43602.451 | 1.246 | 1.4883 | 1.4049 | 1.0469 | 0.91433 | 0.80803 | 0.77323 | 0.71977
43602.451 | 1.2564 | 1.4899 | 1.4056 | 1.0484 | 0.91421 | 0.80782 | 0.77302 | 0.7195
43602.4511 | 1.2544 | 1.489 | 1.4052 | 1.0473 | 0.9147 | 0.80794 | 0.77411 | 0.7194
43602.4511 | 1.2492 | 1.4882 | 1.4054 | 1.0471 | 0.91553 | 0.80887 | 0.77586 | 0.72062
43602.4511 | 1.2561 | 1.4887 | 1.406 | 1.0478 | 0.91391 | 0.80755 | 0.77228 | 0.71949
43602.4511 | 1.2519 | 1.4886 | 1.4057 | 1.0473 | 0.91533 | 0.80836 | 0.77306 | 0.72007
43602.4511 | 1.2495 | 1.4884 | 1.4053 | 1.0472 | 0.91385 | 0.80695 | 0.77129 | 0.71908
43602.4511 | 1.2521 | 1.4878 | 1.4059 | 1.047 | 0.91442 | 0.80749 | 0.77193 | 0.71935
43602.4511 | 1.2442 | 1.4898 | 1.4074 | 1.047 | 0.91508 | 0.80864 | 0.77397 | 0.72019
43602.4511 | 1.2508 | 1.4899 | 1.4064 | 1.0473 | 0.91342 | 0.80713 | 0.77309 | 0.71894
43602.4511 | 1.25 | 1.4896 | 1.4069 | 1.0475 | 0.91518 | 0.80885 | 0.77708 | 0.72051
43602.4512 | 1.2514 | 1.4893 | 1.4074 | 1.0477 | 0.9149 | 0.80847 | 0.7738 | 0.7198
43602.4512 | 1.2447 | 1.4917 | 1.4083 | 1.0491 | 0.91473 | 0.80824 | 0.77309 | 0.71964
43602.4512 | 1.2473 | 1.4902 | 1.4079 | 1.0485 | 0.91586 | 0.80875 | 0.77361 | 0.72006
43602.4512 | 1.2535 | 1.4915 | 1.4082 | 1.0485 | 0.91609 | 0.80896 | 0.77364 | 0.72014
43602.4512 | 1.2448 | 1.4893 | 1.4066 | 1.0461 | 0.91419 | 0.80794 | 0.77316 | 0.71969
43602.4512 | 1.2613 | 1.4946 | 1.4104 | 1.0501 | 0.91484 | 0.8079 | 0.77312 | 0.71949
43602.4512 | 1.2517 | 1.4906 | 1.4081 | 1.0474 | 0.91598 | 0.80903 | 0.77291 | 0.72004
43602.4512 | 1.2548 | 1.4926 | 1.4094 | 1.0485 | 0.91641 | 0.80935 | 0.77461 | 0.72044
43602.4509 | 1.2523 | 1.4929 | 1.4094 | 1.0485 | 0.91608 | 0.8089 | 0.77655 | 0.72006
43602.4513 | 1.2533 | 1.4997 | 1.4165 | 1.0529 | 0.91949 | 0.81177 | 0.77584 | 0.72065
43602.4514 | 1.2543 | 1.4995 | 1.4161 | 1.0524 | 0.91912 | 0.81124 | 0.77592 | 0.72017
43602.4514 | 1.2555 | 1.5 | 1.4164 | 1.0518 | 0.9196 | 0.81228 | 0.77622 | 0.72098
43602.4514 | 1.2552 | 1.5007 | 1.4178 | 1.0529 | 0.91993 | 0.81246 | 0.77541 | 0.72078
43602.4514 | 1.2565 | 1.5014 | 1.4183 | 1.0538 | 0.9198 | 0.81206 | 0.77617 | 0.72073
43602.4514 | 1.2565 | 1.5016 | 1.4191 | 1.0535 | 0.92107 | 0.81305 | 0.7769 | 0.72138
43602.4514 | 1.2546 | 1.5025 | 1.4202 | 1.0543 | 0.92091 | 0.81324 | 0.77899 | 0.72133
43602.4514 | 1.253 | 1.5035 | 1.4203 | 1.0536 | 0.92127 | 0.81346 | 0.78168 | 0.72124
43602.4514 | 1.2576 | 1.5052 | 1.4216 | 1.0547 | 0.92153 | 0.81345 | 0.77807 | 0.72088
43602.4514 | 1.2558 | 1.5052 | 1.4225 | 1.0558 | 0.9216 | 0.81366 | 0.77775 | 0.72119
43602.4515 | 1.2573 | 1.5073 | 1.4246 | 1.0568 | 0.92301 | 0.81471 | 0.77881 | 0.72168
43602.4515 | 1.2594 | 1.5095 | 1.4262 | 1.0577 | 0.92401 | 0.81525 | 0.77918 | 0.72185
43602.4515 | 1.2634 | 1.511 | 1.4268 | 1.0585 | 0.92458 | 0.81592 | 0.78047 | 0.72206
43602.4515 | 1.2622 | 1.5113 | 1.4276 | 1.0589 | 0.92556 | 0.81647 | 0.77994 | 0.72231
43602.4515 | 1.263 | 1.5129 | 1.4291 | 1.0597 | 0.92597 | 0.81663 | 0.78013 | 0.72266
43602.4515 | 1.2634 | 1.5138 | 1.4296 | 1.0608 | 0.92714 | 0.81755 | 0.78462 | 0.72309
43602.4515 | 1.2663 | 1.5143 | 1.4306 | 1.0612 | 0.92802 | 0.81817 | 0.78327 | 0.72345
43602.4515 | 1.2609 | 1.515 | 1.4306 | 1.0612 | 0.92843 | 0.81883 | 0.7822 | 0.7236
43602.4515 | 1.2619 | 1.5158 | 1.4315 | 1.0607 | 0.92766 | 0.81845 | 0.78198 | 0.72347
43602.4516 | 1.2642 | 1.5162 | 1.4312 | 1.0603 | 0.92781 | 0.81801 | 0.78173 | 0.72307
43602.4516 | 1.2615 | 1.5159 | 1.4319 | 1.06 | 0.92752 | 0.81774 | 0.78127 | 0.72298
43602.4516 | 1.2649 | 1.5173 | 1.4325 | 1.0616 | 0.92825 | 0.81825 | 0.7818 | 0.7229
43602.4516 | 1.2602 | 1.5158 | 1.4321 | 1.0598 | 0.92787 | 0.81781 | 0.78154 | 0.72253
43602.4516 | 1.2561 | 1.5157 | 1.4308 | 1.0584 | 0.92662 | 0.81678 | 0.7798 | 0.72195
43602.4516 | 1.2589 | 1.5166 | 1.4311 | 1.0581 | 0.926 | 0.81671 | 0.77966 | 0.72197
43602.4516 | 1.2572 | 1.5137 | 1.4293 | 1.0567 | 0.92571 | 0.8161 | 0.78107 | 0.72161
43602.4516 | 1.2564 | 1.5143 | 1.429 | 1.0563 | 0.92496 | 0.81541 | 0.78246 | 0.72145
43602.4516 | 1.25 | 1.5127 | 1.4291 | 1.0557 | 0.92438 | 0.81503 | 0.77928 | 0.72107
43602.4513 | 1.2491 | 1.5109 | 1.4279 | 1.0543 | 0.92348 | 0.81433 | 0.77814 | 0.72073
43602.4518 | 1.2375 | 1.4997 | 1.4201 | 1.0474 | 0.91725 | 0.80963 | 0.77339 | 0.71865
43602.4518 | 1.2361 | 1.4991 | 1.4196 | 1.0472 | 0.91598 | 0.80862 | 0.77456 | 0.71802
43602.4518 | 1.2349 | 1.4986 | 1.4191 | 1.0465 | 0.91619 | 0.80897 | 0.77492 | 0.71811
43602.4518 | 1.2401 | 1.4983 | 1.4174 | 1.0457 | 0.9159 | 0.80838 | 0.77378 | 0.71804
43602.4518 | 1.2394 | 1.4979 | 1.4176 | 1.0461 | 0.9154 | 0.80781 | 0.77225 | 0.7177
43602.4518 | 1.2319 | 1.4977 | 1.4179 | 1.0457 | 0.91494 | 0.80795 | 0.77187 | 0.71774
43602.4518 | 1.233 | 1.4963 | 1.4166 | 1.0449 | 0.91509 | 0.80766 | 0.7721 | 0.71764
43602.4518 | 1.2326 | 1.4958 | 1.4152 | 1.0438 | 0.91353 | 0.80644 | 0.77308 | 0.71703
43602.4518 | 1.2282 | 1.4933 | 1.4145 | 1.0417 | 0.91269 | 0.80595 | 0.77181 | 0.71671
43602.4519 | 1.2355 | 1.4942 | 1.4151 | 1.0436 | 0.91206 | 0.80554 | 0.7705 | 0.71648
43602.4519 | 1.2383 | 1.494 | 1.4138 | 1.0424 | 0.91308 | 0.80584 | 0.77091 | 0.71689
43602.4519 | 1.2282 | 1.4925 | 1.4139 | 1.0415 | 0.91229 | 0.80541 | 0.77075 | 0.71666
43602.4519 | 1.2333 | 1.4911 | 1.412 | 1.0399 | 0.91085 | 0.80466 | 0.77071 | 0.71632
43602.4519 | 1.2286 | 1.4901 | 1.4112 | 1.0395 | 0.91056 | 0.80478 | 0.76963 | 0.71644
43602.4519 | 1.2265 | 1.4889 | 1.4105 | 1.0398 | 0.91011 | 0.80402 | 0.76876 | 0.71605
43602.4519 | 1.2197 | 1.4876 | 1.4106 | 1.0386 | 0.91043 | 0.80398 | 0.76894 | 0.71625
43602.4519 | 1.2267 | 1.4878 | 1.4087 | 1.0379 | 0.90911 | 0.80357 | 0.77296 | 0.71581
43602.4519 | 1.2251 | 1.4873 | 1.4093 | 1.038 | 0.90844 | 0.80251 | 0.76944 | 0.7155
43602.452 | 1.223 | 1.4856 | 1.4078 | 1.0365 | 0.90827 | 0.80255 | 0.76797 | 0.71536
43602.452 | 1.2225 | 1.4841 | 1.4072 | 1.036 | 0.90768 | 0.80188 | 0.76674 | 0.7154
43602.452 | 1.2276 | 1.4863 | 1.4073 | 1.0368 | 0.90734 | 0.80209 | 0.76674 | 0.71542
43602.452 | 1.2287 | 1.4864 | 1.4073 | 1.0371 | 0.9075 | 0.80159 | 0.76688 | 0.71517
43602.452 | 1.229 | 1.4853 | 1.4062 | 1.0353 | 0.90692 | 0.80144 | 0.76642 | 0.71498
43602.452 | 1.226 | 1.4849 | 1.4055 | 1.0355 | 0.9067 | 0.80104 | 0.76557 | 0.71461
43602.452 | 1.2239 | 1.4835 | 1.4045 | 1.0341 | 0.90631 | 0.80078 | 0.76644 | 0.71442
43602.452 | 1.2236 | 1.4825 | 1.4046 | 1.0343 | 0.90597 | 0.80032 | 0.76962 | 0.71434
43602.4517 | 1.2244 | 1.4849 | 1.4057 | 1.0361 | 0.90625 | 0.80058 | 0.76673 | 0.7147
43602.4521 | 1.2228 | 1.4804 | 1.4013 | 1.0323 | 0.90467 | 0.79916 | 0.76566 | 0.7141
43602.4522 | 1.2265 | 1.4827 | 1.4028 | 1.0341 | 0.9047 | 0.79972 | 0.76474 | 0.71431
43602.4522 | 1.2283 | 1.4819 | 1.4029 | 1.0341 | 0.90599 | 0.80016 | 0.76508 | 0.71427
43602.4522 | 1.2252 | 1.482 | 1.402 | 1.0337 | 0.90541 | 0.80015 | 0.76565 | 0.7142
43602.4522 | 1.2255 | 1.4831 | 1.4021 | 1.034 | 0.90521 | 0.79961 | 0.76722 | 0.71426
43602.4522 | 1.2255 | 1.4836 | 1.4029 | 1.0348 | 0.90604 | 0.80024 | 0.76557 | 0.71453
43602.4522 | 1.2289 | 1.4846 | 1.4037 | 1.0345 | 0.90625 | 0.80043 | 0.76578 | 0.71459
43602.4522 | 1.2292 | 1.4833 | 1.4032 | 1.0347 | 0.90662 | 0.80087 | 0.76584 | 0.71444
43602.4522 | 1.2255 | 1.4827 | 1.403 | 1.034 | 0.90647 | 0.80048 | 0.76728 | 0.71433
43602.4522 | 1.223 | 1.4834 | 1.4036 | 1.0355 | 0.90614 | 0.80079 | 0.76625 | 0.71468
43602.4523 | 1.2241 | 1.484 | 1.4038 | 1.0354 | 0.90684 | 0.80104 | 0.76596 | 0.71499
43602.4523 | 1.2247 | 1.4823 | 1.4025 | 1.0341 | 0.90685 | 0.80074 | 0.76605 | 0.71484
43602.4523 | 1.2282 | 1.4859 | 1.4042 | 1.0362 | 0.90627 | 0.80063 | 0.76691 | 0.71477
43602.4523 | 1.2277 | 1.4841 | 1.4038 | 1.0354 | 0.90763 | 0.80127 | 0.76667 | 0.715
43602.4523 | 1.2332 | 1.4872 | 1.4044 | 1.0358 | 0.90754 | 0.80169 | 0.7667 | 0.7149
43602.4523 | 1.2323 | 1.4872 | 1.4049 | 1.0361 | 0.90853 | 0.80177 | 0.76692 | 0.71521
43602.4523 | 1.2317 | 1.4868 | 1.405 | 1.0375 | 0.90802 | 0.80171 | 0.76997 | 0.71509
43602.4523 | 1.2359 | 1.4885 | 1.4059 | 1.0376 | 0.90897 | 0.80233 | 0.76791 | 0.71561
43602.4523 | 1.2331 | 1.4868 | 1.4052 | 1.0372 | 0.90933 | 0.80237 | 0.76805 | 0.71567
43602.4524 | 1.2376 | 1.4863 | 1.4051 | 1.0373 | 0.90884 | 0.80235 | 0.76995 | 0.71555
43602.4524 | 1.2335 | 1.4868 | 1.4059 | 1.0374 | 0.90907 | 0.80274 | 0.76845 | 0.7156
43602.4524 | 1.234 | 1.488 | 1.4062 | 1.0384 | 0.90921 | 0.80242 | 0.76774 | 0.71553
43602.4524 | 1.2299 | 1.4868 | 1.4053 | 1.0374 | 0.90958 | 0.80319 | 0.76761 | 0.71584
43602.4524 | 1.2377 | 1.4887 | 1.4069 | 1.0386 | 0.90977 | 0.80285 | 0.76757 | 0.71596
43602.4524 | 1.2305 | 1.4874 | 1.4066 | 1.0382 | 0.90973 | 0.80329 | 0.76816 | 0.71592
43602.4524 | 1.2348 | 1.4879 | 1.4066 | 1.0381 | 0.90945 | 0.80283 | 0.7674 | 0.71521
43602.4521 | 1.2355 | 1.4885 | 1.4061 | 1.0389 | 0.91067 | 0.80369 | 0.76982 | 0.71575
43602.4525 | 1.2323 | 1.4847 | 1.4025 | 1.0355 | 0.90737 | 0.80141 | 0.76617 | 0.71535
43602.4525 | 1.2328 | 1.4839 | 1.4024 | 1.0352 | 0.90751 | 0.80099 | 0.76663 | 0.71498
43602.4526 | 1.2305 | 1.483 | 1.4019 | 1.0348 | 0.90711 | 0.80127 | 0.76539 | 0.71505
43602.4526 | 1.2306 | 1.4808 | 1.3994 | 1.0331 | 0.90609 | 0.80019 | 0.76476 | 0.71459
43602.4526 | 1.2224 | 1.4792 | 1.3988 | 1.0328 | 0.90537 | 0.79953 | 0.76746 | 0.71433
43602.4526 | 1.2281 | 1.4791 | 1.3988 | 1.0329 | 0.90464 | 0.79941 | 0.76749 | 0.71448
43602.4526 | 1.2299 | 1.4795 | 1.3983 | 1.032 | 0.90465 | 0.79914 | 0.76555 | 0.71452
43602.4526 | 1.2255 | 1.4794 | 1.3991 | 1.0325 | 0.90506 | 0.79907 | 0.76555 | 0.71431
43602.4526 | 1.2311 | 1.4797 | 1.3979 | 1.0322 | 0.90473 | 0.79909 | 0.76496 | 0.71418
43602.4526 | 1.2307 | 1.4798 | 1.398 | 1.0324 | 0.90501 | 0.79916 | 0.76452 | 0.71428
43602.4526 | 1.2314 | 1.4809 | 1.3993 | 1.0337 | 0.90465 | 0.79877 | 0.76407 | 0.71427
43602.4527 | 1.2285 | 1.4798 | 1.3985 | 1.0328 | 0.90538 | 0.79939 | 0.76496 | 0.71421
43602.4527 | 1.2361 | 1.4811 | 1.3989 | 1.0339 | 0.90483 | 0.79919 | 0.76782 | 0.71439
43602.4527 | 1.2311 | 1.4806 | 1.399 | 1.0322 | 0.90494 | 0.79959 | 0.76494 | 0.71429
43602.4527 | 1.2308 | 1.4832 | 1.4009 | 1.0352 | 0.90606 | 0.80015 | 0.76495 | 0.71481
43602.4527 | 1.2356 | 1.4812 | 1.3999 | 1.0348 | 0.90646 | 0.80039 | 0.7654 | 0.715
43602.4527 | 1.2279 | 1.4814 | 1.4002 | 1.0335 | 0.90597 | 0.79998 | 0.76471 | 0.71491
43602.4527 | 1.2312 | 1.4825 | 1.4008 | 1.0346 | 0.90616 | 0.80068 | 0.7658 | 0.71521
43602.4527 | 1.2366 | 1.4831 | 1.4011 | 1.0359 | 0.90648 | 0.80081 | 0.76859 | 0.71472
43602.4527 | 1.2339 | 1.4822 | 1.4006 | 1.0344 | 0.90671 | 0.80052 | 0.76665 | 0.71483
43602.4528 | 1.2284 | 1.4827 | 1.4015 | 1.0348 | 0.90633 | 0.80091 | 0.76564 | 0.71497
43602.4528 | 1.2362 | 1.4844 | 1.4022 | 1.036 | 0.907 | 0.80088 | 0.76587 | 0.71493
43602.4528 | 1.2341 | 1.483 | 1.401 | 1.0349 | 0.90686 | 0.80075 | 0.7656 | 0.71495
43602.4528 | 1.2364 | 1.4836 | 1.402 | 1.0357 | 0.90671 | 0.80101 | 0.76544 | 0.71501
43602.4528 | 1.2347 | 1.484 | 1.4023 | 1.0352 | 0.9075 | 0.80152 | 0.76639 | 0.71549
43602.4525 | 1.2402 | 1.4858 | 1.404 | 1.0371 | 0.90747 | 0.80124 | 0.76773 | 0.715
43602.4529 | 1.2513 | 1.4972 | 1.4146 | 1.0443 | 0.91445 | 0.80696 | 0.77125 | 0.71725
43602.4529 | 1.246 | 1.4985 | 1.416 | 1.0452 | 0.91585 | 0.80808 | 0.77466 | 0.71777
43602.4529 | 1.2521 | 1.5006 | 1.4173 | 1.0466 | 0.91567 | 0.80802 | 0.77371 | 0.71748
43602.4529 | 1.2544 | 1.5025 | 1.4185 | 1.0477 | 0.91748 | 0.80894 | 0.77261 | 0.71764
43602.453 | 1.2536 | 1.5032 | 1.4196 | 1.0488 | 0.91842 | 0.80978 | 0.77372 | 0.7185
43602.453 | 1.2521 | 1.5055 | 1.4218 | 1.0501 | 0.91877 | 0.81076 | 0.77372 | 0.71864
43602.453 | 1.2514 | 1.5065 | 1.4221 | 1.0506 | 0.91978 | 0.8111 | 0.77513 | 0.71856
43602.453 | 1.2493 | 1.5082 | 1.425 | 1.0525 | 0.92095 | 0.81212 | 0.77872 | 0.71907
43602.453 | 1.2609 | 1.5095 | 1.4253 | 1.0527 | 0.92151 | 0.81261 | 0.77672 | 0.71931
43602.453 | 1.257 | 1.5091 | 1.4247 | 1.0513 | 0.92157 | 0.81276 | 0.77648 | 0.71942
43602.453 | 1.2572 | 1.51 | 1.4257 | 1.0526 | 0.92202 | 0.81304 | 0.77627 | 0.71951
43602.453 | 1.2543 | 1.5106 | 1.4267 | 1.0529 | 0.92194 | 0.81297 | 0.77599 | 0.71969
43602.4531 | 1.2585 | 1.5117 | 1.4272 | 1.0535 | 0.92322 | 0.81385 | 0.77739 | 0.7199
43602.4531 | 1.2528 | 1.5115 | 1.428 | 1.0536 | 0.92224 | 0.81337 | 0.77643 | 0.71964
43602.4531 | 1.2562 | 1.5119 | 1.4279 | 1.0534 | 0.9236 | 0.8143 | 0.77657 | 0.72001
43602.4531 | 1.2597 | 1.5129 | 1.4284 | 1.054 | 0.92274 | 0.81359 | 0.77857 | 0.71952
43602.4531 | 1.2604 | 1.5156 | 1.4303 | 1.055 | 0.92415 | 0.8144 | 0.77961 | 0.7202
43602.4531 | 1.2539 | 1.5147 | 1.4302 | 1.0547 | 0.92492 | 0.81538 | 0.77955 | 0.72062
43602.4531 | 1.2545 | 1.5129 | 1.4288 | 1.0533 | 0.92312 | 0.81439 | 0.77841 | 0.7201
43602.4531 | 1.2594 | 1.5135 | 1.4303 | 1.0539 | 0.92348 | 0.81422 | 0.77785 | 0.7198
43602.4531 | 1.2546 | 1.5144 | 1.43 | 1.0537 | 0.92346 | 0.81456 | 0.7779 | 0.71989
43602.4532 | 1.2583 | 1.5136 | 1.4301 | 1.0533 | 0.92353 | 0.81438 | 0.78006 | 0.72003
43602.4532 | 1.2564 | 1.5134 | 1.4294 | 1.053 | 0.92333 | 0.8141 | 0.7786 | 0.72003
43602.4529 | 1.2512 | 1.5124 | 1.4284 | 1.052 | 0.92248 | 0.81388 | 0.77682 | 0.72001
43602.4533 | 1.2482 | 1.5078 | 1.4247 | 1.0481 | 0.92054 | 0.81255 | 0.77558 | 0.71964
43602.4533 | 1.2392 | 1.5062 | 1.4244 | 1.0474 | 0.91937 | 0.81133 | 0.7786 | 0.719
43602.4533 | 1.2411 | 1.5064 | 1.4226 | 1.0462 | 0.91858 | 0.81039 | 0.77598 | 0.71877
43602.4533 | 1.2399 | 1.5044 | 1.4226 | 1.0454 | 0.91795 | 0.80985 | 0.77409 | 0.71831
43602.4533 | 1.2415 | 1.5032 | 1.4215 | 1.0451 | 0.9174 | 0.80965 | 0.77359 | 0.71842
43602.4533 | 1.2422 | 1.5036 | 1.4213 | 1.0453 | 0.91704 | 0.8092 | 0.77333 | 0.71838
43602.4533 | 1.2348 | 1.4998 | 1.4187 | 1.042 | 0.91645 | 0.80897 | 0.77317 | 0.71812
43602.4534 | 1.234 | 1.4978 | 1.4175 | 1.0414 | 0.91446 | 0.80734 | 0.77201 | 0.71752
43602.4534 | 1.233 | 1.4978 | 1.4178 | 1.0409 | 0.91418 | 0.80679 | 0.77434 | 0.71751
43602.4534 | 1.2334 | 1.4968 | 1.4165 | 1.0399 | 0.9137 | 0.8065 | 0.77304 | 0.7175
43602.4534 | 1.2254 | 1.495 | 1.4151 | 1.0391 | 0.91283 | 0.806 | 0.77068 | 0.71725
43602.4534 | 1.2303 | 1.4927 | 1.4133 | 1.0376 | 0.91185 | 0.80555 | 0.76959 | 0.71722
43602.4534 | 1.2319 | 1.4921 | 1.4115 | 1.0371 | 0.91088 | 0.80457 | 0.76951 | 0.71665
43602.4534 | 1.2265 | 1.4913 | 1.4121 | 1.0375 | 0.91097 | 0.80473 | 0.77023 | 0.71708
43602.4534 | 1.2227 | 1.4899 | 1.4107 | 1.0359 | 0.91044 | 0.80475 | 0.76916 | 0.71707
43602.4534 | 1.2256 | 1.4905 | 1.4114 | 1.0363 | 0.90982 | 0.80382 | 0.76796 | 0.71644
43602.4535 | 1.2298 | 1.4897 | 1.41 | 1.0351 | 0.90967 | 0.80362 | 0.76822 | 0.71639
43602.4535 | 1.2279 | 1.488 | 1.4086 | 1.0345 | 0.90925 | 0.80319 | 0.77033 | 0.71644
43602.4535 | 1.2257 | 1.4877 | 1.4081 | 1.0337 | 0.90829 | 0.8024 | 0.76714 | 0.71586
43602.4535 | 1.227 | 1.4892 | 1.4094 | 1.0349 | 0.90828 | 0.80244 | 0.76794 | 0.71613
43602.4535 | 1.2284 | 1.4882 | 1.4091 | 1.0347 | 0.90878 | 0.80306 | 0.76816 | 0.71631
43602.4535 | 1.2286 | 1.488 | 1.409 | 1.0347 | 0.90848 | 0.80259 | 0.76695 | 0.71626
43602.4533 | 1.2249 | 1.4867 | 1.4094 | 1.0348 | 0.90886 | 0.8028 | 0.76809 | 0.71622
43602.4536 | 1.2304 | 1.488 | 1.4096 | 1.0352 | 0.90898 | 0.80295 | 0.77053 | 0.71593
43602.4536 | 1.224 | 1.4882 | 1.4089 | 1.0352 | 0.90948 | 0.80317 | 0.76831 | 0.71595
43602.4536 | 1.2321 | 1.4889 | 1.4093 | 1.035 | 0.90932 | 0.80301 | 0.76771 | 0.71597
43602.4537 | 1.2293 | 1.4876 | 1.4086 | 1.0345 | 0.90921 | 0.80272 | 0.76704 | 0.71606
43602.4537 | 1.2274 | 1.4874 | 1.4085 | 1.0348 | 0.90919 | 0.80284 | 0.76815 | 0.71618
43602.4537 | 1.2291 | 1.487 | 1.4078 | 1.0349 | 0.90983 | 0.80324 | 0.76845 | 0.7161
43602.4537 | 1.2225 | 1.4871 | 1.4083 | 1.0348 | 0.90895 | 0.80287 | 0.77013 | 0.71614
43602.4537 | 1.2235 | 1.4856 | 1.4073 | 1.0341 | 0.90832 | 0.80285 | 0.77063 | 0.7159
43602.4537 | 1.2328 | 1.4858 | 1.407 | 1.0337 | 0.90829 | 0.80214 | 0.76721 | 0.71573
43602.4537 | 1.2323 | 1.489 | 1.4089 | 1.0359 | 0.90862 | 0.80239 | 0.76757 | 0.71563
43602.4537 | 1.2349 | 1.4901 | 1.4092 | 1.0368 | 0.90984 | 0.80378 | 0.76853 | 0.71612
43602.4537 | 1.2346 | 1.4908 | 1.4103 | 1.0365 | 0.90997 | 0.80373 | 0.76852 | 0.71604
43602.4538 | 1.2392 | 1.4927 | 1.4123 | 1.0386 | 0.911 | 0.8043 | 0.76889 | 0.71633
43602.4538 | 1.2397 | 1.4952 | 1.415 | 1.0403 | 0.91301 | 0.80593 | 0.77035 | 0.71688
43602.4538 | 1.2399 | 1.4969 | 1.4163 | 1.0422 | 0.91426 | 0.80656 | 0.77136 | 0.71714
43602.4538 | 1.2446 | 1.4984 | 1.4161 | 1.0416 | 0.91433 | 0.80689 | 0.77439 | 0.71717
43602.4538 | 1.2449 | 1.5009 | 1.4191 | 1.0437 | 0.91534 | 0.80787 | 0.77288 | 0.71736
43602.4538 | 1.249 | 1.5044 | 1.4217 | 1.0464 | 0.91729 | 0.80897 | 0.77309 | 0.71767
43602.4538 | 1.2496 | 1.5061 | 1.4226 | 1.0474 | 0.91908 | 0.81055 | 0.77418 | 0.71855
43602.4538 | 1.2517 | 1.5095 | 1.4257 | 1.0483 | 0.9197 | 0.81118 | 0.77441 | 0.71863
43602.4539 | 1.2551 | 1.5123 | 1.4283 | 1.0521 | 0.92224 | 0.81246 | 0.77592 | 0.71932
43602.4539 | 1.2517 | 1.5139 | 1.4304 | 1.0527 | 0.92365 | 0.81438 | 0.77763 | 0.72015
43602.4539 | 1.2608 | 1.5161 | 1.4321 | 1.0542 | 0.92487 | 0.81514 | 0.77716 | 0.72045
43602.4536 | 1.2671 | 1.5201 | 1.4357 | 1.0569 | 0.92668 | 0.81708 | 0.77982 | 0.7211
43602.454 | 1.2735 | 1.5308 | 1.4441 | 1.064 | 0.93357 | 0.82263 | 0.78467 | 0.72344
43602.454 | 1.2728 | 1.5316 | 1.445 | 1.0644 | 0.93354 | 0.82245 | 0.78506 | 0.72346
43602.454 | 1.2765 | 1.5313 | 1.4452 | 1.065 | 0.93439 | 0.82286 | 0.78689 | 0.72383
43602.454 | 1.2717 | 1.5317 | 1.4451 | 1.0646 | 0.93454 | 0.82336 | 0.78644 | 0.72445
43602.454 | 1.2703 | 1.5309 | 1.4446 | 1.0641 | 0.93393 | 0.82318 | 0.78577 | 0.72438
43602.454 | 1.2727 | 1.531 | 1.4449 | 1.0638 | 0.93376 | 0.82305 | 0.7852 | 0.72432
43602.4541 | 1.2707 | 1.5311 | 1.4446 | 1.0646 | 0.93349 | 0.82287 | 0.78531 | 0.72436
43602.4541 | 1.2714 | 1.5322 | 1.4453 | 1.065 | 0.93485 | 0.82366 | 0.78697 | 0.72466
43602.4541 | 1.2693 | 1.531 | 1.4448 | 1.0639 | 0.93363 | 0.82302 | 0.78728 | 0.72442
43602.4541 | 1.2666 | 1.5305 | 1.4446 | 1.0646 | 0.93412 | 0.82307 | 0.78594 | 0.72427
43602.4541 | 1.2605 | 1.5278 | 1.4426 | 1.0615 | 0.93252 | 0.82256 | 0.78547 | 0.72404
43602.4541 | 1.2633 | 1.527 | 1.442 | 1.0613 | 0.93135 | 0.8218 | 0.7848 | 0.72432
43602.4541 | 1.2655 | 1.5284 | 1.4424 | 1.0619 | 0.93166 | 0.82161 | 0.78405 | 0.72425
43602.4541 | 1.2669 | 1.5259 | 1.4409 | 1.0603 | 0.93156 | 0.82201 | 0.78504 | 0.72419
43602.4541 | 1.2605 | 1.5265 | 1.4413 | 1.0604 | 0.93135 | 0.82113 | 0.78375 | 0.72422
43602.4542 | 1.2572 | 1.5246 | 1.4398 | 1.0587 | 0.93044 | 0.82065 | 0.78452 | 0.72407
43602.4542 | 1.2635 | 1.5249 | 1.4403 | 1.0596 | 0.93068 | 0.82127 | 0.78618 | 0.72442
43602.4542 | 1.2585 | 1.5229 | 1.4389 | 1.0582 | 0.93013 | 0.82111 | 0.78473 | 0.72413
43602.4542 | 1.2526 | 1.5209 | 1.4383 | 1.0572 | 0.92907 | 0.81996 | 0.78346 | 0.7237
43602.4542 | 1.2546 | 1.5193 | 1.437 | 1.0564 | 0.92824 | 0.81972 | 0.78245 | 0.72359
43602.4542 | 1.2571 | 1.5195 | 1.4369 | 1.056 | 0.92844 | 0.81917 | 0.78395 | 0.72369
43602.4542 | 1.2623 | 1.5211 | 1.4373 | 1.0564 | 0.92822 | 0.81889 | 0.78512 | 0.72342
43602.454 | 1.2575 | 1.5198 | 1.4362 | 1.0559 | 0.92766 | 0.81843 | 0.78216 | 0.72344
43602.4543 | 1.2544 | 1.5181 | 1.4357 | 1.0542 | 0.92688 | 0.81789 | 0.78188 | 0.72289
43602.4544 | 1.2579 | 1.5209 | 1.4369 | 1.0554 | 0.92732 | 0.81819 | 0.78233 | 0.72312
43602.4544 | 1.2573 | 1.5208 | 1.4375 | 1.0565 | 0.92813 | 0.81862 | 0.78561 | 0.72315
43602.4544 | 1.2558 | 1.5221 | 1.4383 | 1.0564 | 0.92792 | 0.81894 | 0.78302 | 0.72308
43602.4544 | 1.2584 | 1.5229 | 1.4387 | 1.0569 | 0.92856 | 0.81923 | 0.78236 | 0.7234
43602.4544 | 1.2555 | 1.5215 | 1.4389 | 1.057 | 0.92939 | 0.81964 | 0.78265 | 0.72386
43602.4544 | 1.2579 | 1.5221 | 1.4389 | 1.0571 | 0.92866 | 0.81938 | 0.78229 | 0.72336
43602.4544 | 1.2574 | 1.5227 | 1.4401 | 1.058 | 0.92897 | 0.81948 | 0.78264 | 0.72333
43602.4544 | 1.256 | 1.5223 | 1.4391 | 1.0571 | 0.92876 | 0.81961 | 0.78258 | 0.72311
43602.4544 | 1.2607 | 1.5228 | 1.4393 | 1.0566 | 0.92929 | 0.81983 | 0.78195 | 0.72345
43602.4545 | 1.2612 | 1.5236 | 1.4407 | 1.0581 | 0.92907 | 0.81972 | 0.78257 | 0.72317
43602.4545 | 1.2647 | 1.5247 | 1.4409 | 1.0585 | 0.92983 | 0.82036 | 0.78349 | 0.72334
43602.4545 | 1.2599 | 1.5239 | 1.4419 | 1.0586 | 0.93025 | 0.82081 | 0.78413 | 0.72368
43602.4545 | 1.2686 | 1.5264 | 1.443 | 1.0602 | 0.93182 | 0.82151 | 0.78808 | 0.724
43602.4545 | 1.2611 | 1.5267 | 1.4434 | 1.0594 | 0.93109 | 0.82132 | 0.78528 | 0.72374
43602.4545 | 1.2563 | 1.5282 | 1.4453 | 1.0611 | 0.93203 | 0.82227 | 0.78524 | 0.72436
43602.4545 | 1.2644 | 1.5279 | 1.4444 | 1.0619 | 0.93216 | 0.82212 | 0.78495 | 0.72428
43602.4545 | 1.2646 | 1.5297 | 1.4462 | 1.0623 | 0.93344 | 0.82287 | 0.78567 | 0.72422
43602.4545 | 1.271 | 1.5314 | 1.4466 | 1.063 | 0.93346 | 0.82315 | 0.78596 | 0.72423
43602.4546 | 1.2673 | 1.5319 | 1.4474 | 1.0637 | 0.93454 | 0.82366 | 0.78998 | 0.72432
43602.4543 | 1.2671 | 1.5324 | 1.4482 | 1.0637 | 0.93456 | 0.82439 | 0.78739 | 0.72498
43602.4547 | 1.273 | 1.5426 | 1.4559 | 1.0715 | 0.94142 | 0.82857 | 0.79056 | 0.72637
43602.4547 | 1.2801 | 1.5432 | 1.4568 | 1.0721 | 0.94085 | 0.82932 | 0.79137 | 0.72649
43602.4547 | 1.2805 | 1.5435 | 1.4568 | 1.072 | 0.94125 | 0.82965 | 0.79078 | 0.7272
43602.4547 | 1.2766 | 1.5445 | 1.4573 | 1.0721 | 0.9413 | 0.82968 | 0.79171 | 0.7272
43602.4547 | 1.279 | 1.545 | 1.4579 | 1.0728 | 0.94224 | 0.8303 | 0.795 | 0.72744
43602.4547 | 1.2892 | 1.5466 | 1.4579 | 1.0739 | 0.94194 | 0.83039 | 0.7929 | 0.7275
43602.4547 | 1.282 | 1.5459 | 1.4571 | 1.0728 | 0.94241 | 0.83066 | 0.7927 | 0.72755
43602.4547 | 1.2851 | 1.5423 | 1.4529 | 1.0724 | 0.94227 | 0.83062 | 0.79233 | 0.72872
43602.4549 | 1.2822 | 1.5345 | 1.4478 | 1.07 | 0.93822 | 0.82784 | 0.78999 | 0.72792
43602.455 | 1.2786 | 1.5335 | 1.4471 | 1.0692 | 0.93935 | 0.82829 | 0.79149 | 0.72854
43602.455 | 1.2775 | 1.5321 | 1.4449 | 1.0665 | 0.93701 | 0.8268 | 0.79226 | 0.72781
43602.455 | 1.2747 | 1.5322 | 1.4448 | 1.0665 | 0.93658 | 0.82675 | 0.78978 | 0.72764
43602.455 | 1.2768 | 1.5314 | 1.4433 | 1.0658 | 0.93597 | 0.8259 | 0.78847 | 0.72751
43602.455 | 1.2783 | 1.5314 | 1.4432 | 1.0662 | 0.93607 | 0.82585 | 0.78771 | 0.72749
43602.455 | 1.2771 | 1.5304 | 1.4421 | 1.0651 | 0.93559 | 0.82521 | 0.78763 | 0.72677
43602.455 | 1.2706 | 1.5298 | 1.4427 | 1.066 | 0.93567 | 0.82546 | 0.79092 | 0.72732
43602.455 | 1.2736 | 1.5293 | 1.4408 | 1.0647 | 0.93518 | 0.82572 | 0.78951 | 0.72757
43602.455 | 1.2756 | 1.5286 | 1.44 | 1.0641 | 0.93445 | 0.82475 | 0.78792 | 0.72746
43602.4551 | 1.2741 | 1.5312 | 1.4407 | 1.0657 | 0.93484 | 0.825 | 0.78747 | 0.72754
43602.4551 | 1.2754 | 1.5284 | 1.4399 | 1.0647 | 0.93431 | 0.82446 | 0.78653 | 0.7272
43602.4551 | 1.2777 | 1.5285 | 1.4391 | 1.0642 | 0.93479 | 0.82435 | 0.78755 | 0.72719
43602.4551 | 1.2688 | 1.5268 | 1.4384 | 1.0631 | 0.93323 | 0.82363 | 0.78651 | 0.72667
43602.4551 | 1.2733 | 1.5263 | 1.4383 | 1.0645 | 0.93361 | 0.82398 | 0.78648 | 0.72692
43602.4551 | 1.282 | 1.5278 | 1.438 | 1.0645 | 0.93402 | 0.82374 | 0.78982 | 0.72688
43602.4551 | 1.2751 | 1.5254 | 1.4377 | 1.0642 | 0.93334 | 0.82403 | 0.78805 | 0.72706
43602.4549 | 1.274 | 1.5251 | 1.4369 | 1.0638 | 0.93354 | 0.82399 | 0.78761 | 0.72705
43602.4552 | 1.2788 | 1.5193 | 1.4302 | 1.061 | 0.93099 | 0.82242 | 0.78632 | 0.72734
43602.4552 | 1.2764 | 1.5179 | 1.4289 | 1.061 | 0.93066 | 0.82182 | 0.78522 | 0.72703
43602.4553 | 1.2705 | 1.5179 | 1.4285 | 1.0603 | 0.93023 | 0.82164 | 0.78631 | 0.72692
43602.4553 | 1.2771 | 1.5172 | 1.4276 | 1.0604 | 0.92983 | 0.82128 | 0.78793 | 0.72677
43602.4553 | 1.2679 | 1.5141 | 1.4251 | 1.0584 | 0.92923 | 0.82095 | 0.78544 | 0.72676
43602.4553 | 1.268 | 1.5127 | 1.4245 | 1.058 | 0.92866 | 0.82054 | 0.78417 | 0.72682
43602.4553 | 1.2733 | 1.513 | 1.424 | 1.0586 | 0.92858 | 0.82028 | 0.78334 | 0.72658
43602.4553 | 1.2712 | 1.5115 | 1.4224 | 1.0577 | 0.92749 | 0.81963 | 0.78294 | 0.72621
43602.4553 | 1.2701 | 1.5106 | 1.4219 | 1.0568 | 0.92749 | 0.81958 | 0.78351 | 0.72649
43602.4553 | 1.2721 | 1.5118 | 1.4221 | 1.0573 | 0.92729 | 0.819 | 0.78292 | 0.72593
43602.4553 | 1.2705 | 1.5105 | 1.4215 | 1.0567 | 0.92684 | 0.81866 | 0.78223 | 0.72585
43602.4554 | 1.2687 | 1.5109 | 1.4215 | 1.0576 | 0.92677 | 0.81879 | 0.78549 | 0.72613
43602.4554 | 1.2716 | 1.5109 | 1.4211 | 1.0574 | 0.92686 | 0.81908 | 0.78509 | 0.72628
43602.4554 | 1.2758 | 1.5119 | 1.4218 | 1.0597 | 0.92791 | 0.81949 | 0.78387 | 0.72664
43602.4554 | 1.2737 | 1.5109 | 1.4206 | 1.0581 | 0.92845 | 0.82054 | 0.7845 | 0.72763
43602.4554 | 1.2765 | 1.512 | 1.4206 | 1.0593 | 0.92882 | 0.82028 | 0.78414 | 0.72703
43602.4554 | 1.2759 | 1.5128 | 1.4215 | 1.0594 | 0.92743 | 0.8191 | 0.78362 | 0.72641
43602.4554 | 1.2747 | 1.5113 | 1.4202 | 1.0585 | 0.9283 | 0.81957 | 0.78358 | 0.72681
43602.4554 | 1.2718 | 1.5123 | 1.4218 | 1.06 | 0.92885 | 0.82066 | 0.78425 | 0.72715
43602.4554 | 1.2794 | 1.5124 | 1.4215 | 1.061 | 0.92892 | 0.82021 | 0.78377 | 0.72692
43602.4552 | 1.2791 | 1.5132 | 1.4218 | 1.0611 | 0.92841 | 0.82068 | 0.78605 | 0.72754
43602.4556 | 1.2834 | 1.5133 | 1.4212 | 1.0632 | 0.93016 | 0.82188 | 0.78585 | 0.72817
43602.4556 | 1.2776 | 1.5115 | 1.4196 | 1.0617 | 0.93042 | 0.82215 | 0.78953 | 0.72847
43602.4556 | 1.276 | 1.5104 | 1.4195 | 1.0615 | 0.92953 | 0.82134 | 0.7858 | 0.72837
43602.4556 | 1.2725 | 1.5079 | 1.4169 | 1.0597 | 0.92862 | 0.8208 | 0.78465 | 0.72805
43602.4556 | 1.2749 | 1.5086 | 1.4174 | 1.0593 | 0.92817 | 0.82094 | 0.78478 | 0.72801
43602.4556 | 1.2761 | 1.5088 | 1.4176 | 1.0607 | 0.92773 | 0.82049 | 0.78426 | 0.72821
43602.4556 | 1.2662 | 1.5063 | 1.4155 | 1.0598 | 0.92777 | 0.82061 | 0.78416 | 0.72785
43602.4556 | 1.271 | 1.5051 | 1.4139 | 1.058 | 0.92694 | 0.81979 | 0.78407 | 0.72811
43602.4557 | 1.2697 | 1.5025 | 1.4123 | 1.0566 | 0.92599 | 0.81895 | 0.78292 | 0.72768
43602.4557 | 1.2718 | 1.5011 | 1.4112 | 1.0559 | 0.92456 | 0.81784 | 0.78374 | 0.72716
43602.4557 | 1.2718 | 1.4995 | 1.4091 | 1.0541 | 0.92453 | 0.81783 | 0.78378 | 0.72748
43602.4557 | 1.2648 | 1.498 | 1.4085 | 1.0534 | 0.92276 | 0.81616 | 0.78088 | 0.72631
43602.4557 | 1.268 | 1.4972 | 1.4075 | 1.0524 | 0.92238 | 0.81592 | 0.78078 | 0.72615
43602.4557 | 1.2724 | 1.4964 | 1.4065 | 1.0528 | 0.92122 | 0.81524 | 0.78127 | 0.72651
43602.4557 | 1.2591 | 1.4932 | 1.404 | 1.0499 | 0.9218 | 0.81578 | 0.77989 | 0.72657
43602.4556 | 1.267 | 1.4925 | 1.4041 | 1.0508 | 0.91978 | 0.81386 | 0.77809 | 0.72578
43602.4558 | 1.2571 | 1.482 | 1.3938 | 1.0433 | 0.91472 | 0.80939 | 0.77485 | 0.72398
43602.4558 | 1.2623 | 1.4832 | 1.394 | 1.0445 | 0.91475 | 0.80908 | 0.77528 | 0.7237
43602.4559 | 1.2503 | 1.4824 | 1.3927 | 1.0444 | 0.9151 | 0.80951 | 0.77664 | 0.72426
43602.4559 | 1.258 | 1.4797 | 1.3908 | 1.0419 | 0.91242 | 0.80792 | 0.77301 | 0.7236
43602.4559 | 1.2584 | 1.4797 | 1.3906 | 1.0419 | 0.91279 | 0.80799 | 0.77368 | 0.72374
43602.4559 | 1.2592 | 1.4788 | 1.3908 | 1.0426 | 0.91254 | 0.80771 | 0.77503 | 0.72352
43602.4559 | 1.2557 | 1.4782 | 1.3889 | 1.0413 | 0.91215 | 0.80719 | 0.77362 | 0.7235
43602.4559 | 1.2519 | 1.4778 | 1.3881 | 1.0407 | 0.91149 | 0.80711 | 0.77299 | 0.72337
43602.4559 | 1.2442 | 1.4758 | 1.3864 | 1.0394 | 0.91033 | 0.80608 | 0.77155 | 0.72286
43602.4559 | 1.255 | 1.4753 | 1.3864 | 1.0397 | 0.9095 | 0.80565 | 0.77264 | 0.7226
43602.4559 | 1.244 | 1.4757 | 1.3867 | 1.0399 | 0.9105 | 0.80595 | 0.77364 | 0.72268
43602.456 | 1.2461 | 1.4721 | 1.3839 | 1.0381 | 0.90997 | 0.80571 | 0.77178 | 0.7223
43602.456 | 1.2486 | 1.4734 | 1.3843 | 1.0381 | 0.90825 | 0.80418 | 0.77052 | 0.72193
43602.456 | 1.2492 | 1.4721 | 1.3838 | 1.0389 | 0.90968 | 0.80482 | 0.77061 | 0.72171
43602.456 | 1.2475 | 1.4725 | 1.3831 | 1.0377 | 0.90893 | 0.80447 | 0.77105 | 0.72236
43602.456 | 1.2477 | 1.4725 | 1.3835 | 1.0382 | 0.90799 | 0.80398 | 0.77405 | 0.72164
43602.456 | 1.256 | 1.4733 | 1.3839 | 1.0392 | 0.90871 | 0.80436 | 0.77112 | 0.72203
43602.456 | 1.242 | 1.4718 | 1.3822 | 1.0377 | 0.90907 | 0.80502 | 0.77107 | 0.72271
43602.4558 | 1.253 | 1.4719 | 1.3819 | 1.0382 | 0.90859 | 0.80425 | 0.77015 | 0.72188
43602.4561 | 1.25 | 1.474 | 1.3825 | 1.0395 | 0.90946 | 0.80479 | 0.77072 | 0.72238
43602.4561 | 1.2559 | 1.4727 | 1.3812 | 1.0385 | 0.90844 | 0.80385 | 0.7707 | 0.72185
43602.4562 | 1.2554 | 1.4731 | 1.3817 | 1.04 | 0.90836 | 0.80388 | 0.76965 | 0.72202
43602.4562 | 1.259 | 1.4729 | 1.3809 | 1.0394 | 0.90879 | 0.80387 | 0.77253 | 0.72182
43602.4562 | 1.2387 | 1.4702 | 1.3786 | 1.0375 | 0.90864 | 0.80452 | 0.77095 | 0.72181
43602.4562 | 1.2535 | 1.4731 | 1.3808 | 1.0391 | 0.90777 | 0.80364 | 0.7701 | 0.72119
43602.4562 | 1.2484 | 1.4695 | 1.3788 | 1.0373 | 0.90744 | 0.80299 | 0.76933 | 0.72073
43602.4562 | 1.2555 | 1.4733 | 1.3807 | 1.0396 | 0.90746 | 0.80344 | 0.76927 | 0.72142
43602.4562 | 1.249 | 1.4731 | 1.3812 | 1.0395 | 0.90889 | 0.8044 | 0.76973 | 0.72181
43602.4562 | 1.2535 | 1.4728 | 1.3803 | 1.0394 | 0.90818 | 0.80375 | 0.76956 | 0.72163
43602.4562 | 1.2445 | 1.4748 | 1.3816 | 1.0404 | 0.90864 | 0.80404 | 0.76995 | 0.72119
43602.4563 | 1.2431 | 1.474 | 1.3818 | 1.0399 | 0.90967 | 0.80534 | 0.773 | 0.72233
43602.4563 | 1.2637 | 1.4721 | 1.3805 | 1.0398 | 0.90904 | 0.80484 | 0.77085 | 0.72168
43602.4563 | 1.2741 | 1.4833 | 1.3877 | 1.0465 | 0.91166 | 0.80629 | 0.77212 | 0.72171
43602.4563 | 1.2584 | 1.4812 | 1.3877 | 1.0453 | 0.91451 | 0.80855 | 0.77394 | 0.72299
43602.4563 | 1.2622 | 1.484 | 1.3898 | 1.0468 | 0.91476 | 0.8091 | 0.77379 | 0.72312
43602.4563 | 1.2588 | 1.48 | 1.3866 | 1.0442 | 0.9127 | 0.80771 | 0.77258 | 0.72293
43602.4563 | 1.2602 | 1.4846 | 1.3899 | 1.0471 | 0.91469 | 0.80893 | 0.77717 | 0.72277
43602.4563 | 1.2561 | 1.4843 | 1.3901 | 1.0469 | 0.915 | 0.80897 | 0.77606 | 0.72315
43602.4564 | 1.2571 | 1.4855 | 1.3918 | 1.0491 | 0.91598 | 0.81013 | 0.77606 | 0.72321
43602.4561 | 1.2616 | 1.4873 | 1.3932 | 1.0498 | 0.91823 | 0.81156 | 0.77606 | 0.7241
43602.4565 | 1.2682 | 1.4875 | 1.3946 | 1.0502 | 0.91757 | 0.81101 | 0.77852 | 0.72511
43602.4565 | 1.26 | 1.4859 | 1.3925 | 1.0487 | 0.91604 | 0.81017 | 0.77681 | 0.72425
43602.4565 | 1.2692 | 1.4867 | 1.3932 | 1.0495 | 0.91731 | 0.81062 | 0.77642 | 0.72431
43602.4565 | 1.2569 | 1.4878 | 1.3939 | 1.0496 | 0.91593 | 0.81013 | 0.77524 | 0.72423
43602.4565 | 1.2564 | 1.4849 | 1.3922 | 1.0474 | 0.91657 | 0.81081 | 0.77603 | 0.72452
43602.4565 | 1.2699 | 1.4846 | 1.3917 | 1.0475 | 0.91421 | 0.80893 | 0.7746 | 0.72356
43602.4565 | 1.2559 | 1.4832 | 1.3898 | 1.0454 | 0.91373 | 0.80813 | 0.77695 | 0.72348
43602.4565 | 1.2539 | 1.4832 | 1.3897 | 1.045 | 0.91314 | 0.80791 | 0.77389 | 0.72355
43602.4566 | 1.2426 | 1.4803 | 1.3882 | 1.0434 | 0.91327 | 0.80847 | 0.7739 | 0.72323
43602.4566 | 1.243 | 1.4779 | 1.387 | 1.0424 | 0.91232 | 0.80806 | 0.77349 | 0.72313
43602.4566 | 1.2643 | 1.4797 | 1.3878 | 1.0443 | 0.91151 | 0.8071 | 0.77299 | 0.7233
43602.4566 | 1.2535 | 1.4764 | 1.3851 | 1.0406 | 0.91154 | 0.8064 | 0.77154 | 0.72286
43602.4566 | 1.2506 | 1.4735 | 1.3828 | 1.0399 | 0.90911 | 0.80431 | 0.77021 | 0.72228
43602.4566 | 1.2466 | 1.4736 | 1.3831 | 1.0393 | 0.90858 | 0.8042 | 0.77 | 0.72214
43602.4566 | 1.2457 | 1.4717 | 1.3813 | 1.0374 | 0.9069 | 0.80372 | 0.77307 | 0.72208
43602.4566 | 1.2447 | 1.4686 | 1.3786 | 1.0351 | 0.90751 | 0.8031 | 0.77178 | 0.72237
43602.4567 | 1.2411 | 1.4664 | 1.3774 | 1.0332 | 0.90514 | 0.80154 | 0.76833 | 0.72139
43602.4567 | 1.2377 | 1.4642 | 1.3758 | 1.0325 | 0.90332 | 0.80017 | 0.76683 | 0.72085
43602.4565 | 1.2367 | 1.4639 | 1.3754 | 1.0322 | 0.90269 | 0.79909 | 0.76564 | 0.71993
43602.4568 | 1.228 | 1.4524 | 1.3658 | 1.0247 | 0.89659 | 0.79432 | 0.76372 | 0.7183
43602.4568 | 1.2382 | 1.453 | 1.3657 | 1.025 | 0.89612 | 0.79382 | 0.76205 | 0.71839
43602.4568 | 1.2288 | 1.4516 | 1.3649 | 1.0239 | 0.89589 | 0.79395 | 0.76186 | 0.7186
43602.4568 | 1.2272 | 1.4495 | 1.3635 | 1.0218 | 0.89497 | 0.79294 | 0.76096 | 0.71779
43602.4568 | 1.235 | 1.4508 | 1.3642 | 1.0239 | 0.89593 | 0.794 | 0.76147 | 0.71856
43602.4568 | 1.2253 | 1.4505 | 1.3638 | 1.0239 | 0.89604 | 0.79427 | 0.76271 | 0.71833
43602.4568 | 1.23 | 1.4502 | 1.3633 | 1.0233 | 0.89577 | 0.79387 | 0.76414 | 0.7187
43602.4569 | 1.2321 | 1.4475 | 1.3615 | 1.022 | 0.89543 | 0.79333 | 0.76113 | 0.71786
43602.4569 | 1.222 | 1.4471 | 1.3605 | 1.0212 | 0.89443 | 0.79269 | 0.76033 | 0.71837
43602.4569 | 1.2272 | 1.4481 | 1.3612 | 1.0228 | 0.89523 | 0.7932 | 0.76096 | 0.71825
43602.4569 | 1.2194 | 1.4448 | 1.3586 | 1.0198 | 0.89412 | 0.79275 | 0.76071 | 0.71776
43602.4569 | 1.2162 | 1.4456 | 1.3587 | 1.02 | 0.89338 | 0.79191 | 0.76144 | 0.71764
43602.4569 | 1.2318 | 1.4488 | 1.361 | 1.024 | 0.89432 | 0.79231 | 0.75975 | 0.71755
43602.4569 | 1.2215 | 1.4423 | 1.3565 | 1.0196 | 0.89533 | 0.79309 | 0.7601 | 0.71823
43602.4569 | 1.2256 | 1.4419 | 1.3555 | 1.0186 | 0.89192 | 0.79055 | 0.75953 | 0.71752
43602.4569 | 1.2196 | 1.4429 | 1.3553 | 1.019 | 0.89219 | 0.79064 | 0.76223 | 0.71719
43602.457 | 1.2234 | 1.441 | 1.3547 | 1.0184 | 0.89194 | 0.79094 | 0.75936 | 0.71751
43602.457 | 1.2191 | 1.4406 | 1.3543 | 1.0191 | 0.89194 | 0.79073 | 0.75912 | 0.7175
43602.4568 | 1.219 | 1.4403 | 1.3533 | 1.0179 | 0.89175 | 0.7905 | 0.75885 | 0.71705
43602.4571 | 1.2334 | 1.4512 | 1.3617 | 1.0263 | 0.89679 | 0.79408 | 0.76231 | 0.71799
43602.4571 | 1.2397 | 1.4516 | 1.3625 | 1.0269 | 0.89843 | 0.79574 | 0.76453 | 0.71935
43602.4571 | 1.2375 | 1.4548 | 1.3644 | 1.028 | 0.89839 | 0.79517 | 0.76291 | 0.71911
43602.4571 | 1.2383 | 1.4565 | 1.3663 | 1.0299 | 0.89986 | 0.79718 | 0.76382 | 0.71941
43602.4571 | 1.241 | 1.4567 | 1.366 | 1.0295 | 0.90072 | 0.79752 | 0.76539 | 0.72006
43602.4571 | 1.2367 | 1.4576 | 1.3671 | 1.0301 | 0.90117 | 0.798 | 0.76659 | 0.72
43602.4571 | 1.2416 | 1.4598 | 1.3687 | 1.0321 | 0.90162 | 0.798 | 0.76568 | 0.71989
43602.4572 | 1.2313 | 1.4596 | 1.3692 | 1.0319 | 0.90298 | 0.79974 | 0.76639 | 0.72057
43602.4572 | 1.234 | 1.4609 | 1.3701 | 1.0323 | 0.90348 | 0.80022 | 0.76641 | 0.72055
43602.4572 | 1.2348 | 1.4624 | 1.3719 | 1.034 | 0.90261 | 0.80028 | 0.76797 | 0.72061
43602.4572 | 1.2517 | 1.463 | 1.3725 | 1.0342 | 0.90481 | 0.80068 | 0.76876 | 0.72103
43602.4572 | 1.2368 | 1.459 | 1.3694 | 1.0315 | 0.90381 | 0.8003 | 0.76696 | 0.72088
43602.4572 | 1.235 | 1.4629 | 1.3724 | 1.0339 | 0.90362 | 0.80031 | 0.76679 | 0.72119
43602.4572 | 1.2477 | 1.4666 | 1.3743 | 1.0367 | 0.90566 | 0.80198 | 0.7681 | 0.72166
43602.4572 | 1.2485 | 1.4637 | 1.3728 | 1.0344 | 0.90558 | 0.80165 | 0.77009 | 0.722
43602.4572 | 1.2431 | 1.4631 | 1.3723 | 1.0346 | 0.90495 | 0.80075 | 0.76798 | 0.72186
43602.4573 | 1.2424 | 1.4606 | 1.3707 | 1.0323 | 0.90428 | 0.80033 | 0.76722 | 0.72159
43602.4573 | 1.2451 | 1.4604 | 1.3709 | 1.0325 | 0.90336 | 0.79921 | 0.76607 | 0.72149
43602.4571 | 1.2414 | 1.4601 | 1.3713 | 1.0321 | 0.90252 | 0.7992 | 0.76603 | 0.72178
43602.4574 | 1.2316 | 1.4482 | 1.3635 | 1.0235 | 0.89819 | 0.79611 | 0.76321 | 0.7207
43602.4574 | 1.225 | 1.4487 | 1.3639 | 1.0236 | 0.89659 | 0.79506 | 0.76288 | 0.72067
43602.4574 | 1.2244 | 1.447 | 1.3622 | 1.022 | 0.89675 | 0.79552 | 0.76277 | 0.7205
43602.4574 | 1.2177 | 1.4447 | 1.361 | 1.021 | 0.8945 | 0.79341 | 0.7644 | 0.71981
43602.4574 | 1.2193 | 1.4447 | 1.361 | 1.0215 | 0.89445 | 0.79378 | 0.76281 | 0.71969
43602.4574 | 1.219 | 1.4446 | 1.3602 | 1.0215 | 0.8941 | 0.79326 | 0.76201 | 0.72034
43602.4575 | 1.2161 | 1.4394 | 1.3562 | 1.0171 | 0.89202 | 0.79191 | 0.76016 | 0.71919
43602.4575 | 1.2148 | 1.4392 | 1.3571 | 1.0182 | 0.89149 | 0.79116 | 0.76003 | 0.7193
43602.4575 | 1.2155 | 1.4371 | 1.355 | 1.0159 | 0.89114 | 0.791 | 0.76045 | 0.71966
43602.4575 | 1.2125 | 1.4366 | 1.3543 | 1.0155 | 0.89008 | 0.79003 | 0.75901 | 0.71938
43602.4575 | 1.2115 | 1.4346 | 1.3523 | 1.0138 | 0.88879 | 0.78893 | 0.75726 | 0.71897
43602.4575 | 1.2094 | 1.4347 | 1.3528 | 1.0142 | 0.88829 | 0.78872 | 0.75755 | 0.71911
43602.4575 | 1.21 | 1.4334 | 1.3521 | 1.0134 | 0.889 | 0.78899 | 0.76145 | 0.71857
43602.4575 | 1.208 | 1.4316 | 1.3504 | 1.0124 | 0.88663 | 0.78746 | 0.75713 | 0.71814
43602.4575 | 1.2059 | 1.4311 | 1.35 | 1.0117 | 0.88743 | 0.78799 | 0.75718 | 0.71841
43602.4576 | 1.2087 | 1.4319 | 1.3504 | 1.0115 | 0.88654 | 0.78732 | 0.75634 | 0.71819
43602.4576 | 1.2065 | 1.4311 | 1.3499 | 1.0104 | 0.88665 | 0.78796 | 0.75662 | 0.71866
43602.4576 | 1.2098 | 1.4318 | 1.3504 | 1.0112 | 0.8856 | 0.78621 | 0.75545 | 0.71748
43602.4574 | 1.1987 | 1.4338 | 1.3522 | 1.0131 | 0.88726 | 0.78802 | 0.75706 | 0.71821
43602.4577 | 1.2112 | 1.4348 | 1.3537 | 1.0132 | 0.88816 | 0.78832 | 0.75701 | 0.7184
43602.4577 | 1.2128 | 1.4355 | 1.3538 | 1.0128 | 0.88914 | 0.78965 | 0.75857 | 0.71898
43602.4577 | 1.2091 | 1.4337 | 1.3525 | 1.0122 | 0.88739 | 0.78826 | 0.75647 | 0.71827
43602.4577 | 1.2116 | 1.434 | 1.3525 | 1.0129 | 0.88796 | 0.78831 | 0.75701 | 0.71833
43602.4577 | 1.205 | 1.4328 | 1.3519 | 1.011 | 0.88731 | 0.78784 | 0.75852 | 0.71845
43602.4578 | 1.2083 | 1.4341 | 1.3529 | 1.0127 | 0.88798 | 0.78876 | 0.75805 | 0.71878
43602.4578 | 1.2021 | 1.4323 | 1.351 | 1.0107 | 0.88746 | 0.78822 | 0.75706 | 0.7184
43602.4578 | 1.2063 | 1.4331 | 1.3516 | 1.0122 | 0.88652 | 0.78748 | 0.75674 | 0.71812
43602.4578 | 1.2038 | 1.4328 | 1.3519 | 1.0119 | 0.88752 | 0.7881 | 0.75667 | 0.71874
43602.4578 | 1.2067 | 1.4326 | 1.3516 | 1.0111 | 0.88706 | 0.7881 | 0.75803 | 0.71834
43602.4578 | 1.2083 | 1.4341 | 1.3532 | 1.0134 | 0.8876 | 0.78832 | 0.75997 | 0.71843
43602.4578 | 1.207 | 1.433 | 1.3521 | 1.0116 | 0.88772 | 0.78869 | 0.75752 | 0.71859
43602.4578 | 1.2091 | 1.4337 | 1.3531 | 1.0119 | 0.88691 | 0.78772 | 0.75639 | 0.7182
43602.4578 | 1.2082 | 1.4373 | 1.3556 | 1.0143 | 0.88969 | 0.78988 | 0.75829 | 0.71931
43602.4579 | 1.2089 | 1.436 | 1.3555 | 1.0135 | 0.88929 | 0.78979 | 0.75848 | 0.71935
43602.4579 | 1.2137 | 1.4388 | 1.3576 | 1.0153 | 0.88934 | 0.7899 | 0.75811 | 0.71885
43602.4579 | 1.2161 | 1.4396 | 1.3581 | 1.0161 | 0.89161 | 0.79095 | 0.76174 | 0.71937
43602.4577 | 1.2222 | 1.4466 | 1.365 | 1.0205 | 0.8937 | 0.79283 | 0.76082 | 0.71977
43602.458 | 1.2214 | 1.4505 | 1.3688 | 1.0222 | 0.89611 | 0.79496 | 0.76296 | 0.72092
43602.458 | 1.2213 | 1.4492 | 1.3676 | 1.0216 | 0.89719 | 0.79543 | 0.76294 | 0.72134
43602.458 | 1.2208 | 1.4496 | 1.3677 | 1.0214 | 0.89538 | 0.79448 | 0.76314 | 0.72079
43602.458 | 1.2203 | 1.4477 | 1.3665 | 1.0203 | 0.89627 | 0.79565 | 0.76566 | 0.72174
43602.458 | 1.2162 | 1.4466 | 1.3661 | 1.0196 | 0.89503 | 0.79514 | 0.76298 | 0.72143
43602.4581 | 1.2196 | 1.4472 | 1.3661 | 1.0203 | 0.89405 | 0.79415 | 0.76175 | 0.72083
43602.4581 | 1.2134 | 1.4438 | 1.3641 | 1.0178 | 0.89361 | 0.7939 | 0.76156 | 0.72088
43602.4581 | 1.2133 | 1.4438 | 1.3635 | 1.0174 | 0.89293 | 0.79296 | 0.7614 | 0.7207
43602.4581 | 1.2105 | 1.4424 | 1.363 | 1.0166 | 0.89217 | 0.79263 | 0.76089 | 0.72082
43602.4581 | 1.2094 | 1.4404 | 1.3607 | 1.0148 | 0.89141 | 0.79215 | 0.7636 | 0.72061
43602.4581 | 1.2096 | 1.4396 | 1.3604 | 1.0139 | 0.89021 | 0.79132 | 0.76182 | 0.72007
43602.4581 | 1.2015 | 1.4371 | 1.3586 | 1.0122 | 0.88933 | 0.79048 | 0.75957 | 0.72011
43602.4581 | 1.2038 | 1.4367 | 1.3579 | 1.0118 | 0.88844 | 0.78953 | 0.75835 | 0.71956
43602.4581 | 1.2021 | 1.4358 | 1.3572 | 1.011 | 0.88754 | 0.78882 | 0.75752 | 0.71897
43602.4582 | 1.2021 | 1.4351 | 1.3563 | 1.0096 | 0.88703 | 0.78948 | 0.75831 | 0.71961
43602.4582 | 1.197 | 1.4333 | 1.3548 | 1.0094 | 0.88638 | 0.78786 | 0.75666 | 0.71849
43602.4582 | 1.2012 | 1.4331 | 1.3548 | 1.0081 | 0.88465 | 0.78717 | 0.7566 | 0.71814
43602.4582 | 1.1932 | 1.432 | 1.3542 | 1.0074 | 0.88551 | 0.7878 | 0.75972 | 0.719
43602.458 | 1.195 | 1.4322 | 1.3542 | 1.0072 | 0.88452 | 0.78656 | 0.75581 | 0.71798
43602.4583 | 1.201 | 1.4375 | 1.3599 | 1.0104 | 0.88704 | 0.78812 | 0.75807 | 0.71815
43602.4583 | 1.1978 | 1.4387 | 1.3601 | 1.01 | 0.88629 | 0.78802 | 0.75699 | 0.71772
43602.4583 | 1.2021 | 1.4407 | 1.3627 | 1.0118 | 0.88809 | 0.78875 | 0.75745 | 0.71791
43602.4583 | 1.201 | 1.4419 | 1.3641 | 1.0122 | 0.88893 | 0.78978 | 0.7577 | 0.71857
43602.4584 | 1.2034 | 1.4439 | 1.3658 | 1.0139 | 0.88918 | 0.78991 | 0.75862 | 0.71851
43602.4584 | 1.2082 | 1.4452 | 1.3665 | 1.0145 | 0.89024 | 0.79078 | 0.76101 | 0.71871
43602.4584 | 1.2061 | 1.4476 | 1.3679 | 1.0151 | 0.89142 | 0.79156 | 0.75986 | 0.71883
43602.4584 | 1.2124 | 1.4495 | 1.3699 | 1.0167 | 0.89208 | 0.79172 | 0.7594 | 0.71859
43602.4584 | 1.2125 | 1.4496 | 1.3699 | 1.0162 | 0.89229 | 0.79233 | 0.75964 | 0.71925
43602.4584 | 1.2094 | 1.4499 | 1.3711 | 1.0164 | 0.89271 | 0.79248 | 0.762 | 0.71919
43602.4584 | 1.208 | 1.4496 | 1.3714 | 1.0174 | 0.89331 | 0.79333 | 0.76304 | 0.71923
43602.4584 | 1.2056 | 1.4506 | 1.3717 | 1.0171 | 0.89316 | 0.79314 | 0.76155 | 0.71964
43602.4584 | 1.2024 | 1.4496 | 1.372 | 1.0159 | 0.89275 | 0.79286 | 0.76082 | 0.71922
43602.4585 | 1.2071 | 1.4513 | 1.3719 | 1.0168 | 0.89302 | 0.79263 | 0.76082 | 0.71901
43602.4585 | 1.2073 | 1.451 | 1.3726 | 1.0175 | 0.89279 | 0.79262 | 0.76028 | 0.71892
43602.4583 | 1.2097 | 1.4518 | 1.3726 | 1.0175 | 0.8933 | 0.79275 | 0.76085 | 0.71926
43602.4586 | 1.201 | 1.4472 | 1.3697 | 1.014 | 0.89101 | 0.7911 | 0.76182 | 0.7187
43602.4586 | 1.2037 | 1.4477 | 1.3707 | 1.0144 | 0.89113 | 0.79158 | 0.76028 | 0.71884
43602.4586 | 1.2057 | 1.4487 | 1.3706 | 1.0144 | 0.89142 | 0.79123 | 0.75941 | 0.71824
43602.4586 | 1.196 | 1.4457 | 1.3701 | 1.0128 | 0.89099 | 0.79135 | 0.75973 | 0.7186
43602.4586 | 1.2044 | 1.4483 | 1.3713 | 1.0139 | 0.89092 | 0.79129 | 0.75973 | 0.71835
43602.4586 | 1.2037 | 1.4506 | 1.3728 | 1.0155 | 0.89189 | 0.79177 | 0.76253 | 0.71835
43602.4586 | 1.2049 | 1.451 | 1.373 | 1.0154 | 0.89248 | 0.79212 | 0.76108 | 0.71886
43602.4587 | 1.2078 | 1.4521 | 1.3739 | 1.0159 | 0.89256 | 0.79198 | 0.75962 | 0.71841
43602.4587 | 1.2025 | 1.4529 | 1.3748 | 1.0169 | 0.89319 | 0.79292 | 0.76025 | 0.71848
43602.4587 | 1.2065 | 1.4541 | 1.3754 | 1.0158 | 0.89403 | 0.79362 | 0.76028 | 0.719
43602.4587 | 1.2019 | 1.4523 | 1.3754 | 1.0156 | 0.89293 | 0.79336 | 0.76206 | 0.71859
43602.4587 | 1.2059 | 1.4548 | 1.3771 | 1.0175 | 0.89449 | 0.79436 | 0.76481 | 0.71965
43602.4587 | 1.2048 | 1.4538 | 1.3756 | 1.0162 | 0.89383 | 0.79354 | 0.76102 | 0.71864
43602.4587 | 1.2075 | 1.4542 | 1.3763 | 1.0162 | 0.89372 | 0.79346 | 0.76102 | 0.71901
43602.4587 | 1.2114 | 1.4553 | 1.3767 | 1.0176 | 0.89367 | 0.79375 | 0.76099 | 0.71874
43602.4587 | 1.201 | 1.4528 | 1.3755 | 1.0159 | 0.89394 | 0.7936 | 0.76157 | 0.71857
43602.4586 | 1.2033 | 1.4511 | 1.3742 | 1.0148 | 0.89347 | 0.79389 | 0.76142 | 0.71932
43602.4589 | 1.203 | 1.4525 | 1.3757 | 1.0158 | 0.89332 | 0.79312 | 0.76065 | 0.71827
43602.4589 | 1.1999 | 1.4531 | 1.3765 | 1.0155 | 0.89372 | 0.79307 | 0.76039 | 0.71828
43602.4589 | 1.2057 | 1.4536 | 1.3759 | 1.0156 | 0.89304 | 0.79288 | 0.76037 | 0.71833
43602.4589 | 1.2078 | 1.4545 | 1.3757 | 1.0161 | 0.89311 | 0.79287 | 0.76053 | 0.71825
43602.4589 | 1.2069 | 1.4543 | 1.3759 | 1.0159 | 0.89357 | 0.79305 | 0.76127 | 0.71809
43602.4589 | 1.2093 | 1.4547 | 1.3768 | 1.0168 | 0.89354 | 0.79351 | 0.76322 | 0.71841
43602.4589 | 1.2026 | 1.4544 | 1.3778 | 1.0167 | 0.89381 | 0.79364 | 0.76113 | 0.71858
43602.4589 | 1.2101 | 1.4564 | 1.3778 | 1.0173 | 0.89432 | 0.79379 | 0.76084 | 0.71828
43602.459 | 1.2085 | 1.4562 | 1.3784 | 1.0172 | 0.89454 | 0.79405 | 0.7612 | 0.71832
43602.459 | 1.2047 | 1.457 | 1.3786 | 1.0172 | 0.89458 | 0.79423 | 0.76283 | 0.71853
43602.459 | 1.2078 | 1.4565 | 1.3784 | 1.0168 | 0.89446 | 0.79406 | 0.76118 | 0.71813
43602.459 | 1.2056 | 1.456 | 1.3789 | 1.0177 | 0.89431 | 0.79338 | 0.76091 | 0.71765
43602.459 | 1.2091 | 1.4561 | 1.3788 | 1.0172 | 0.89453 | 0.79401 | 0.76403 | 0.71813
43602.459 | 1.2054 | 1.456 | 1.3788 | 1.0179 | 0.89465 | 0.79427 | 0.76194 | 0.71771
43602.459 | 1.212 | 1.4585 | 1.3801 | 1.0188 | 0.89493 | 0.79431 | 0.7616 | 0.71823
43602.4588 | 1.2032 | 1.4579 | 1.3804 | 1.0182 | 0.89602 | 0.79506 | 0.76228 | 0.71852
43602.4591 | 1.2191 | 1.4703 | 1.3915 | 1.0261 | 0.90155 | 0.79942 | 0.76916 | 0.7196
43602.4591 | 1.2319 | 1.475 | 1.3937 | 1.0295 | 0.90314 | 0.8 | 0.76651 | 0.71944
43602.4592 | 1.2247 | 1.4742 | 1.3932 | 1.0286 | 0.90448 | 0.80103 | 0.76747 | 0.7198
43602.4592 | 1.2293 | 1.4762 | 1.395 | 1.0295 | 0.9044 | 0.80124 | 0.76786 | 0.72004
43602.4592 | 1.2303 | 1.4788 | 1.3962 | 1.0308 | 0.90427 | 0.80143 | 0.76805 | 0.71959
43602.4592 | 1.231 | 1.4798 | 1.3975 | 1.0318 | 0.90649 | 0.80292 | 0.76855 | 0.72039
43602.4592 | 1.2339 | 1.4815 | 1.3989 | 1.0327 | 0.90693 | 0.80339 | 0.76924 | 0.72068
43602.4592 | 1.2305 | 1.4832 | 1.3995 | 1.0329 | 0.90821 | 0.80451 | 0.77172 | 0.72128
43602.4592 | 1.23 | 1.4842 | 1.4009 | 1.0336 | 0.90818 | 0.80455 | 0.77173 | 0.72158
43602.4592 | 1.2308 | 1.4848 | 1.4015 | 1.0344 | 0.90968 | 0.80566 | 0.77151 | 0.7221
43602.4592 | 1.2328 | 1.4847 | 1.4017 | 1.0347 | 0.90975 | 0.8058 | 0.77208 | 0.72203
43602.4593 | 1.2332 | 1.485 | 1.4023 | 1.0357 | 0.9105 | 0.80609 | 0.77214 | 0.72251
43602.4593 | 1.2361 | 1.4864 | 1.4031 | 1.0369 | 0.91144 | 0.80785 | 0.77394 | 0.7237
43602.4593 | 1.2431 | 1.4872 | 1.4038 | 1.0374 | 0.91249 | 0.80791 | 0.77392 | 0.72375
43602.4593 | 1.2339 | 1.4849 | 1.4024 | 1.036 | 0.91201 | 0.80743 | 0.77713 | 0.72332
43602.4591 | 1.2323 | 1.485 | 1.4028 | 1.0355 | 0.91131 | 0.80752 | 0.77455 | 0.72347
43602.4594 | 1.2294 | 1.4868 | 1.4039 | 1.0371 | 0.91173 | 0.80823 | 0.77417 | 0.72423
43602.4594 | 1.2397 | 1.488 | 1.4044 | 1.0379 | 0.91163 | 0.80797 | 0.77374 | 0.72412
43602.4594 | 1.237 | 1.4882 | 1.4055 | 1.039 | 0.91361 | 0.80965 | 0.77525 | 0.72494
43602.4594 | 1.2403 | 1.4887 | 1.4054 | 1.0387 | 0.91394 | 0.80984 | 0.77549 | 0.72511
43602.4594 | 1.2357 | 1.4869 | 1.4047 | 1.0378 | 0.91367 | 0.80967 | 0.77822 | 0.72494
43602.4595 | 1.2403 | 1.4871 | 1.4056 | 1.0392 | 0.91423 | 0.81034 | 0.77801 | 0.72611
43602.4595 | 1.2371 | 1.4867 | 1.4042 | 1.0371 | 0.91352 | 0.80962 | 0.77582 | 0.72541
43602.4595 | 1.2389 | 1.4869 | 1.4038 | 1.0378 | 0.91293 | 0.80925 | 0.77517 | 0.72484
43602.4595 | 1.2434 | 1.4879 | 1.405 | 1.0387 | 0.91379 | 0.81006 | 0.77589 | 0.72534
43602.4595 | 1.2354 | 1.4862 | 1.4047 | 1.0378 | 0.91443 | 0.81016 | 0.77597 | 0.72597
43602.4595 | 1.2352 | 1.4854 | 1.4035 | 1.0375 | 0.91329 | 0.80974 | 0.77663 | 0.72565
43602.4595 | 1.2359 | 1.4873 | 1.4056 | 1.0385 | 0.91336 | 0.81001 | 0.77765 | 0.72574
43602.4595 | 1.2347 | 1.4874 | 1.4053 | 1.0381 | 0.91495 | 0.8111 | 0.77732 | 0.72669
43602.4595 | 1.2349 | 1.4844 | 1.4032 | 1.0363 | 0.91387 | 0.81024 | 0.77575 | 0.72589
43602.4596 | 1.2368 | 1.4848 | 1.4029 | 1.0356 | 0.91301 | 0.8095 | 0.77536 | 0.72554
43602.4594 | 1.2373 | 1.4858 | 1.4042 | 1.0371 | 0.91319 | 0.81009 | 0.77693 | 0.7263
43602.4597 | 1.2349 | 1.4866 | 1.4057 | 1.039 | 0.91529 | 0.81129 | 0.77753 | 0.7273
43602.4597 | 1.2387 | 1.4865 | 1.4058 | 1.0394 | 0.91579 | 0.81164 | 0.77729 | 0.72733
43602.4597 | 1.243 | 1.488 | 1.4071 | 1.0398 | 0.91608 | 0.81198 | 0.77993 | 0.72762
43602.4597 | 1.2392 | 1.4873 | 1.4074 | 1.0404 | 0.91682 | 0.81312 | 0.77982 | 0.72797
43602.4597 | 1.233 | 1.4868 | 1.4065 | 1.0398 | 0.91622 | 0.81266 | 0.77888 | 0.72796
43602.4597 | 1.2416 | 1.4874 | 1.407 | 1.0396 | 0.91563 | 0.81246 | 0.77803 | 0.72775
43602.4597 | 1.2435 | 1.488 | 1.4069 | 1.0401 | 0.91627 | 0.81297 | 0.77864 | 0.72856
43602.4598 | 1.2426 | 1.4882 | 1.4071 | 1.0402 | 0.91654 | 0.81262 | 0.77951 | 0.72819
43602.4598 | 1.2453 | 1.4885 | 1.4073 | 1.0407 | 0.91679 | 0.81331 | 0.78157 | 0.7285
43602.4598 | 1.2411 | 1.4883 | 1.4079 | 1.0408 | 0.91723 | 0.81373 | 0.78012 | 0.72878
43602.4598 | 1.2413 | 1.4889 | 1.4077 | 1.0404 | 0.9166 | 0.81263 | 0.77845 | 0.72756
43602.4598 | 1.2352 | 1.4871 | 1.4063 | 1.0398 | 0.91689 | 0.81294 | 0.77851 | 0.72824
43602.4598 | 1.236 | 1.4877 | 1.4074 | 1.0405 | 0.9168 | 0.8132 | 0.77913 | 0.72833
43602.4598 | 1.2376 | 1.4862 | 1.4062 | 1.0388 | 0.9165 | 0.813 | 0.78232 | 0.72863
43602.4598 | 1.2412 | 1.4887 | 1.4078 | 1.0405 | 0.91603 | 0.81249 | 0.77962 | 0.72799
43602.4597 | 1.2421 | 1.4891 | 1.4077 | 1.0413 | 0.91731 | 0.81299 | 0.77905 | 0.72795
43602.46 | 1.242 | 1.4893 | 1.4091 | 1.0417 | 0.91778 | 0.81375 | 0.78152 | 0.72846
43602.46 | 1.2428 | 1.4899 | 1.4091 | 1.0403 | 0.9173 | 0.81311 | 0.78096 | 0.72803
43602.46 | 1.2434 | 1.4902 | 1.4101 | 1.0418 | 0.91817 | 0.81422 | 0.78059 | 0.72892
43602.46 | 1.2454 | 1.4904 | 1.41 | 1.0419 | 0.91882 | 0.81548 | 0.78006 | 0.72962
43602.46 | 1.239 | 1.4902 | 1.4098 | 1.0413 | 0.91896 | 0.81546 | 0.78081 | 0.72959
43602.46 | 1.2481 | 1.4904 | 1.4097 | 1.0426 | 0.91907 | 0.81512 | 0.78122 | 0.72917
43602.46 | 1.2422 | 1.4882 | 1.4086 | 1.0403 | 0.91766 | 0.81385 | 0.78052 | 0.72853
43602.46 | 1.2401 | 1.4905 | 1.4097 | 1.0415 | 0.91832 | 0.81423 | 0.7808 | 0.7289
43602.46 | 1.2344 | 1.49 | 1.4095 | 1.0414 | 0.91859 | 0.81484 | 0.78058 | 0.72921
43602.4601 | 1.2431 | 1.4889 | 1.4082 | 1.0408 | 0.9179 | 0.81378 | 0.77988 | 0.72841
43602.4601 | 1.2431 | 1.4893 | 1.4089 | 1.0411 | 0.91774 | 0.81383 | 0.77984 | 0.72861
43602.4601 | 1.2429 | 1.4888 | 1.4082 | 1.0407 | 0.91793 | 0.81406 | 0.78363 | 0.7287
43602.4601 | 1.2331 | 1.4867 | 1.4081 | 1.0407 | 0.91771 | 0.81427 | 0.78148 | 0.72879
43602.4601 | 1.2343 | 1.4868 | 1.4076 | 1.0403 | 0.91781 | 0.81447 | 0.78079 | 0.72925
43602.4601 | 1.2458 | 1.4888 | 1.408 | 1.041 | 0.91796 | 0.81405 | 0.78001 | 0.72922
43602.4599 | 1.234 | 1.4868 | 1.407 | 1.0392 | 0.91679 | 0.81367 | 0.77951 | 0.72871
43602.4602 | 1.2356 | 1.4852 | 1.4055 | 1.0389 | 0.91665 | 0.81348 | 0.77886 | 0.72899
43602.4602 | 1.2363 | 1.4852 | 1.4047 | 1.0379 | 0.91636 | 0.81286 | 0.77976 | 0.7286
43602.4603 | 1.2377 | 1.4844 | 1.404 | 1.0378 | 0.91558 | 0.81251 | 0.78226 | 0.7285
43602.4603 | 1.2394 | 1.4853 | 1.4043 | 1.0372 | 0.91572 | 0.8126 | 0.77959 | 0.72835
43602.4603 | 1.2371 | 1.482 | 1.4023 | 1.0358 | 0.91444 | 0.81163 | 0.7778 | 0.72763
43602.4603 | 1.2324 | 1.4815 | 1.4021 | 1.0356 | 0.91443 | 0.8115 | 0.77754 | 0.72774
43602.4603 | 1.2354 | 1.4814 | 1.4017 | 1.0357 | 0.91418 | 0.81113 | 0.7771 | 0.72768
43602.4603 | 1.234 | 1.4809 | 1.4018 | 1.0359 | 0.91424 | 0.811 | 0.77908 | 0.72767
43602.4603 | 1.2313 | 1.4796 | 1.4005 | 1.0355 | 0.91427 | 0.81116 | 0.77879 | 0.72802
43602.4603 | 1.2281 | 1.4777 | 1.3992 | 1.0345 | 0.91335 | 0.81144 | 0.77796 | 0.72864
43602.4603 | 1.2291 | 1.478 | 1.3989 | 1.0339 | 0.91246 | 0.81037 | 0.77656 | 0.72784
43602.4604 | 1.2317 | 1.4782 | 1.398 | 1.0336 | 0.91302 | 0.81039 | 0.77714 | 0.72776
43602.4604 | 1.2345 | 1.476 | 1.3969 | 1.0328 | 0.91205 | 0.80965 | 0.77594 | 0.7272
43602.4604 | 1.2305 | 1.4756 | 1.3961 | 1.0326 | 0.91139 | 0.80884 | 0.77671 | 0.72751
43602.4604 | 1.2345 | 1.4751 | 1.3952 | 1.0321 | 0.91207 | 0.80978 | 0.77989 | 0.72808
43602.4602 | 1.2337 | 1.4702 | 1.3899 | 1.0297 | 0.90898 | 0.80725 | 0.77433 | 0.72695
43602.4605 | 1.2347 | 1.4691 | 1.3881 | 1.0293 | 0.90846 | 0.80603 | 0.77353 | 0.72637
43602.4605 | 1.2347 | 1.4694 | 1.3884 | 1.0297 | 0.90914 | 0.80716 | 0.77385 | 0.72744
43602.4605 | 1.2391 | 1.4713 | 1.3905 | 1.0322 | 0.90884 | 0.80674 | 0.77483 | 0.72664
43602.4605 | 1.2397 | 1.4728 | 1.3915 | 1.0326 | 0.91128 | 0.80863 | 0.77879 | 0.72769
43602.4606 | 1.2373 | 1.4729 | 1.3908 | 1.0327 | 0.91058 | 0.80852 | 0.77625 | 0.72771
43602.4606 | 1.238 | 1.4741 | 1.3912 | 1.0334 | 0.91092 | 0.80866 | 0.77573 | 0.72747
43602.4606 | 1.2379 | 1.4749 | 1.392 | 1.0347 | 0.91174 | 0.80934 | 0.77618 | 0.72798
43602.4606 | 1.2386 | 1.4753 | 1.3925 | 1.0352 | 0.91246 | 0.80972 | 0.77627 | 0.72783
43602.4606 | 1.2454 | 1.4763 | 1.3932 | 1.0364 | 0.91251 | 0.81029 | 0.7768 | 0.72808
43602.4606 | 1.249 | 1.4776 | 1.394 | 1.0375 | 0.9136 | 0.81109 | 0.77955 | 0.72867
43602.4606 | 1.2507 | 1.4788 | 1.3948 | 1.0379 | 0.91458 | 0.81166 | 0.77946 | 0.72891
43602.4606 | 1.2448 | 1.4792 | 1.396 | 1.0394 | 0.91519 | 0.81217 | 0.77839 | 0.72899
43602.4606 | 1.2521 | 1.4801 | 1.3958 | 1.0395 | 0.91588 | 0.81305 | 0.77902 | 0.72975
43602.4607 | 1.2499 | 1.4815 | 1.3959 | 1.0409 | 0.91612 | 0.81251 | 0.77825 | 0.72925
43602.4605 | 1.2567 | 1.4837 | 1.3978 | 1.0433 | 0.9181 | 0.81416 | 0.782 | 0.73022
43602.4608 | 1.2588 | 1.4862 | 1.3988 | 1.0465 | 0.92103 | 0.81728 | 0.78301 | 0.7318
43602.4608 | 1.2541 | 1.487 | 1.399 | 1.047 | 0.9223 | 0.81803 | 0.78441 | 0.73194
43602.4608 | 1.2603 | 1.488 | 1.3991 | 1.0477 | 0.92143 | 0.81791 | 0.7836 | 0.73186
43602.4608 | 1.2633 | 1.4866 | 1.3986 | 1.0474 | 0.9223 | 0.81854 | 0.78673 | 0.73245
43602.4608 | 1.2599 | 1.4859 | 1.3979 | 1.0477 | 0.92192 | 0.81772 | 0.78534 | 0.73155
43602.4608 | 1.2609 | 1.4839 | 1.396 | 1.0463 | 0.92089 | 0.81761 | 0.78412 | 0.73166
43602.4608 | 1.2606 | 1.4846 | 1.3962 | 1.0463 | 0.9211 | 0.81716 | 0.78375 | 0.73184
43602.4609 | 1.2569 | 1.483 | 1.3953 | 1.0458 | 0.9212 | 0.81737 | 0.78412 | 0.73232
43602.4609 | 1.2535 | 1.4821 | 1.3946 | 1.045 | 0.91906 | 0.81582 | 0.78202 | 0.7313
43602.4609 | 1.2521 | 1.4812 | 1.3933 | 1.0436 | 0.91985 | 0.81657 | 0.78361 | 0.73201
43602.4609 | 1.2562 | 1.4805 | 1.3929 | 1.0434 | 0.91877 | 0.81543 | 0.7845 | 0.73135
43602.4609 | 1.2553 | 1.4793 | 1.392 | 1.0427 | 0.91807 | 0.8151 | 0.78199 | 0.73158
43602.4609 | 1.2557 | 1.4791 | 1.3918 | 1.0432 | 0.91841 | 0.81507 | 0.7812 | 0.7314
43602.4609 | 1.255 | 1.4791 | 1.3914 | 1.0431 | 0.91824 | 0.81526 | 0.78137 | 0.73173
43602.4608 | 1.2562 | 1.4754 | 1.3892 | 1.0415 | 0.91498 | 0.81278 | 0.78021 | 0.73119
43602.461 | 1.2428 | 1.4695 | 1.3833 | 1.0374 | 0.91311 | 0.81189 | 0.77872 | 0.73102
43602.461 | 1.2392 | 1.4675 | 1.3822 | 1.036 | 0.91267 | 0.81092 | 0.77933 | 0.7306
43602.4611 | 1.2419 | 1.4669 | 1.3816 | 1.0362 | 0.91182 | 0.81024 | 0.78102 | 0.73001
43602.4611 | 1.2432 | 1.4664 | 1.3805 | 1.0358 | 0.91178 | 0.81062 | 0.77817 | 0.73089
43602.4611 | 1.2427 | 1.4656 | 1.3803 | 1.0342 | 0.9116 | 0.8099 | 0.77743 | 0.73019
43602.4611 | 1.241 | 1.4643 | 1.3795 | 1.0339 | 0.9106 | 0.80929 | 0.7763 | 0.73011
43602.4611 | 1.2375 | 1.4633 | 1.3788 | 1.0329 | 0.91025 | 0.80914 | 0.77658 | 0.72994
43602.4611 | 1.231 | 1.4619 | 1.3778 | 1.0315 | 0.90969 | 0.80895 | 0.778 | 0.72998
43602.4611 | 1.2363 | 1.4611 | 1.3774 | 1.0316 | 0.90835 | 0.80792 | 0.7754 | 0.72934
43602.4611 | 1.2403 | 1.4634 | 1.3782 | 1.0331 | 0.90885 | 0.80818 | 0.77574 | 0.72989
43602.4611 | 1.2377 | 1.4608 | 1.3767 | 1.0315 | 0.90926 | 0.80829 | 0.77541 | 0.72946
43602.4612 | 1.2395 | 1.4599 | 1.3753 | 1.0302 | 0.90832 | 0.80747 | 0.77591 | 0.72944
43602.4612 | 1.2399 | 1.4621 | 1.3776 | 1.0322 | 0.90899 | 0.80794 | 0.77786 | 0.72954
43602.4612 | 1.2369 | 1.4596 | 1.3755 | 1.0304 | 0.90892 | 0.80819 | 0.77626 | 0.73001
43602.4612 | 1.2349 | 1.4612 | 1.3759 | 1.0309 | 0.90772 | 0.80714 | 0.77522 | 0.72921
43602.461 | 1.2386 | 1.4608 | 1.3758 | 1.0318 | 0.90893 | 0.80762 | 0.77522 | 0.72973
43602.4613 | 1.2397 | 1.4642 | 1.3799 | 1.0339 | 0.91003 | 0.80842 | 0.77681 | 0.73025
43602.4613 | 1.2417 | 1.4666 | 1.3811 | 1.0354 | 0.91079 | 0.80983 | 0.77931 | 0.73038
43602.4613 | 1.2393 | 1.4676 | 1.382 | 1.0355 | 0.91182 | 0.80998 | 0.77748 | 0.73068
43602.4613 | 1.2435 | 1.4676 | 1.382 | 1.0358 | 0.91225 | 0.81012 | 0.77689 | 0.7303
43602.4614 | 1.2439 | 1.4695 | 1.3837 | 1.0377 | 0.91262 | 0.81086 | 0.77731 | 0.73091
43602.4614 | 1.2449 | 1.4684 | 1.383 | 1.0361 | 0.91316 | 0.81134 | 0.77892 | 0.73086
43602.4614 | 1.2415 | 1.4686 | 1.3826 | 1.0353 | 0.91188 | 0.81009 | 0.77789 | 0.73022
43602.4614 | 1.2449 | 1.4693 | 1.3843 | 1.0368 | 0.91316 | 0.81117 | 0.77857 | 0.73047
43602.4614 | 1.2482 | 1.4708 | 1.385 | 1.038 | 0.91346 | 0.81146 | 0.77869 | 0.73097
43602.4614 | 1.2445 | 1.4714 | 1.3857 | 1.0379 | 0.91412 | 0.81155 | 0.77899 | 0.73072
43602.4614 | 1.2457 | 1.4704 | 1.3853 | 1.0373 | 0.91384 | 0.81179 | 0.78247 | 0.73111
43602.4614 | 1.2459 | 1.4712 | 1.3852 | 1.0374 | 0.91316 | 0.81093 | 0.77968 | 0.73066
43602.4614 | 1.2422 | 1.4717 | 1.3863 | 1.0378 | 0.91396 | 0.81148 | 0.77928 | 0.73097
43602.4613 | 1.2465 | 1.4723 | 1.3863 | 1.0377 | 0.9141 | 0.81159 | 0.77864 | 0.7307
43602.4616 | 1.2408 | 1.4724 | 1.3882 | 1.0384 | 0.9145 | 0.81224 | 0.77985 | 0.73123
43602.4616 | 1.2462 | 1.4762 | 1.391 | 1.0409 | 0.91448 | 0.81227 | 0.77891 | 0.73089
43602.4616 | 1.2421 | 1.4747 | 1.3897 | 1.0385 | 0.91579 | 0.81319 | 0.77931 | 0.73136
43602.4616 | 1.2437 | 1.4763 | 1.391 | 1.0396 | 0.91431 | 0.81249 | 0.78232 | 0.73094
43602.4616 | 1.2423 | 1.4743 | 1.3898 | 1.0382 | 0.91478 | 0.81257 | 0.78122 | 0.73143
43602.4616 | 1.2466 | 1.4764 | 1.3917 | 1.04 | 0.91418 | 0.81174 | 0.77943 | 0.73102
43602.4616 | 1.2458 | 1.4766 | 1.3922 | 1.0408 | 0.91556 | 0.8134 | 0.78002 | 0.73169
43602.4616 | 1.2478 | 1.4757 | 1.3912 | 1.0397 | 0.91628 | 0.81344 | 0.77964 | 0.73168
43602.4616 | 1.2388 | 1.4761 | 1.3918 | 1.0395 | 0.9154 | 0.81295 | 0.78205 | 0.73149
43602.4617 | 1.2496 | 1.4783 | 1.3929 | 1.0409 | 0.9159 | 0.81348 | 0.78202 | 0.73196
43602.4617 | 1.2404 | 1.4767 | 1.3918 | 1.0398 | 0.91631 | 0.81381 | 0.78124 | 0.73206
43602.4617 | 1.2481 | 1.4783 | 1.3927 | 1.0408 | 0.91643 | 0.81362 | 0.78066 | 0.73175
43602.4617 | 1.2376 | 1.4757 | 1.3918 | 1.0385 | 0.91566 | 0.81304 | 0.77991 | 0.73115
43602.4617 | 1.2406 | 1.4772 | 1.3929 | 1.04 | 0.91563 | 0.81342 | 0.78041 | 0.73205
43602.4617 | 1.2457 | 1.4779 | 1.3932 | 1.0401 | 0.91584 | 0.81378 | 0.78059 | 0.73168
43602.4615 | 1.2417 | 1.4779 | 1.3939 | 1.0392 | 0.91674 | 0.81424 | 0.78349 | 0.73225
43602.4618 | 1.2416 | 1.4816 | 1.3976 | 1.0407 | 0.91692 | 0.81454 | 0.7839 | 0.73236
43602.4619 | 1.2471 | 1.48 | 1.3964 | 1.0405 | 0.91722 | 0.81481 | 0.78192 | 0.73214
43602.4619 | 1.2407 | 1.4801 | 1.3972 | 1.0398 | 0.91627 | 0.81409 | 0.78103 | 0.7321
43602.4619 | 1.2473 | 1.4813 | 1.3971 | 1.0402 | 0.91704 | 0.81447 | 0.78128 | 0.73215
43602.4619 | 1.2407 | 1.4801 | 1.397 | 1.0397 | 0.91613 | 0.81364 | 0.78051 | 0.73161
43602.4619 | 1.2392 | 1.4804 | 1.3975 | 1.0401 | 0.91664 | 0.81454 | 0.78311 | 0.73224
43602.4619 | 1.2419 | 1.4802 | 1.3976 | 1.0394 | 0.91596 | 0.81375 | 0.78154 | 0.73166
43602.4619 | 1.2467 | 1.4834 | 1.3991 | 1.0415 | 0.91734 | 0.81484 | 0.78169 | 0.73237
43602.4619 | 1.2446 | 1.483 | 1.3994 | 1.0408 | 0.918 | 0.81583 | 0.78269 | 0.73278
43602.4619 | 1.2489 | 1.4833 | 1.3992 | 1.041 | 0.91746 | 0.81501 | 0.78176 | 0.7324
43602.462 | 1.2454 | 1.4853 | 1.4002 | 1.0425 | 0.91845 | 0.81546 | 0.78284 | 0.73218
43602.462 | 1.2412 | 1.483 | 1.3997 | 1.041 | 0.91773 | 0.81544 | 0.78481 | 0.73259
43602.462 | 1.2454 | 1.4841 | 1.4009 | 1.0415 | 0.91827 | 0.81612 | 0.78371 | 0.73303
43602.462 | 1.2449 | 1.4846 | 1.4008 | 1.0424 | 0.91856 | 0.816 | 0.78247 | 0.7329
43602.4618 | 1.2405 | 1.4862 | 1.4017 | 1.0422 | 0.91899 | 0.8159 | 0.78235 | 0.73253
43602.4621 | 1.2444 | 1.4872 | 1.4034 | 1.0418 | 0.91934 | 0.81668 | 0.78366 | 0.73305
43602.4621 | 1.2434 | 1.4865 | 1.4031 | 1.0419 | 0.91955 | 0.81652 | 0.78265 | 0.73291
43602.4621 | 1.2405 | 1.4863 | 1.4032 | 1.0422 | 0.91883 | 0.81634 | 0.78236 | 0.73324
43602.4621 | 1.2415 | 1.4866 | 1.404 | 1.0422 | 0.91987 | 0.81721 | 0.78727 | 0.73338
43602.4621 | 1.2374 | 1.4868 | 1.4034 | 1.042 | 0.91947 | 0.81644 | 0.7842 | 0.73257
43602.4622 | 1.242 | 1.4855 | 1.4023 | 1.041 | 0.91933 | 0.81673 | 0.78366 | 0.73333
43602.4622 | 1.2385 | 1.4858 | 1.4025 | 1.0415 | 0.91974 | 0.81652 | 0.78339 | 0.73362
43602.4622 | 1.2417 | 1.4836 | 1.4017 | 1.0399 | 0.91812 | 0.8158 | 0.78216 | 0.73297
43602.4622 | 1.2397 | 1.4839 | 1.4012 | 1.0401 | 0.91835 | 0.81633 | 0.78277 | 0.73353
43602.4622 | 1.2426 | 1.4841 | 1.4015 | 1.0395 | 0.9179 | 0.81531 | 0.78285 | 0.73241
43602.4622 | 1.242 | 1.486 | 1.4024 | 1.0414 | 0.91899 | 0.81632 | 0.78562 | 0.73352
43602.4622 | 1.2443 | 1.4845 | 1.4012 | 1.0397 | 0.91845 | 0.81566 | 0.78282 | 0.73303
43602.4622 | 1.2441 | 1.4834 | 1.4014 | 1.0398 | 0.91775 | 0.81491 | 0.78119 | 0.7324
43602.4621 | 1.2374 | 1.4828 | 1.4013 | 1.0385 | 0.91815 | 0.8156 | 0.78239 | 0.733
43602.4624 | 1.2381 | 1.4813 | 1.3982 | 1.0365 | 0.91644 | 0.81417 | 0.78121 | 0.73259
43602.4624 | 1.2351 | 1.479 | 1.3971 | 1.0355 | 0.91559 | 0.81344 | 0.7804 | 0.73264
43602.4624 | 1.2361 | 1.4788 | 1.3964 | 1.0352 | 0.91559 | 0.81368 | 0.78106 | 0.73295
43602.4624 | 1.2385 | 1.4795 | 1.3966 | 1.0358 | 0.91576 | 0.81324 | 0.78014 | 0.73261
43602.4624 | 1.2303 | 1.4765 | 1.3951 | 1.0343 | 0.91448 | 0.81253 | 0.78112 | 0.73209
43602.4624 | 1.2297 | 1.4777 | 1.3964 | 1.0354 | 0.91454 | 0.81309 | 0.78034 | 0.73241
43602.4624 | 1.2376 | 1.4797 | 1.3967 | 1.036 | 0.91545 | 0.81314 | 0.77983 | 0.73253
43602.4624 | 1.2359 | 1.4774 | 1.395 | 1.0341 | 0.91491 | 0.81287 | 0.78204 | 0.73239
43602.4624 | 1.2313 | 1.4786 | 1.3962 | 1.0347 | 0.91514 | 0.81343 | 0.78181 | 0.73286
43602.4625 | 1.2353 | 1.477 | 1.395 | 1.0345 | 0.91477 | 0.81296 | 0.78042 | 0.73225
43602.4625 | 1.2279 | 1.4758 | 1.3947 | 1.0329 | 0.91385 | 0.81264 | 0.77984 | 0.73249
43602.4625 | 1.2334 | 1.4778 | 1.3948 | 1.0332 | 0.9143 | 0.81263 | 0.7796 | 0.73247
43602.4625 | 1.236 | 1.4799 | 1.3954 | 1.0337 | 0.91364 | 0.81173 | 0.77951 | 0.73207
43602.4623 | 1.2358 | 1.4782 | 1.3939 | 1.0331 | 0.91511 | 0.81303 | 0.78172 | 0.73277
43602.4626 | 1.2309 | 1.4788 | 1.3972 | 1.0357 | 0.9152 | 0.81347 | 0.78048 | 0.73273
43602.4626 | 1.2365 | 1.4788 | 1.3968 | 1.0349 | 0.91583 | 0.81417 | 0.78053 | 0.73296
43602.4626 | 1.2289 | 1.4784 | 1.3973 | 1.0356 | 0.9151 | 0.81356 | 0.77998 | 0.73262
43602.4626 | 1.234 | 1.4803 | 1.398 | 1.0367 | 0.91608 | 0.81407 | 0.78234 | 0.73311
43602.4627 | 1.2405 | 1.4799 | 1.3965 | 1.0349 | 0.91588 | 0.81367 | 0.78107 | 0.73286
43602.4627 | 1.231 | 1.4787 | 1.3973 | 1.0361 | 0.9158 | 0.81375 | 0.77994 | 0.73261
43602.4627 | 1.2354 | 1.4777 | 1.3957 | 1.0344 | 0.9162 | 0.81424 | 0.78021 | 0.73359
43602.4627 | 1.237 | 1.4769 | 1.3952 | 1.0343 | 0.9144 | 0.81292 | 0.78148 | 0.7326
43602.4627 | 1.2355 | 1.4775 | 1.3946 | 1.0335 | 0.91429 | 0.81261 | 0.78282 | 0.73249
43602.4627 | 1.2379 | 1.4782 | 1.3953 | 1.0347 | 0.9147 | 0.81269 | 0.7805 | 0.73235
43602.4627 | 1.2311 | 1.4782 | 1.3956 | 1.0345 | 0.91463 | 0.81315 | 0.78045 | 0.73283
43602.4627 | 1.2271 | 1.4767 | 1.3952 | 1.034 | 0.91398 | 0.81286 | 0.77951 | 0.73236
43602.4627 | 1.234 | 1.4768 | 1.394 | 1.0329 | 0.91467 | 0.81304 | 0.78019 | 0.73286
43602.4626 | 1.2352 | 1.475 | 1.3935 | 1.0319 | 0.91342 | 0.81212 | 0.77931 | 0.73207
43602.4629 | 1.234 | 1.4755 | 1.3937 | 1.0328 | 0.91351 | 0.81175 | 0.77894 | 0.73197
43602.4629 | 1.2309 | 1.4768 | 1.3957 | 1.0339 | 0.9134 | 0.81191 | 0.77897 | 0.73197
43602.4629 | 1.2427 | 1.479 | 1.3954 | 1.0347 | 0.91529 | 0.81288 | 0.7797 | 0.7327
43602.4629 | 1.2369 | 1.4765 | 1.3944 | 1.0337 | 0.91495 | 0.81248 | 0.77975 | 0.73213
43602.4629 | 1.2377 | 1.4783 | 1.3951 | 1.0347 | 0.91481 | 0.81255 | 0.78001 | 0.73207
43602.4629 | 1.2358 | 1.4781 | 1.3953 | 1.0352 | 0.91531 | 0.81333 | 0.78334 | 0.73237
43602.4629 | 1.24 | 1.4777 | 1.3948 | 1.0344 | 0.91522 | 0.81315 | 0.78079 | 0.73244
43602.4629 | 1.2366 | 1.4776 | 1.3946 | 1.0338 | 0.91502 | 0.81264 | 0.7796 | 0.73209
43602.463 | 1.2407 | 1.4793 | 1.3966 | 1.0356 | 0.91589 | 0.81322 | 0.7798 | 0.73232
43602.463 | 1.2404 | 1.4798 | 1.3967 | 1.0359 | 0.91648 | 0.81386 | 0.78017 | 0.73271
43602.463 | 1.2365 | 1.4798 | 1.396 | 1.0351 | 0.91736 | 0.81442 | 0.78175 | 0.73351
43602.463 | 1.2426 | 1.4806 | 1.3975 | 1.0371 | 0.91653 | 0.81369 | 0.78017 | 0.73218
43602.463 | 1.248 | 1.4819 | 1.3982 | 1.0369 | 0.91796 | 0.8143 | 0.78189 | 0.73247
43602.4629 | 1.244 | 1.481 | 1.3979 | 1.0371 | 0.91787 | 0.81463 | 0.78173 | 0.73275
43602.4631 | 1.2489 | 1.482 | 1.3972 | 1.0383 | 0.91964 | 0.81665 | 0.7858 | 0.73386
43602.4631 | 1.2431 | 1.4814 | 1.398 | 1.0379 | 0.91839 | 0.81532 | 0.78243 | 0.73299
43602.4631 | 1.2509 | 1.4845 | 1.3989 | 1.0403 | 0.91933 | 0.8163 | 0.7828 | 0.73352
43602.4632 | 1.2462 | 1.4828 | 1.3976 | 1.0386 | 0.92041 | 0.81678 | 0.78302 | 0.73407
43602.4632 | 1.2446 | 1.4818 | 1.3974 | 1.0379 | 0.91857 | 0.81571 | 0.78193 | 0.73346
43602.4632 | 1.2485 | 1.4821 | 1.3979 | 1.0385 | 0.91838 | 0.81538 | 0.78214 | 0.73272
43602.4632 | 1.2535 | 1.4844 | 1.3995 | 1.0405 | 0.9199 | 0.81652 | 0.78267 | 0.73365
43602.4632 | 1.2517 | 1.484 | 1.3985 | 1.0407 | 0.9199 | 0.81677 | 0.78582 | 0.73364
43602.4632 | 1.248 | 1.4825 | 1.3981 | 1.04 | 0.91975 | 0.81667 | 0.78433 | 0.73373
43602.4632 | 1.2484 | 1.4861 | 1.4009 | 1.0425 | 0.92094 | 0.81746 | 0.78389 | 0.73424
43602.4632 | 1.2491 | 1.4858 | 1.4011 | 1.042 | 0.92206 | 0.81842 | 0.7846 | 0.73436
43602.4632 | 1.2565 | 1.4863 | 1.4007 | 1.0422 | 0.92125 | 0.81799 | 0.78366 | 0.73453
43602.4633 | 1.2572 | 1.488 | 1.402 | 1.0431 | 0.92254 | 0.81858 | 0.78519 | 0.73462
43602.4631 | 1.2542 | 1.487 | 1.4015 | 1.0433 | 0.92306 | 0.8198 | 0.78633 | 0.73548
43602.4634 | 1.2551 | 1.4866 | 1.4012 | 1.0433 | 0.92208 | 0.81912 | 0.78481 | 0.73541
43602.4634 | 1.2531 | 1.4878 | 1.4018 | 1.044 | 0.92381 | 0.81985 | 0.78568 | 0.73572
43602.4634 | 1.2559 | 1.4873 | 1.4009 | 1.0441 | 0.92321 | 0.81967 | 0.78804 | 0.73565
43602.4634 | 1.2524 | 1.4872 | 1.4013 | 1.0433 | 0.92256 | 0.81922 | 0.78627 | 0.73545
43602.4634 | 1.2595 | 1.4878 | 1.4015 | 1.0439 | 0.922 | 0.81921 | 0.78514 | 0.73523
43602.4634 | 1.2571 | 1.4868 | 1.4011 | 1.0437 | 0.9225 | 0.81941 | 0.78503 | 0.73523
43602.4634 | 1.2549 | 1.4886 | 1.4014 | 1.0449 | 0.92328 | 0.82017 | 0.786 | 0.73612
43602.4635 | 1.2567 | 1.4887 | 1.4017 | 1.0446 | 0.92304 | 0.82022 | 0.78764 | 0.73594
43602.4635 | 1.2562 | 1.4882 | 1.4016 | 1.0443 | 0.92306 | 0.81982 | 0.78783 | 0.73543
43602.4635 | 1.2555 | 1.4873 | 1.4017 | 1.0438 | 0.92266 | 0.81905 | 0.78532 | 0.73526
43602.4635 | 1.2565 | 1.489 | 1.4031 | 1.0453 | 0.92363 | 0.82029 | 0.78639 | 0.73604
43602.4635 | 1.2558 | 1.4899 | 1.4032 | 1.0455 | 0.92385 | 0.82054 | 0.78672 | 0.73618
43602.4634 | 1.2546 | 1.4908 | 1.4037 | 1.0454 | 0.92399 | 0.82079 | 0.78691 | 0.73594
43602.4636 | 1.2585 | 1.4921 | 1.4056 | 1.0459 | 0.92554 | 0.82249 | 0.78766 | 0.7372
43602.4636 | 1.2583 | 1.4919 | 1.4052 | 1.0461 | 0.92392 | 0.82074 | 0.78621 | 0.73609
43602.4636 | 1.2548 | 1.49 | 1.4039 | 1.0454 | 0.9243 | 0.82085 | 0.78682 | 0.73633
43602.4637 | 1.2521 | 1.4903 | 1.4044 | 1.0447 | 0.92431 | 0.82096 | 0.78821 | 0.73627
43602.4637 | 1.2522 | 1.4894 | 1.4034 | 1.0438 | 0.92353 | 0.82071 | 0.78853 | 0.73635
43602.4637 | 1.2553 | 1.4907 | 1.4039 | 1.0448 | 0.92383 | 0.82072 | 0.78715 | 0.73679
43602.4637 | 1.2545 | 1.4885 | 1.4027 | 1.0422 | 0.92334 | 0.82042 | 0.78665 | 0.73633
43602.4637 | 1.2546 | 1.489 | 1.4024 | 1.0439 | 0.92225 | 0.81946 | 0.78626 | 0.73561
43602.4637 | 1.2526 | 1.4875 | 1.4023 | 1.0424 | 0.92307 | 0.8201 | 0.78798 | 0.73615
43602.4637 | 1.2504 | 1.4868 | 1.4009 | 1.0425 | 0.92187 | 0.81917 | 0.78558 | 0.73565
43602.4637 | 1.2493 | 1.486 | 1.4004 | 1.0418 | 0.92138 | 0.81892 | 0.78499 | 0.73579
43602.4637 | 1.2467 | 1.4849 | 1.3997 | 1.0408 | 0.921 | 0.8188 | 0.7848 | 0.73587
43602.4636 | 1.2465 | 1.4819 | 1.3972 | 1.0386 | 0.91921 | 0.81687 | 0.78395 | 0.73495
43602.4639 | 1.2459 | 1.479 | 1.3946 | 1.0364 | 0.91698 | 0.81525 | 0.78467 | 0.73454
43602.4639 | 1.2372 | 1.478 | 1.3949 | 1.0363 | 0.91682 | 0.8152 | 0.78255 | 0.73456
43602.4639 | 1.2451 | 1.4796 | 1.3948 | 1.0371 | 0.91726 | 0.81562 | 0.78242 | 0.73454
43602.4639 | 1.2372 | 1.4774 | 1.3933 | 1.0349 | 0.91703 | 0.81509 | 0.78151 | 0.73412
43602.4639 | 1.2438 | 1.48 | 1.3952 | 1.038 | 0.91637 | 0.81456 | 0.78184 | 0.7338
43602.4639 | 1.2443 | 1.4788 | 1.3939 | 1.0361 | 0.91729 | 0.81476 | 0.78456 | 0.73403
43602.4639 | 1.2448 | 1.4784 | 1.394 | 1.0366 | 0.91618 | 0.81438 | 0.78156 | 0.73345
43602.4639 | 1.2433 | 1.4781 | 1.3945 | 1.0362 | 0.91678 | 0.81454 | 0.78129 | 0.73378
43602.464 | 1.2454 | 1.4795 | 1.3945 | 1.0366 | 0.91717 | 0.81518 | 0.78106 | 0.73408
43602.464 | 1.2347 | 1.4758 | 1.3928 | 1.0333 | 0.91629 | 0.81434 | 0.78082 | 0.73348
43602.464 | 1.2461 | 1.4772 | 1.3925 | 1.0351 | 0.91467 | 0.81348 | 0.78362 | 0.73353
43602.464 | 1.2425 | 1.4751 | 1.3912 | 1.0341 | 0.9154 | 0.81348 | 0.7812 | 0.73308
43602.464 | 1.2402 | 1.4751 | 1.3908 | 1.0337 | 0.91437 | 0.81338 | 0.78026 | 0.73314
43602.4639 | 1.2469 | 1.4751 | 1.3897 | 1.0343 | 0.91493 | 0.81368 | 0.78098 | 0.73362
43602.4641 | 1.2457 | 1.4775 | 1.3913 | 1.0369 | 0.91535 | 0.81361 | 0.78025 | 0.73287
43602.4641 | 1.2467 | 1.4768 | 1.3912 | 1.036 | 0.91586 | 0.81405 | 0.78322 | 0.73399
43602.4641 | 1.2465 | 1.4775 | 1.392 | 1.0367 | 0.91653 | 0.81447 | 0.78155 | 0.73322
43602.4642 | 1.2502 | 1.4809 | 1.3938 | 1.0388 | 0.91758 | 0.81515 | 0.78191 | 0.734
43602.4642 | 1.2492 | 1.4821 | 1.3952 | 1.0392 | 0.91855 | 0.81565 | 0.78188 | 0.73385
43602.4642 | 1.2573 | 1.4856 | 1.3971 | 1.0419 | 0.91994 | 0.81688 | 0.7829 | 0.73447
43602.4642 | 1.2595 | 1.4862 | 1.3982 | 1.0423 | 0.92133 | 0.81793 | 0.78442 | 0.73491
43602.4642 | 1.2509 | 1.4871 | 1.3995 | 1.0432 | 0.92219 | 0.81898 | 0.78844 | 0.73513
43602.4642 | 1.2578 | 1.4889 | 1.4003 | 1.0437 | 0.92226 | 0.819 | 0.78611 | 0.73491
43602.4642 | 1.2601 | 1.4908 | 1.4014 | 1.0452 | 0.92339 | 0.81953 | 0.78585 | 0.73532
43602.4642 | 1.2658 | 1.492 | 1.4021 | 1.0471 | 0.92435 | 0.82004 | 0.78615 | 0.73575
43602.4642 | 1.2647 | 1.492 | 1.4028 | 1.0467 | 0.92532 | 0.82113 | 0.78718 | 0.73591
43602.4643 | 1.2657 | 1.4938 | 1.4047 | 1.0485 | 0.92563 | 0.82164 | 0.78725 | 0.73647
43602.4641 | 1.2731 | 1.5022 | 1.4101 | 1.0536 | 0.93071 | 0.82567 | 0.79302 | 0.73799
43602.4644 | 1.2786 | 1.5082 | 1.415 | 1.057 | 0.93358 | 0.82781 | 0.79189 | 0.73855
43602.4644 | 1.2867 | 1.5093 | 1.4162 | 1.0584 | 0.93399 | 0.828 | 0.79529 | 0.73839
43602.4644 | 1.2783 | 1.5104 | 1.416 | 1.0584 | 0.93556 | 0.82938 | 0.79504 | 0.73903
43602.4644 | 1.2867 | 1.5111 | 1.4175 | 1.0598 | 0.93495 | 0.82897 | 0.7941 | 0.73893
43602.4644 | 1.2783 | 1.5122 | 1.4192 | 1.0607 | 0.93613 | 0.8302 | 0.7945 | 0.73936
43602.4644 | 1.2792 | 1.513 | 1.4196 | 1.0612 | 0.93741 | 0.83081 | 0.79746 | 0.73954
43602.4644 | 1.2852 | 1.5142 | 1.4209 | 1.0624 | 0.93744 | 0.83106 | 0.797 | 0.73985
43602.4645 | 1.2845 | 1.5183 | 1.4237 | 1.0645 | 0.93946 | 0.83223 | 0.79714 | 0.74037
43602.4645 | 1.2906 | 1.5165 | 1.4224 | 1.0631 | 0.93914 | 0.83206 | 0.79658 | 0.7402
43602.4645 | 1.2906 | 1.5189 | 1.4243 | 1.0648 | 0.93939 | 0.83226 | 0.79631 | 0.74025
43602.4645 | 1.286 | 1.5205 | 1.4262 | 1.0662 | 0.94086 | 0.834 | 0.79896 | 0.74098
43602.4645 | 1.2914 | 1.5222 | 1.427 | 1.0667 | 0.94103 | 0.83398 | 0.79935 | 0.74069
43602.4644 | 1.2861 | 1.5245 | 1.4298 | 1.069 | 0.94301 | 0.83563 | 0.79951 | 0.74166
43602.4646 | 1.2841 | 1.5266 | 1.4326 | 1.0698 | 0.94462 | 0.83733 | 0.80151 | 0.74209
43602.4646 | 1.2953 | 1.5262 | 1.4312 | 1.0695 | 0.94473 | 0.83721 | 0.80125 | 0.74228
43602.4646 | 1.2911 | 1.5244 | 1.4302 | 1.0678 | 0.94391 | 0.83667 | 0.8008 | 0.74226
43602.4647 | 1.2928 | 1.5254 | 1.431 | 1.0678 | 0.94341 | 0.83607 | 0.80167 | 0.74208
43602.4647 | 1.2893 | 1.525 | 1.4297 | 1.0675 | 0.94341 | 0.83566 | 0.80026 | 0.74157
43602.4647 | 1.2849 | 1.5243 | 1.4298 | 1.067 | 0.94312 | 0.83551 | 0.80001 | 0.74219
43602.4647 | 1.285 | 1.5237 | 1.4291 | 1.0664 | 0.94383 | 0.8363 | 0.80026 | 0.74216
43602.4647 | 1.2858 | 1.5237 | 1.4298 | 1.067 | 0.94314 | 0.83553 | 0.80174 | 0.74183
43602.4647 | 1.2895 | 1.5252 | 1.4308 | 1.0685 | 0.94379 | 0.83641 | 0.80179 | 0.74226
43602.4647 | 1.2897 | 1.5244 | 1.4301 | 1.0669 | 0.9442 | 0.83649 | 0.80086 | 0.74244
43602.4647 | 1.2901 | 1.5237 | 1.4303 | 1.0669 | 0.94344 | 0.83577 | 0.80021 | 0.74264
43602.4647 | 1.2933 | 1.525 | 1.4312 | 1.0678 | 0.94376 | 0.83554 | 0.79965 | 0.74174
43602.4648 | 1.2889 | 1.5236 | 1.43 | 1.0666 | 0.94424 | 0.83583 | 0.79998 | 0.74193
43602.4646 | 1.2842 | 1.5261 | 1.4331 | 1.0688 | 0.94481 | 0.83728 | 0.80259 | 0.74289
43602.4649 | 1.2887 | 1.528 | 1.4347 | 1.0705 | 0.94449 | 0.83745 | 0.80409 | 0.74331
43602.4649 | 1.2826 | 1.5261 | 1.4337 | 1.0696 | 0.94542 | 0.83781 | 0.80271 | 0.74328
43602.4649 | 1.2868 | 1.5266 | 1.4339 | 1.0695 | 0.9449 | 0.8374 | 0.80126 | 0.74318
43602.4649 | 1.2889 | 1.5258 | 1.4327 | 1.0686 | 0.94524 | 0.83767 | 0.80131 | 0.74322
43602.4649 | 1.2885 | 1.5255 | 1.4327 | 1.0693 | 0.94502 | 0.83723 | 0.80102 | 0.74316
43602.4649 | 1.2815 | 1.5255 | 1.4331 | 1.0689 | 0.94488 | 0.83706 | 0.80213 | 0.74304
43602.465 | 1.2885 | 1.5239 | 1.4323 | 1.0678 | 0.94472 | 0.83732 | 0.80428 | 0.7437
43602.465 | 1.2834 | 1.5238 | 1.4311 | 1.0669 | 0.94385 | 0.8363 | 0.80098 | 0.74274
43602.465 | 1.286 | 1.5227 | 1.4297 | 1.066 | 0.94262 | 0.83589 | 0.80024 | 0.74288
43602.465 | 1.2832 | 1.5221 | 1.4294 | 1.0657 | 0.94254 | 0.83527 | 0.79955 | 0.74301
43602.4649 | 1.2854 | 1.5194 | 1.427 | 1.0641 | 0.94265 | 0.8354 | 0.79971 | 0.74308
43602.4651 | 1.2728 | 1.5098 | 1.4182 | 1.0572 | 0.93558 | 0.83025 | 0.79803 | 0.74115
43602.4651 | 1.2783 | 1.51 | 1.4182 | 1.0581 | 0.93569 | 0.83001 | 0.79575 | 0.74104
43602.4651 | 1.275 | 1.5086 | 1.4178 | 1.0586 | 0.93622 | 0.82996 | 0.79577 | 0.74096
43602.4651 | 1.2769 | 1.5087 | 1.4184 | 1.0575 | 0.93629 | 0.83064 | 0.79576 | 0.74117
43602.4651 | 1.2777 | 1.5095 | 1.4178 | 1.0588 | 0.93539 | 0.83001 | 0.7948 | 0.74087
43602.4652 | 1.2686 | 1.5078 | 1.4172 | 1.0565 | 0.93579 | 0.8305 | 0.79707 | 0.74137
43602.4652 | 1.2768 | 1.5106 | 1.4183 | 1.0593 | 0.93515 | 0.83009 | 0.7969 | 0.74073
43602.4652 | 1.2727 | 1.5092 | 1.4173 | 1.0583 | 0.93634 | 0.83059 | 0.79629 | 0.74138
43602.4652 | 1.2748 | 1.5109 | 1.4193 | 1.0595 | 0.93585 | 0.83035 | 0.7955 | 0.74118
43602.4652 | 1.2797 | 1.5108 | 1.4195 | 1.0596 | 0.93743 | 0.83184 | 0.7969 | 0.74184
43602.4652 | 1.276 | 1.5125 | 1.4203 | 1.0612 | 0.93699 | 0.83199 | 0.79685 | 0.74193
43602.4652 | 1.2794 | 1.5119 | 1.4198 | 1.0608 | 0.93818 | 0.83264 | 0.79853 | 0.74172
43602.4651 | 1.2761 | 1.5088 | 1.4168 | 1.0582 | 0.93645 | 0.8311 | 0.79872 | 0.74176
43602.4653 | 1.2801 | 1.5052 | 1.4133 | 1.0565 | 0.93341 | 0.82902 | 0.79397 | 0.74063
43602.4654 | 1.2684 | 1.504 | 1.4119 | 1.0549 | 0.93305 | 0.82839 | 0.79349 | 0.74034
43602.4654 | 1.2702 | 1.501 | 1.4103 | 1.053 | 0.93379 | 0.82862 | 0.79516 | 0.74056
43602.4654 | 1.2715 | 1.5021 | 1.4105 | 1.0533 | 0.93018 | 0.82659 | 0.794 | 0.73964
43602.4654 | 1.2728 | 1.5014 | 1.4101 | 1.0543 | 0.93276 | 0.82798 | 0.79372 | 0.74037
43602.4654 | 1.269 | 1.5015 | 1.4096 | 1.0543 | 0.93267 | 0.82809 | 0.79357 | 0.74045
43602.4654 | 1.2769 | 1.5039 | 1.4117 | 1.056 | 0.93282 | 0.82832 | 0.79338 | 0.74033
43602.4654 | 1.2745 | 1.5034 | 1.4106 | 1.0547 | 0.93296 | 0.82837 | 0.7937 | 0.74024
43602.4654 | 1.274 | 1.5008 | 1.4097 | 1.0537 | 0.93206 | 0.82795 | 0.79463 | 0.74015
43602.4654 | 1.2748 | 1.501 | 1.4084 | 1.0534 | 0.93165 | 0.82743 | 0.79629 | 0.73974
43602.4655 | 1.2763 | 1.5035 | 1.4103 | 1.0553 | 0.93195 | 0.82738 | 0.79376 | 0.73989
43602.4653 | 1.2825 | 1.5037 | 1.4101 | 1.0558 | 0.93355 | 0.82805 | 0.79385 | 0.7402
43602.4656 | 1.274 | 1.5028 | 1.4088 | 1.0553 | 0.9315 | 0.82697 | 0.79333 | 0.73931
43602.4656 | 1.2792 | 1.5047 | 1.4094 | 1.0566 | 0.93276 | 0.82757 | 0.79324 | 0.73998
43602.4656 | 1.2705 | 1.5027 | 1.4086 | 1.0567 | 0.93361 | 0.82876 | 0.79382 | 0.74053
43602.4656 | 1.2755 | 1.504 | 1.4088 | 1.0571 | 0.93303 | 0.82834 | 0.79416 | 0.74012
43602.4656 | 1.2667 | 1.5021 | 1.4078 | 1.0561 | 0.93297 | 0.82808 | 0.79368 | 0.74025
43602.4656 | 1.2792 | 1.5043 | 1.4081 | 1.0569 | 0.93323 | 0.82795 | 0.79322 | 0.73983
43602.4656 | 1.2779 | 1.5002 | 1.4061 | 1.0548 | 0.93222 | 0.8273 | 0.79607 | 0.73965
43602.4656 | 1.2774 | 1.5008 | 1.4067 | 1.0558 | 0.93255 | 0.82713 | 0.79396 | 0.73974
43602.4657 | 1.2801 | 1.4994 | 1.4053 | 1.0552 | 0.93221 | 0.82691 | 0.7926 | 0.7392
43602.4657 | 1.2754 | 1.5 | 1.4058 | 1.0548 | 0.9309 | 0.8262 | 0.79226 | 0.73895
43602.4656 | 1.2754 | 1.5014 | 1.4066 | 1.057 | 0.9327 | 0.82737 | 0.79286 | 0.73922
43602.4658 | 1.2792 | 1.5103 | 1.413 | 1.0619 | 0.93682 | 0.83084 | 0.79844 | 0.74093
43602.4658 | 1.2738 | 1.5102 | 1.4131 | 1.0626 | 0.93741 | 0.83155 | 0.79671 | 0.74092
43602.4658 | 1.2831 | 1.5114 | 1.4146 | 1.0631 | 0.93812 | 0.83183 | 0.79632 | 0.74051
43602.4658 | 1.2932 | 1.5145 | 1.4167 | 1.0653 | 0.94004 | 0.83252 | 0.79707 | 0.74145
43602.4658 | 1.2878 | 1.5163 | 1.4173 | 1.0651 | 0.94022 | 0.83314 | 0.79792 | 0.74163
43602.4658 | 1.2792 | 1.5145 | 1.416 | 1.0639 | 0.93942 | 0.83299 | 0.79823 | 0.74107
43602.4659 | 1.2933 | 1.5173 | 1.4186 | 1.066 | 0.93975 | 0.83314 | 0.80047 | 0.74148
43602.4659 | 1.2869 | 1.5178 | 1.4195 | 1.0668 | 0.94093 | 0.83369 | 0.79897 | 0.74139
43602.4659 | 1.2936 | 1.5193 | 1.4204 | 1.067 | 0.94137 | 0.8341 | 0.7984 | 0.74157
43602.4659 | 1.2902 | 1.5175 | 1.4185 | 1.065 | 0.9408 | 0.83334 | 0.79736 | 0.74092
43602.4659 | 1.284 | 1.5191 | 1.4202 | 1.0666 | 0.94054 | 0.83382 | 0.79812 | 0.74133
43602.4658 | 1.2892 | 1.519 | 1.4207 | 1.0661 | 0.94107 | 0.83347 | 0.79776 | 0.74094
43602.466 | 1.2884 | 1.5236 | 1.4247 | 1.0674 | 0.94188 | 0.83378 | 0.7985 | 0.74031
43602.466 | 1.2952 | 1.5245 | 1.4255 | 1.0688 | 0.94125 | 0.83406 | 0.7983 | 0.74055
43602.466 | 1.2934 | 1.5233 | 1.4255 | 1.0676 | 0.94311 | 0.83449 | 0.79872 | 0.74077
43602.4661 | 1.2938 | 1.5241 | 1.4264 | 1.0686 | 0.94064 | 0.83288 | 0.79663 | 0.73999
43602.4661 | 1.2973 | 1.5257 | 1.4271 | 1.069 | 0.94275 | 0.83428 | 0.79922 | 0.74035
43602.4661 | 1.2963 | 1.5253 | 1.4267 | 1.0677 | 0.94183 | 0.83381 | 0.79846 | 0.74015
43602.4661 | 1.295 | 1.527 | 1.4286 | 1.0706 | 0.94287 | 0.83469 | 0.79848 | 0.7408
43602.4661 | 1.3022 | 1.5278 | 1.4296 | 1.0703 | 0.94311 | 0.83503 | 0.80024 | 0.74077
43602.4661 | 1.2886 | 1.5303 | 1.4318 | 1.0721 | 0.94446 | 0.83635 | 0.80217 | 0.74128
43602.4661 | 1.2934 | 1.5314 | 1.4326 | 1.0724 | 0.94484 | 0.83684 | 0.80092 | 0.74116
43602.466 | 1.2961 | 1.5302 | 1.432 | 1.0708 | 0.94409 | 0.83567 | 0.79981 | 0.74058
43602.4662 | 1.297 | 1.5343 | 1.438 | 1.072 | 0.94655 | 0.83785 | 0.80143 | 0.74162
43602.4662 | 1.3001 | 1.5363 | 1.4396 | 1.0736 | 0.9462 | 0.8379 | 0.80158 | 0.74197
43602.4663 | 1.2958 | 1.5367 | 1.4392 | 1.0731 | 0.9471 | 0.83849 | 0.80344 | 0.74194
43602.4663 | 1.2929 | 1.5345 | 1.4388 | 1.0719 | 0.94656 | 0.83817 | 0.80155 | 0.74173
43602.4663 | 1.2876 | 1.5364 | 1.4409 | 1.0729 | 0.94499 | 0.83688 | 0.80053 | 0.74091
43602.4663 | 1.2887 | 1.5351 | 1.4398 | 1.0715 | 0.94571 | 0.83749 | 0.80074 | 0.74153
43602.4663 | 1.2977 | 1.5354 | 1.4401 | 1.0724 | 0.94584 | 0.83724 | 0.80192 | 0.74198
43602.4663 | 1.2866 | 1.5332 | 1.4385 | 1.0692 | 0.94445 | 0.83627 | 0.80313 | 0.74118
43602.4663 | 1.2832 | 1.5331 | 1.4392 | 1.0697 | 0.94438 | 0.8367 | 0.80158 | 0.74143
43602.4663 | 1.2925 | 1.5338 | 1.4391 | 1.0703 | 0.94435 | 0.83639 | 0.80054 | 0.74128
43602.4662 | 1.2794 | 1.5281 | 1.4354 | 1.0661 | 0.94283 | 0.83508 | 0.79944 | 0.74076
43602.4665 | 1.2592 | 1.51 | 1.4203 | 1.0522 | 0.93032 | 0.8251 | 0.79078 | 0.73684
43602.4665 | 1.2564 | 1.5067 | 1.4177 | 1.0503 | 0.92956 | 0.8247 | 0.79041 | 0.73721
43602.4665 | 1.2519 | 1.5044 | 1.4161 | 1.048 | 0.92788 | 0.82395 | 0.78916 | 0.73661
43602.4665 | 1.2521 | 1.5021 | 1.4142 | 1.0462 | 0.9263 | 0.82243 | 0.78785 | 0.7366
43602.4665 | 1.2438 | 1.4988 | 1.4111 | 1.0441 | 0.92513 | 0.82148 | 0.78692 | 0.73657
43602.4665 | 1.2497 | 1.4973 | 1.4101 | 1.0429 | 0.92359 | 0.81951 | 0.78906 | 0.73513
43602.4665 | 1.2454 | 1.4955 | 1.4078 | 1.0413 | 0.92205 | 0.81869 | 0.78613 | 0.73464
43602.4665 | 1.2461 | 1.4942 | 1.4076 | 1.0411 | 0.9215 | 0.81831 | 0.78462 | 0.73447
43602.4665 | 1.2433 | 1.4926 | 1.4062 | 1.0394 | 0.92026 | 0.81739 | 0.78296 | 0.73364
43602.4666 | 1.2437 | 1.4903 | 1.4038 | 1.0386 | 0.91921 | 0.8164 | 0.7822 | 0.73351
43602.4664 | 1.243 | 1.4885 | 1.4021 | 1.0362 | 0.91771 | 0.81492 | 0.78148 | 0.73285
43602.4667 | 1.248 | 1.4908 | 1.4033 | 1.0384 | 0.91796 | 0.81469 | 0.78124 | 0.73206
43602.4667 | 1.2526 | 1.4921 | 1.4041 | 1.0394 | 0.91831 | 0.81515 | 0.78113 | 0.73216
43602.4667 | 1.2551 | 1.4953 | 1.4053 | 1.0413 | 0.91922 | 0.81564 | 0.78119 | 0.7321
43602.4667 | 1.2528 | 1.4935 | 1.4054 | 1.0412 | 0.92085 | 0.81683 | 0.78189 | 0.73276
43602.4667 | 1.2571 | 1.4959 | 1.4062 | 1.0419 | 0.92031 | 0.81671 | 0.78236 | 0.73262
43602.4667 | 1.2593 | 1.4987 | 1.4088 | 1.0445 | 0.92182 | 0.81784 | 0.78383 | 0.73284
43602.4667 | 1.2667 | 1.501 | 1.4104 | 1.0461 | 0.92326 | 0.81896 | 0.78377 | 0.7332
43602.4667 | 1.2637 | 1.5005 | 1.4109 | 1.0464 | 0.92401 | 0.81917 | 0.78538 | 0.73301
43602.4668 | 1.2629 | 1.5025 | 1.4126 | 1.0485 | 0.92497 | 0.81995 | 0.78579 | 0.7334
43602.4668 | 1.2623 | 1.5048 | 1.4137 | 1.0497 | 0.92723 | 0.82213 | 0.78751 | 0.73459
43602.4668 | 1.2708 | 1.5044 | 1.4136 | 1.0498 | 0.9269 | 0.82167 | 0.78653 | 0.73413
43602.4667 | 1.2728 | 1.5077 | 1.4156 | 1.0528 | 0.92934 | 0.82351 | 0.79087 | 0.73471
43602.4669 | 1.2772 | 1.5146 | 1.4208 | 1.0587 | 0.93433 | 0.82793 | 0.79177 | 0.73679
43602.4669 | 1.2836 | 1.5155 | 1.4211 | 1.06 | 0.9344 | 0.8282 | 0.79418 | 0.73689
43602.4669 | 1.2841 | 1.5148 | 1.4203 | 1.0599 | 0.93551 | 0.82877 | 0.79538 | 0.73799
43602.4669 | 1.2853 | 1.5152 | 1.4205 | 1.0602 | 0.93571 | 0.829 | 0.79366 | 0.73778
43602.4669 | 1.28 | 1.5157 | 1.4208 | 1.0604 | 0.93564 | 0.82902 | 0.79327 | 0.7378
43602.467 | 1.2854 | 1.5165 | 1.4207 | 1.0606 | 0.93652 | 0.82956 | 0.794 | 0.73833
43602.467 | 1.2863 | 1.5162 | 1.42 | 1.0606 | 0.93553 | 0.82906 | 0.79355 | 0.73809
43602.467 | 1.2765 | 1.5116 | 1.4177 | 1.0585 | 0.93514 | 0.829 | 0.79387 | 0.73793
43602.467 | 1.2804 | 1.5134 | 1.4189 | 1.0589 | 0.93434 | 0.82774 | 0.79458 | 0.73719
43602.467 | 1.2835 | 1.5148 | 1.419 | 1.061 | 0.93531 | 0.82911 | 0.79402 | 0.73835
43602.4669 | 1.2713 | 1.5127 | 1.4177 | 1.0583 | 0.93501 | 0.82918 | 0.79361 | 0.73843
43602.4671 | 1.2645 | 1.5056 | 1.4124 | 1.053 | 0.93142 | 0.82577 | 0.79047 | 0.73677
43602.4671 | 1.2721 | 1.5055 | 1.4107 | 1.0519 | 0.92783 | 0.82331 | 0.79077 | 0.73577
43602.4671 | 1.2732 | 1.5056 | 1.4108 | 1.0521 | 0.92925 | 0.82389 | 0.79079 | 0.73554
43602.4671 | 1.2684 | 1.5016 | 1.4089 | 1.0501 | 0.92829 | 0.82304 | 0.78868 | 0.73583
43602.4672 | 1.2663 | 1.503 | 1.4091 | 1.0508 | 0.9269 | 0.82214 | 0.78752 | 0.7354
43602.4672 | 1.2686 | 1.5016 | 1.4077 | 1.0498 | 0.92769 | 0.82287 | 0.78848 | 0.73617
43602.4672 | 1.2692 | 1.502 | 1.4078 | 1.0491 | 0.92679 | 0.82182 | 0.78714 | 0.73535
43602.4672 | 1.2649 | 1.5026 | 1.4079 | 1.0497 | 0.92673 | 0.82214 | 0.78773 | 0.73571
43602.4672 | 1.2727 | 1.5031 | 1.4078 | 1.0495 | 0.92726 | 0.82194 | 0.7892 | 0.73496
43602.4672 | 1.2641 | 1.4984 | 1.4049 | 1.046 | 0.92545 | 0.82085 | 0.78802 | 0.73471
43602.4671 | 1.2645 | 1.4991 | 1.4047 | 1.0463 | 0.92447 | 0.82008 | 0.78585 | 0.73468
43602.4673 | 1.2556 | 1.4889 | 1.3965 | 1.0395 | 0.91991 | 0.81641 | 0.78257 | 0.73349
43602.4673 | 1.2576 | 1.4872 | 1.3958 | 1.0384 | 0.91793 | 0.81456 | 0.78032 | 0.7322
43602.4674 | 1.2551 | 1.4865 | 1.3956 | 1.0387 | 0.91792 | 0.81448 | 0.78038 | 0.73219
43602.4674 | 1.2514 | 1.4867 | 1.3948 | 1.0384 | 0.91817 | 0.81483 | 0.78114 | 0.73243
43602.4674 | 1.2526 | 1.487 | 1.3947 | 1.0375 | 0.91758 | 0.81438 | 0.78444 | 0.73247
43602.4674 | 1.2486 | 1.4841 | 1.3932 | 1.0362 | 0.91708 | 0.81372 | 0.78131 | 0.73203
43602.4674 | 1.2491 | 1.4836 | 1.3921 | 1.0357 | 0.91616 | 0.81351 | 0.78016 | 0.73203
43602.4674 | 1.2519 | 1.4838 | 1.3925 | 1.0353 | 0.91648 | 0.81355 | 0.78004 | 0.73245
43602.4674 | 1.2436 | 1.4835 | 1.3919 | 1.0362 | 0.91539 | 0.81214 | 0.7786 | 0.73128
43602.4674 | 1.2482 | 1.4808 | 1.3894 | 1.0335 | 0.91484 | 0.81219 | 0.77885 | 0.73153
43602.4673 | 1.2467 | 1.4835 | 1.3921 | 1.0354 | 0.91411 | 0.81153 | 0.77813 | 0.73115
43602.4675 | 1.2471 | 1.4797 | 1.3891 | 1.0319 | 0.91325 | 0.81058 | 0.77732 | 0.73063
43602.4676 | 1.2404 | 1.479 | 1.3888 | 1.0313 | 0.91205 | 0.8103 | 0.77597 | 0.73058
43602.4676 | 1.2482 | 1.4817 | 1.3904 | 1.0336 | 0.91282 | 0.81038 | 0.7762 | 0.73031
43602.4676 | 1.2451 | 1.4809 | 1.39 | 1.0329 | 0.91294 | 0.81041 | 0.77924 | 0.73033
43602.4676 | 1.2441 | 1.48 | 1.3897 | 1.0327 | 0.91269 | 0.81029 | 0.77804 | 0.73045
43602.4676 | 1.248 | 1.4801 | 1.3896 | 1.0325 | 0.91287 | 0.81034 | 0.77674 | 0.7301
43602.4676 | 1.2472 | 1.4821 | 1.3906 | 1.0339 | 0.91289 | 0.81045 | 0.77677 | 0.73032
43602.4676 | 1.2472 | 1.4821 | 1.3907 | 1.0334 | 0.91371 | 0.81106 | 0.77712 | 0.73064
43602.4676 | 1.2425 | 1.4809 | 1.3904 | 1.0327 | 0.91239 | 0.80987 | 0.77785 | 0.72979
43602.4677 | 1.2446 | 1.4796 | 1.3891 | 1.0316 | 0.91238 | 0.81011 | 0.77752 | 0.73002
43602.4675 | 1.2477 | 1.4794 | 1.3887 | 1.0312 | 0.91114 | 0.80878 | 0.77516 | 0.72932
43602.4678 | 1.248 | 1.4795 | 1.3889 | 1.0318 | 0.91069 | 0.80813 | 0.77488 | 0.72892
43602.4678 | 1.2443 | 1.4789 | 1.3888 | 1.0304 | 0.91219 | 0.80924 | 0.77851 | 0.72942
43602.4678 | 1.2446 | 1.4796 | 1.3893 | 1.0312 | 0.91142 | 0.80866 | 0.77548 | 0.72925
43602.4678 | 1.2439 | 1.4804 | 1.3902 | 1.0313 | 0.91154 | 0.8089 | 0.77541 | 0.72889
43602.4678 | 1.2435 | 1.4816 | 1.3922 | 1.0331 | 0.9125 | 0.80983 | 0.7759 | 0.72968
43602.4678 | 1.2459 | 1.4824 | 1.3916 | 1.0328 | 0.91304 | 0.81062 | 0.7773 | 0.72981
43602.4678 | 1.2491 | 1.4838 | 1.3932 | 1.0341 | 0.91289 | 0.80965 | 0.77676 | 0.72885
43602.4678 | 1.2489 | 1.4847 | 1.3928 | 1.0345 | 0.91422 | 0.81099 | 0.7768 | 0.73021
43602.4679 | 1.2527 | 1.488 | 1.3957 | 1.0362 | 0.91518 | 0.81175 | 0.77799 | 0.7302
43602.4679 | 1.2505 | 1.4859 | 1.3954 | 1.0349 | 0.91466 | 0.8113 | 0.77908 | 0.72958
43602.4678 | 1.2497 | 1.4857 | 1.3958 | 1.0349 | 0.91489 | 0.81171 | 0.77788 | 0.72962
43602.468 | 1.2514 | 1.4926 | 1.4028 | 1.0383 | 0.91804 | 0.81393 | 0.77904 | 0.7299
43602.468 | 1.2535 | 1.4938 | 1.4035 | 1.0392 | 0.91775 | 0.81346 | 0.77908 | 0.72971
43602.468 | 1.258 | 1.4947 | 1.4039 | 1.0395 | 0.91848 | 0.81455 | 0.78379 | 0.73057
43602.468 | 1.2565 | 1.4951 | 1.4049 | 1.0392 | 0.9188 | 0.81489 | 0.78143 | 0.73095
43602.468 | 1.2531 | 1.4977 | 1.4063 | 1.0414 | 0.91932 | 0.81542 | 0.78097 | 0.73091
43602.468 | 1.2504 | 1.4951 | 1.4056 | 1.0406 | 0.91994 | 0.81583 | 0.78099 | 0.73108
43602.4681 | 1.2482 | 1.4945 | 1.4051 | 1.0395 | 0.91933 | 0.81501 | 0.78016 | 0.7307
43602.4681 | 1.2516 | 1.4928 | 1.4039 | 1.0389 | 0.91883 | 0.81466 | 0.78085 | 0.73067
43602.4681 | 1.2531 | 1.4941 | 1.4045 | 1.0383 | 0.91762 | 0.81366 | 0.77906 | 0.73013
43602.4681 | 1.2557 | 1.4949 | 1.4038 | 1.0387 | 0.91811 | 0.81398 | 0.78103 | 0.73021
43602.468 | 1.2466 | 1.4925 | 1.403 | 1.0376 | 0.91749 | 0.814 | 0.78146 | 0.73031
43602.4682 | 1.2381 | 1.485 | 1.3965 | 1.0321 | 0.91332 | 0.80977 | 0.77542 | 0.72838
43602.4682 | 1.2388 | 1.4821 | 1.3937 | 1.0285 | 0.91116 | 0.80908 | 0.77538 | 0.72821
43602.4682 | 1.2404 | 1.4811 | 1.3938 | 1.0287 | 0.91096 | 0.80849 | 0.7774 | 0.72811
43602.4682 | 1.2333 | 1.4795 | 1.3923 | 1.0283 | 0.91097 | 0.80854 | 0.77566 | 0.72843
43602.4683 | 1.2366 | 1.4802 | 1.3927 | 1.0277 | 0.90948 | 0.80752 | 0.77387 | 0.7276
43602.4683 | 1.2376 | 1.4797 | 1.3919 | 1.0279 | 0.91044 | 0.80809 | 0.77426 | 0.7283
43602.4683 | 1.2346 | 1.4778 | 1.391 | 1.0265 | 0.90943 | 0.80724 | 0.7734 | 0.7277
43602.4683 | 1.2334 | 1.4781 | 1.3913 | 1.0272 | 0.90981 | 0.80759 | 0.77369 | 0.72838
43602.4683 | 1.2323 | 1.4772 | 1.3904 | 1.0261 | 0.90908 | 0.80727 | 0.77367 | 0.72803
43602.4683 | 1.232 | 1.4754 | 1.3884 | 1.0248 | 0.90823 | 0.80647 | 0.77553 | 0.7279
43602.4682 | 1.2327 | 1.4763 | 1.389 | 1.0252 | 0.90792 | 0.80588 | 0.77253 | 0.72754
43602.4684 | 1.2305 | 1.474 | 1.3878 | 1.0239 | 0.90738 | 0.80504 | 0.77089 | 0.72614
43602.4684 | 1.2251 | 1.4725 | 1.3862 | 1.0228 | 0.90551 | 0.804 | 0.7714 | 0.72581
43602.4685 | 1.2254 | 1.4748 | 1.3876 | 1.0241 | 0.90599 | 0.80397 | 0.77239 | 0.72583
43602.4685 | 1.2306 | 1.4748 | 1.3877 | 1.0243 | 0.90655 | 0.80442 | 0.77103 | 0.72597
43602.4685 | 1.23 | 1.4738 | 1.3871 | 1.0235 | 0.90561 | 0.80382 | 0.76983 | 0.72555
43602.4685 | 1.2367 | 1.4755 | 1.3881 | 1.0242 | 0.90658 | 0.80469 | 0.77149 | 0.72614
43602.4685 | 1.2268 | 1.4728 | 1.3867 | 1.0227 | 0.90605 | 0.80413 | 0.77308 | 0.72574
43602.4685 | 1.2244 | 1.4748 | 1.3881 | 1.0233 | 0.90483 | 0.80327 | 0.77031 | 0.72516
43602.4685 | 1.2308 | 1.4757 | 1.389 | 1.0244 | 0.90659 | 0.80447 | 0.77047 | 0.7259
43602.4685 | 1.2341 | 1.4763 | 1.3889 | 1.0245 | 0.90695 | 0.80468 | 0.77086 | 0.72616
43602.4684 | 1.2291 | 1.4754 | 1.3879 | 1.0241 | 0.90613 | 0.80385 | 0.77185 | 0.72525
43602.4687 | 1.2338 | 1.4781 | 1.3899 | 1.0253 | 0.90701 | 0.80466 | 0.77124 | 0.72597
43602.4687 | 1.2324 | 1.4753 | 1.3889 | 1.0248 | 0.9077 | 0.80522 | 0.77116 | 0.72619
43602.4687 | 1.2344 | 1.4759 | 1.3887 | 1.0243 | 0.90592 | 0.80395 | 0.7708 | 0.72519
43602.4687 | 1.2331 | 1.4768 | 1.3887 | 1.0242 | 0.90671 | 0.80412 | 0.77417 | 0.72521
43602.4687 | 1.2305 | 1.4777 | 1.3901 | 1.0255 | 0.90722 | 0.80484 | 0.77172 | 0.72578
43602.4687 | 1.2288 | 1.4783 | 1.3897 | 1.0247 | 0.90731 | 0.80485 | 0.77109 | 0.72574
43602.4687 | 1.2303 | 1.4765 | 1.389 | 1.0238 | 0.90719 | 0.80484 | 0.77081 | 0.72556
43602.4687 | 1.231 | 1.4784 | 1.3906 | 1.0256 | 0.90663 | 0.80439 | 0.77032 | 0.72533
43602.4687 | 1.2372 | 1.4797 | 1.3919 | 1.0263 | 0.90787 | 0.80523 | 0.7717 | 0.72565
43602.4688 | 1.2358 | 1.4796 | 1.3925 | 1.0269 | 0.90868 | 0.80587 | 0.7716 | 0.72595
43602.4686 | 1.2372 | 1.481 | 1.3924 | 1.0273 | 0.90882 | 0.80592 | 0.77441 | 0.72585
43602.4689 | 1.2346 | 1.4799 | 1.3924 | 1.0261 | 0.9101 | 0.80705 | 0.776 | 0.72681
43602.4689 | 1.2352 | 1.4798 | 1.3921 | 1.0265 | 0.90839 | 0.8056 | 0.77248 | 0.72608
43602.4689 | 1.2324 | 1.4799 | 1.3914 | 1.0255 | 0.90862 | 0.80611 | 0.77235 | 0.72659
43602.4689 | 1.2365 | 1.4796 | 1.3911 | 1.0255 | 0.90775 | 0.80505 | 0.771 | 0.72547
43602.4689 | 1.2302 | 1.4788 | 1.3913 | 1.0253 | 0.90781 | 0.80526 | 0.77128 | 0.72568
43602.4689 | 1.2268 | 1.4773 | 1.3905 | 1.0241 | 0.90865 | 0.80574 | 0.7737 | 0.72651
43602.4689 | 1.2316 | 1.4776 | 1.3906 | 1.025 | 0.90759 | 0.80508 | 0.77165 | 0.72613
43602.4689 | 1.2315 | 1.4788 | 1.3912 | 1.0252 | 0.90857 | 0.80624 | 0.77211 | 0.72682
43602.469 | 1.2375 | 1.4789 | 1.39 | 1.0253 | 0.90786 | 0.80528 | 0.77093 | 0.72608
43602.469 | 1.2328 | 1.477 | 1.3892 | 1.0237 | 0.90765 | 0.80477 | 0.77378 | 0.72616
43602.4689 | 1.2258 | 1.4767 | 1.3897 | 1.0243 | 0.90701 | 0.80464 | 0.77217 | 0.72611
43602.4691 | 1.2303 | 1.4728 | 1.3856 | 1.0212 | 0.90494 | 0.80318 | 0.77207 | 0.7254
43602.4691 | 1.2232 | 1.4718 | 1.3858 | 1.0211 | 0.90538 | 0.80365 | 0.7704 | 0.72601
43602.4691 | 1.2318 | 1.4716 | 1.3845 | 1.0208 | 0.90369 | 0.80275 | 0.76919 | 0.72517
43602.4691 | 1.2279 | 1.4728 | 1.3846 | 1.0209 | 0.90474 | 0.80333 | 0.76943 | 0.72548
43602.4691 | 1.2278 | 1.4712 | 1.3833 | 1.0202 | 0.90473 | 0.80318 | 0.7705 | 0.72602
43602.4691 | 1.2213 | 1.4681 | 1.3818 | 1.0188 | 0.90382 | 0.80257 | 0.77194 | 0.72571
43602.4692 | 1.2245 | 1.4675 | 1.3809 | 1.0177 | 0.9025 | 0.80133 | 0.76898 | 0.72511
43602.4692 | 1.225 | 1.4656 | 1.3788 | 1.0166 | 0.90186 | 0.80042 | 0.7675 | 0.72453
43602.4692 | 1.2222 | 1.4655 | 1.379 | 1.0171 | 0.90083 | 0.80003 | 0.76698 | 0.72456
43602.4692 | 1.224 | 1.4644 | 1.3784 | 1.0167 | 0.90179 | 0.80098 | 0.76776 | 0.72537
43602.4691 | 1.2162 | 1.4637 | 1.378 | 1.0166 | 0.90106 | 0.80048 | 0.76714 | 0.7249
43602.4693 | 1.2203 | 1.4652 | 1.3782 | 1.0182 | 0.90101 | 0.79998 | 0.76707 | 0.72502
43602.4693 | 1.2276 | 1.4673 | 1.3789 | 1.0184 | 0.90166 | 0.80019 | 0.76681 | 0.72444
43602.4693 | 1.2312 | 1.468 | 1.3803 | 1.0201 | 0.90252 | 0.80145 | 0.76769 | 0.72502
43602.4693 | 1.2256 | 1.4685 | 1.3811 | 1.0202 | 0.90382 | 0.80203 | 0.76858 | 0.72525
43602.4694 | 1.2304 | 1.4719 | 1.3834 | 1.0218 | 0.9036 | 0.80184 | 0.76835 | 0.7252
43602.4694 | 1.2317 | 1.4745 | 1.3854 | 1.0233 | 0.90589 | 0.8043 | 0.77155 | 0.72636
43602.4694 | 1.2341 | 1.475 | 1.3857 | 1.0234 | 0.9065 | 0.80454 | 0.77213 | 0.72638
43602.4694 | 1.2355 | 1.4779 | 1.3872 | 1.0249 | 0.90683 | 0.8048 | 0.77101 | 0.72669
43602.4694 | 1.2392 | 1.4783 | 1.3885 | 1.0252 | 0.90839 | 0.80624 | 0.77246 | 0.72753
43602.4694 | 1.2347 | 1.479 | 1.3891 | 1.0256 | 0.90832 | 0.8057 | 0.77292 | 0.72633
43602.4693 | 1.2401 | 1.4819 | 1.3908 | 1.0278 | 0.90948 | 0.80648 | 0.77476 | 0.72717
43602.4695 | 1.2381 | 1.4816 | 1.3899 | 1.0277 | 0.91016 | 0.80753 | 0.77591 | 0.72809
43602.4695 | 1.2395 | 1.4813 | 1.3901 | 1.0273 | 0.90992 | 0.80703 | 0.77378 | 0.72802
43602.4696 | 1.2358 | 1.4842 | 1.3923 | 1.0289 | 0.90983 | 0.80714 | 0.77302 | 0.72823
43602.4696 | 1.2374 | 1.4821 | 1.3902 | 1.0262 | 0.91062 | 0.80752 | 0.77308 | 0.72786
43602.4696 | 1.2389 | 1.4826 | 1.3906 | 1.0266 | 0.90883 | 0.80593 | 0.77224 | 0.72706
43602.4696 | 1.2395 | 1.4826 | 1.3914 | 1.0272 | 0.90947 | 0.80677 | 0.77553 | 0.728
43602.4696 | 1.2356 | 1.4837 | 1.3927 | 1.0285 | 0.91053 | 0.80731 | 0.77375 | 0.72768
43602.4696 | 1.2358 | 1.4847 | 1.3931 | 1.0284 | 0.91064 | 0.80778 | 0.77408 | 0.72759
43602.4696 | 1.2448 | 1.4833 | 1.3925 | 1.0281 | 0.91077 | 0.80826 | 0.77408 | 0.72805
43602.4695 | 1.2432 | 1.485 | 1.3932 | 1.0285 | 0.91109 | 0.80784 | 0.77423 | 0.72783
43602.4697 | 1.2333 | 1.4816 | 1.3915 | 1.0264 | 0.90937 | 0.80723 | 0.77547 | 0.7277
43602.4698 | 1.2364 | 1.4806 | 1.3907 | 1.0261 | 0.90919 | 0.80696 | 0.77398 | 0.72781
43602.4698 | 1.2381 | 1.4813 | 1.391 | 1.0254 | 0.90896 | 0.80668 | 0.77282 | 0.72766
43602.4698 | 1.2372 | 1.4814 | 1.3912 | 1.027 | 0.90825 | 0.80588 | 0.77161 | 0.7269
43602.4698 | 1.2303 | 1.4799 | 1.3907 | 1.0257 | 0.90915 | 0.80655 | 0.77472 | 0.72709
43602.4698 | 1.2344 | 1.4812 | 1.3913 | 1.0258 | 0.90817 | 0.80626 | 0.77392 | 0.72691
43602.4698 | 1.2388 | 1.4827 | 1.3918 | 1.027 | 0.90878 | 0.80643 | 0.77314 | 0.72716
43602.4698 | 1.2343 | 1.4799 | 1.3899 | 1.0247 | 0.90892 | 0.80633 | 0.77223 | 0.72671
43602.4698 | 1.2307 | 1.4802 | 1.3906 | 1.0251 | 0.90852 | 0.80633 | 0.77196 | 0.72677
43602.4697 | 1.2344 | 1.4787 | 1.3889 | 1.0237 | 0.90767 | 0.80569 | 0.77322 | 0.72668
43602.47 | 1.2253 | 1.4711 | 1.3824 | 1.0188 | 0.9044 | 0.80322 | 0.76951 | 0.72621
43602.47 | 1.2253 | 1.4714 | 1.382 | 1.0198 | 0.90394 | 0.80259 | 0.76884 | 0.72592
43602.47 | 1.2198 | 1.4696 | 1.3799 | 1.017 | 0.90275 | 0.80193 | 0.77024 | 0.72572
43602.47 | 1.2249 | 1.4693 | 1.3806 | 1.0174 | 0.90233 | 0.80083 | 0.76768 | 0.72484
43602.47 | 1.2251 | 1.4679 | 1.379 | 1.016 | 0.90175 | 0.80082 | 0.76757 | 0.72498
43602.47 | 1.2188 | 1.466 | 1.3779 | 1.0155 | 0.90136 | 0.80041 | 0.76748 | 0.72501
43602.47 | 1.2145 | 1.4648 | 1.3781 | 1.0155 | 0.90091 | 0.80008 | 0.7676 | 0.72471
43602.47 | 1.2177 | 1.4647 | 1.3773 | 1.0149 | 0.90029 | 0.79961 | 0.76737 | 0.72444
43602.47 | 1.2215 | 1.4639 | 1.3751 | 1.0135 | 0.89871 | 0.79873 | 0.76875 | 0.72402
43602.4701 | 1.2161 | 1.4624 | 1.3749 | 1.0128 | 0.89815 | 0.79819 | 0.7658 | 0.72376
43602.4699 | 1.2203 | 1.4584 | 1.3705 | 1.0112 | 0.89623 | 0.7964 | 0.7637 | 0.7233
43602.4702 | 1.2193 | 1.4565 | 1.3677 | 1.0098 | 0.89528 | 0.79578 | 0.76371 | 0.7235
43602.4702 | 1.215 | 1.4538 | 1.3656 | 1.0082 | 0.89472 | 0.79524 | 0.76286 | 0.72317
43602.4702 | 1.2184 | 1.4544 | 1.3665 | 1.0087 | 0.89418 | 0.79504 | 0.7619 | 0.72306
43602.4702 | 1.2141 | 1.4537 | 1.3665 | 1.0087 | 0.89445 | 0.79512 | 0.76234 | 0.72316
43602.4702 | 1.2162 | 1.4546 | 1.3663 | 1.0094 | 0.89497 | 0.79543 | 0.76583 | 0.7232
43602.4702 | 1.2154 | 1.4535 | 1.3653 | 1.0085 | 0.8945 | 0.79546 | 0.76379 | 0.72351
43602.4702 | 1.2135 | 1.4518 | 1.3646 | 1.0078 | 0.89388 | 0.79454 | 0.76216 | 0.72272
43602.4703 | 1.2166 | 1.4531 | 1.3649 | 1.0087 | 0.89337 | 0.7941 | 0.76146 | 0.72265
43602.4703 | 1.2121 | 1.4524 | 1.3643 | 1.0082 | 0.89418 | 0.79455 | 0.76195 | 0.72289
43602.4702 | 1.2144 | 1.451 | 1.3623 | 1.0068 | 0.8928 | 0.794 | 0.76272 | 0.72318
43602.4704 | 1.2112 | 1.448 | 1.3603 | 1.0062 | 0.89214 | 0.79308 | 0.76296 | 0.72264
43602.4704 | 1.2193 | 1.4524 | 1.3635 | 1.0093 | 0.89333 | 0.79378 | 0.76185 | 0.72298
43602.4704 | 1.2206 | 1.4533 | 1.3645 | 1.0101 | 0.89512 | 0.79555 | 0.76349 | 0.72413
43602.4704 | 1.2228 | 1.4558 | 1.3662 | 1.0118 | 0.89459 | 0.79481 | 0.76223 | 0.72291
43602.4704 | 1.2293 | 1.4572 | 1.3679 | 1.0134 | 0.89717 | 0.79736 | 0.76685 | 0.7245
43602.4704 | 1.2309 | 1.4595 | 1.3696 | 1.0145 | 0.89762 | 0.79754 | 0.76594 | 0.724
43602.4705 | 1.2318 | 1.4622 | 1.3721 | 1.0169 | 0.89862 | 0.79781 | 0.76511 | 0.72394
43602.4705 | 1.2331 | 1.4655 | 1.375 | 1.0189 | 0.90077 | 0.80008 | 0.7668 | 0.72536
43602.4705 | 1.2385 | 1.4676 | 1.377 | 1.0203 | 0.90251 | 0.8013 | 0.76926 | 0.72557
43602.4704 | 1.2409 | 1.4756 | 1.3843 | 1.0264 | 0.90815 | 0.80557 | 0.77315 | 0.72757
43602.4706 | 1.2555 | 1.4909 | 1.3976 | 1.0355 | 0.91587 | 0.81137 | 0.77732 | 0.7293
43602.4706 | 1.2541 | 1.4917 | 1.398 | 1.036 | 0.91623 | 0.81273 | 0.77775 | 0.7298
43602.4706 | 1.2582 | 1.492 | 1.3979 | 1.035 | 0.91634 | 0.81224 | 0.77961 | 0.73012
43602.4706 | 1.2581 | 1.4947 | 1.4002 | 1.0371 | 0.91658 | 0.81272 | 0.78019 | 0.73004
43602.4706 | 1.2539 | 1.496 | 1.4022 | 1.0382 | 0.91788 | 0.81388 | 0.77916 | 0.73004
43602.4706 | 1.254 | 1.4965 | 1.4028 | 1.0383 | 0.91887 | 0.81458 | 0.77941 | 0.73038
43602.4707 | 1.2548 | 1.4983 | 1.404 | 1.0394 | 0.91849 | 0.8142 | 0.77923 | 0.73027
43602.4707 | 1.2575 | 1.4981 | 1.4036 | 1.0389 | 0.91956 | 0.81527 | 0.78035 | 0.73092
43602.4707 | 1.2615 | 1.5014 | 1.4066 | 1.0408 | 0.92009 | 0.81541 | 0.7824 | 0.73061
43602.4706 | 1.262 | 1.5044 | 1.4096 | 1.0415 | 0.92134 | 0.81667 | 0.78188 | 0.73122
43602.4708 | 1.2526 | 1.508 | 1.414 | 1.043 | 0.92288 | 0.81725 | 0.78167 | 0.73109
43602.4708 | 1.2501 | 1.5074 | 1.4136 | 1.0418 | 0.92198 | 0.81703 | 0.78163 | 0.73095
43602.4708 | 1.2562 | 1.5058 | 1.412 | 1.0403 | 0.92179 | 0.81678 | 0.78138 | 0.73099
43602.4708 | 1.2513 | 1.506 | 1.4132 | 1.0407 | 0.92203 | 0.81688 | 0.78345 | 0.73127
43602.4708 | 1.2555 | 1.5061 | 1.4131 | 1.0406 | 0.92155 | 0.81628 | 0.78304 | 0.73055
43602.4709 | 1.2576 | 1.5085 | 1.4145 | 1.0417 | 0.92173 | 0.81649 | 0.78146 | 0.73058
43602.4709 | 1.2538 | 1.5068 | 1.4132 | 1.0406 | 0.92247 | 0.81698 | 0.78154 | 0.73101
43602.4709 | 1.2483 | 1.5065 | 1.4136 | 1.0401 | 0.921 | 0.81605 | 0.78053 | 0.73033
43602.4709 | 1.2539 | 1.5077 | 1.4148 | 1.0408 | 0.92187 | 0.81654 | 0.78113 | 0.73079
43602.4709 | 1.2517 | 1.5074 | 1.4147 | 1.0409 | 0.9222 | 0.81652 | 0.78267 | 0.73071
43602.4708 | 1.2484 | 1.5061 | 1.4135 | 1.039 | 0.92022 | 0.81527 | 0.78194 | 0.73022
43602.471 | 1.2475 | 1.5035 | 1.4121 | 1.0365 | 0.92047 | 0.81554 | 0.78041 | 0.7306
43602.471 | 1.2413 | 1.5015 | 1.4106 | 1.0341 | 0.91904 | 0.81449 | 0.77936 | 0.73004
43602.4711 | 1.2418 | 1.5016 | 1.411 | 1.0342 | 0.91806 | 0.81358 | 0.78121 | 0.72925
43602.4711 | 1.2423 | 1.501 | 1.4103 | 1.0341 | 0.91779 | 0.8135 | 0.77926 | 0.72934
43602.4711 | 1.2376 | 1.5 | 1.4097 | 1.0327 | 0.91725 | 0.813 | 0.77808 | 0.72908
43602.4711 | 1.2356 | 1.4975 | 1.4075 | 1.0318 | 0.9167 | 0.81213 | 0.77706 | 0.72892
43602.4711 | 1.2341 | 1.4962 | 1.4057 | 1.0304 | 0.91553 | 0.81138 | 0.77712 | 0.72866
43602.4711 | 1.2435 | 1.4958 | 1.4056 | 1.0306 | 0.9148 | 0.81083 | 0.7762 | 0.7282
43602.4711 | 1.2275 | 1.4926 | 1.4035 | 1.0279 | 0.91369 | 0.81003 | 0.77577 | 0.72769
43602.471 | 1.2327 | 1.4907 | 1.4018 | 1.0262 | 0.91017 | 0.80708 | 0.77554 | 0.72634
43602.4712 | 1.2294 | 1.4874 | 1.3996 | 1.0233 | 0.90942 | 0.80597 | 0.77136 | 0.72574
43602.4713 | 1.2235 | 1.4862 | 1.3988 | 1.0226 | 0.90904 | 0.80594 | 0.7715 | 0.72527
43602.4713 | 1.2246 | 1.4863 | 1.3989 | 1.0218 | 0.9078 | 0.80492 | 0.77345 | 0.72491
43602.4713 | 1.2267 | 1.4872 | 1.3998 | 1.0228 | 0.90834 | 0.8054 | 0.77188 | 0.72518
43602.4713 | 1.2218 | 1.4859 | 1.3989 | 1.0219 | 0.90883 | 0.80564 | 0.77146 | 0.72523
43602.4713 | 1.2284 | 1.4866 | 1.3994 | 1.0221 | 0.90863 | 0.80534 | 0.77103 | 0.72521
43602.4713 | 1.2244 | 1.487 | 1.3996 | 1.0227 | 0.90867 | 0.80512 | 0.77052 | 0.72496
43602.4713 | 1.225 | 1.4864 | 1.3989 | 1.0219 | 0.90864 | 0.80538 | 0.77296 | 0.72512
43602.4713 | 1.2263 | 1.4879 | 1.4005 | 1.0231 | 0.90877 | 0.80513 | 0.77182 | 0.72508
43602.4712 | 1.2262 | 1.4903 | 1.403 | 1.0245 | 0.91018 | 0.80668 | 0.77268 | 0.72539
43602.4715 | 1.2332 | 1.4989 | 1.4099 | 1.0293 | 0.91439 | 0.80986 | 0.77484 | 0.72627
43602.4715 | 1.23 | 1.4977 | 1.4088 | 1.0284 | 0.91348 | 0.80917 | 0.77398 | 0.7257
43602.4715 | 1.2327 | 1.4984 | 1.4104 | 1.0288 | 0.91383 | 0.80938 | 0.77663 | 0.72566
43602.4715 | 1.2334 | 1.5008 | 1.4123 | 1.0307 | 0.91418 | 0.80995 | 0.77609 | 0.72598
43602.4715 | 1.2312 | 1.5018 | 1.4133 | 1.0312 | 0.91535 | 0.81095 | 0.7757 | 0.7262
43602.4715 | 1.2351 | 1.5038 | 1.4144 | 1.0321 | 0.91602 | 0.8111 | 0.776 | 0.72618
43602.4715 | 1.2344 | 1.5055 | 1.4159 | 1.034 | 0.91695 | 0.81159 | 0.77613 | 0.72637
43602.4715 | 1.2409 | 1.5067 | 1.4165 | 1.034 | 0.91801 | 0.81246 | 0.77697 | 0.72657
43602.4715 | 1.2363 | 1.5072 | 1.4183 | 1.0352 | 0.9187 | 0.81302 | 0.77843 | 0.72676
43602.4714 | 1.2492 | 1.5136 | 1.4223 | 1.0392 | 0.92114 | 0.81487 | 0.77893 | 0.7274
43602.4717 | 1.2521 | 1.5206 | 1.4291 | 1.0432 | 0.92654 | 0.8194 | 0.78351 | 0.72917
43602.4717 | 1.2544 | 1.5229 | 1.4304 | 1.0441 | 0.92605 | 0.81883 | 0.78221 | 0.72873
43602.4717 | 1.2556 | 1.5235 | 1.4317 | 1.0448 | 0.92754 | 0.81986 | 0.78348 | 0.72903
43602.4717 | 1.2545 | 1.5242 | 1.4323 | 1.0449 | 0.92739 | 0.82 | 0.78318 | 0.72876
43602.4717 | 1.2592 | 1.5259 | 1.4336 | 1.0462 | 0.92801 | 0.82054 | 0.78378 | 0.72883
43602.4717 | 1.2549 | 1.5272 | 1.4347 | 1.047 | 0.92849 | 0.82147 | 0.78723 | 0.72947
43602.4717 | 1.2613 | 1.5296 | 1.4363 | 1.0481 | 0.92907 | 0.82177 | 0.78633 | 0.72984
43602.4717 | 1.2635 | 1.5291 | 1.4359 | 1.0485 | 0.93063 | 0.8222 | 0.78548 | 0.73016
43602.4718 | 1.2578 | 1.5293 | 1.4363 | 1.0486 | 0.9305 | 0.82221 | 0.78537 | 0.72977
43602.4716 | 1.2587 | 1.5334 | 1.4398 | 1.051 | 0.93245 | 0.8242 | 0.78715 | 0.73081
43602.4719 | 1.269 | 1.542 | 1.4464 | 1.056 | 0.93714 | 0.82752 | 0.79165 | 0.73152
43602.4719 | 1.2696 | 1.5425 | 1.4485 | 1.0571 | 0.93711 | 0.82777 | 0.7907 | 0.73181
43602.4719 | 1.2727 | 1.545 | 1.4495 | 1.0584 | 0.93815 | 0.8291 | 0.79111 | 0.7324
43602.4719 | 1.2713 | 1.5454 | 1.4499 | 1.0581 | 0.93886 | 0.8295 | 0.79147 | 0.73236
43602.4719 | 1.2702 | 1.5458 | 1.451 | 1.0598 | 0.93898 | 0.82947 | 0.79171 | 0.73254
43602.4719 | 1.2742 | 1.5451 | 1.45 | 1.0581 | 0.93891 | 0.8292 | 0.79383 | 0.73225
43602.4719 | 1.2683 | 1.5447 | 1.4501 | 1.0579 | 0.93858 | 0.82912 | 0.79245 | 0.73219
43602.472 | 1.2673 | 1.5446 | 1.4509 | 1.0573 | 0.93867 | 0.82974 | 0.79214 | 0.73263
43602.472 | 1.2701 | 1.5447 | 1.4505 | 1.0582 | 0.93923 | 0.82958 | 0.79185 | 0.73284
43602.4719 | 1.2745 | 1.5453 | 1.4497 | 1.058 | 0.9387 | 0.82918 | 0.79141 | 0.73241
43602.4721 | 1.2708 | 1.5456 | 1.4507 | 1.0577 | 0.93885 | 0.83006 | 0.79564 | 0.73328
43602.4721 | 1.2679 | 1.5444 | 1.4501 | 1.0564 | 0.93879 | 0.82943 | 0.79229 | 0.73266
43602.4721 | 1.2648 | 1.5431 | 1.4492 | 1.0573 | 0.93859 | 0.82935 | 0.79223 | 0.73287
43602.4721 | 1.2741 | 1.5462 | 1.4513 | 1.0585 | 0.93868 | 0.82943 | 0.79219 | 0.73247
43602.4721 | 1.2737 | 1.546 | 1.4511 | 1.058 | 0.9396 | 0.83014 | 0.79264 | 0.7329
43602.4721 | 1.2737 | 1.5472 | 1.452 | 1.059 | 0.9403 | 0.83054 | 0.79296 | 0.73338
43602.4722 | 1.2788 | 1.5482 | 1.4533 | 1.0597 | 0.94014 | 0.83093 | 0.79348 | 0.73332
43602.4722 | 1.2743 | 1.5493 | 1.4538 | 1.0604 | 0.94158 | 0.83202 | 0.79611 | 0.73372
43602.4721 | 1.2779 | 1.5512 | 1.455 | 1.0611 | 0.942 | 0.83229 | 0.79468 | 0.73394
43602.4723 | 1.2921 | 1.5656 | 1.4684 | 1.0709 | 0.94989 | 0.8385 | 0.79912 | 0.73604
43602.4723 | 1.2883 | 1.5662 | 1.4691 | 1.0718 | 0.9516 | 0.83967 | 0.80331 | 0.73696
43602.4723 | 1.2875 | 1.5666 | 1.4703 | 1.0719 | 0.95188 | 0.84001 | 0.8017 | 0.73655
43602.4723 | 1.2811 | 1.567 | 1.4708 | 1.0717 | 0.95147 | 0.84017 | 0.80144 | 0.73669
43602.4723 | 1.2896 | 1.5684 | 1.4717 | 1.0727 | 0.95221 | 0.84065 | 0.80154 | 0.73701
43602.4723 | 1.2946 | 1.5698 | 1.4726 | 1.0735 | 0.95298 | 0.84101 | 0.80165 | 0.73722
43602.4723 | 1.2911 | 1.5716 | 1.4743 | 1.075 | 0.95412 | 0.84183 | 0.80321 | 0.73752
43602.4724 | 1.3018 | 1.5725 | 1.4748 | 1.0749 | 0.95435 | 0.84192 | 0.80281 | 0.73768
43602.4723 | 1.2977 | 1.5753 | 1.4774 | 1.0784 | 0.95604 | 0.84353 | 0.80725 | 0.73845
43602.4725 | 1.31 | 1.5878 | 1.4883 | 1.0861 | 0.96302 | 0.84946 | 0.80906 | 0.74082
43602.4725 | 1.3031 | 1.5885 | 1.4891 | 1.0868 | 0.96499 | 0.85124 | 0.81394 | 0.7421
43602.4725 | 1.3151 | 1.5901 | 1.4894 | 1.0869 | 0.9654 | 0.85143 | 0.81257 | 0.74204
43602.4725 | 1.3082 | 1.5898 | 1.4902 | 1.0871 | 0.96471 | 0.85091 | 0.81115 | 0.74145
43602.4725 | 1.311 | 1.5891 | 1.4898 | 1.0871 | 0.9656 | 0.85175 | 0.81141 | 0.74197
43602.4725 | 1.3111 | 1.5901 | 1.4898 | 1.0873 | 0.96553 | 0.8516 | 0.81157 | 0.74173
43602.4725 | 1.3086 | 1.5912 | 1.4919 | 1.0882 | 0.96624 | 0.85218 | 0.81179 | 0.74248
43602.4726 | 1.3104 | 1.5914 | 1.4915 | 1.0886 | 0.96652 | 0.85289 | 0.81346 | 0.74226
43602.4726 | 1.3138 | 1.5924 | 1.4926 | 1.0897 | 0.96682 | 0.85293 | 0.81524 | 0.7428
43602.4725 | 1.3115 | 1.5922 | 1.4921 | 1.0887 | 0.96698 | 0.85314 | 0.81314 | 0.74272
43602.4727 | 1.3054 | 1.5913 | 1.4916 | 1.0888 | 0.96711 | 0.85332 | 0.8131 | 0.74353
43602.4727 | 1.31 | 1.5925 | 1.4921 | 1.0896 | 0.96814 | 0.85381 | 0.81575 | 0.74366
43602.4727 | 1.3154 | 1.5934 | 1.4919 | 1.0899 | 0.96826 | 0.85413 | 0.81534 | 0.74389
43602.4727 | 1.3134 | 1.5927 | 1.4925 | 1.0903 | 0.9681 | 0.85408 | 0.81423 | 0.74394
43602.4727 | 1.3144 | 1.5928 | 1.4927 | 1.0902 | 0.96865 | 0.85426 | 0.81444 | 0.74413
43602.4727 | 1.3198 | 1.5948 | 1.4934 | 1.0912 | 0.96911 | 0.85477 | 0.81467 | 0.74443
43602.4728 | 1.3081 | 1.5933 | 1.4933 | 1.0905 | 0.96887 | 0.85454 | 0.81427 | 0.74385
43602.4728 | 1.3116 | 1.5937 | 1.4928 | 1.0902 | 0.9684 | 0.85464 | 0.81486 | 0.74391
43602.4727 | 1.3195 | 1.5939 | 1.4923 | 1.0902 | 0.96878 | 0.85471 | 0.81722 | 0.7444
43602.4729 | 1.3207 | 1.5955 | 1.4942 | 1.0925 | 0.97029 | 0.85614 | 0.81588 | 0.74521
43602.4729 | 1.3176 | 1.5945 | 1.4941 | 1.0916 | 0.9705 | 0.85641 | 0.81905 | 0.74537
43602.4729 | 1.3164 | 1.596 | 1.4948 | 1.0927 | 0.96969 | 0.85601 | 0.81693 | 0.74483
43602.4729 | 1.321 | 1.5957 | 1.4949 | 1.0928 | 0.97109 | 0.85643 | 0.81675 | 0.74547
43602.4729 | 1.3194 | 1.5953 | 1.4945 | 1.0928 | 0.97083 | 0.8569 | 0.81652 | 0.74558
43602.4729 | 1.3173 | 1.5969 | 1.4962 | 1.0933 | 0.97108 | 0.8572 | 0.81637 | 0.74574
43602.4729 | 1.3233 | 1.5981 | 1.4971 | 1.0946 | 0.972 | 0.85777 | 0.81693 | 0.7461
43602.473 | 1.3229 | 1.6003 | 1.498 | 1.0955 | 0.97299 | 0.8583 | 0.81864 | 0.74609
43602.4729 | 1.3334 | 1.6004 | 1.4975 | 1.0963 | 0.97303 | 0.85897 | 0.82041 | 0.7462
43602.4731 | 1.3222 | 1.5997 | 1.4978 | 1.0965 | 0.97388 | 0.85955 | 0.81795 | 0.74669
43602.4731 | 1.3241 | 1.599 | 1.4972 | 1.0964 | 0.97422 | 0.85967 | 0.81965 | 0.74734
43602.4731 | 1.3279 | 1.5985 | 1.4967 | 1.0957 | 0.97378 | 0.85954 | 0.81884 | 0.74741
43602.4731 | 1.325 | 1.5982 | 1.4963 | 1.0957 | 0.97329 | 0.85918 | 0.81883 | 0.74694
43602.4731 | 1.3269 | 1.5981 | 1.4952 | 1.0961 | 0.97293 | 0.85885 | 0.81802 | 0.74723
43602.4731 | 1.3279 | 1.5981 | 1.4947 | 1.0949 | 0.9732 | 0.85834 | 0.8174 | 0.74654
43602.4731 | 1.3283 | 1.5976 | 1.4944 | 1.0951 | 0.97312 | 0.85838 | 0.82078 | 0.7469
43602.4732 | 1.3194 | 1.5969 | 1.4944 | 1.0951 | 0.97254 | 0.85868 | 0.81943 | 0.74701
43602.4731 | 1.3317 | 1.5982 | 1.494 | 1.0955 | 0.9729 | 0.85914 | 0.81909 | 0.74765
43602.4733 | 1.3332 | 1.6 | 1.4957 | 1.0977 | 0.97499 | 0.86003 | 0.81926 | 0.74817
43602.4733 | 1.3293 | 1.6 | 1.4958 | 1.098 | 0.97471 | 0.86043 | 0.82173 | 0.74835
43602.4733 | 1.3358 | 1.5991 | 1.4953 | 1.0985 | 0.97585 | 0.86064 | 0.82057 | 0.74825
43602.4733 | 1.3324 | 1.5995 | 1.4952 | 1.0975 | 0.97432 | 0.8599 | 0.81955 | 0.74834
43602.4733 | 1.334 | 1.5999 | 1.496 | 1.0985 | 0.97465 | 0.86036 | 0.81943 | 0.74816
43602.4733 | 1.3321 | 1.5995 | 1.4963 | 1.0985 | 0.97532 | 0.86049 | 0.81879 | 0.74762
43602.4733 | 1.3355 | 1.6003 | 1.4958 | 1.0984 | 0.97512 | 0.86056 | 0.82008 | 0.74808
43602.4734 | 1.3367 | 1.6027 | 1.497 | 1.0994 | 0.97514 | 0.86081 | 0.82198 | 0.74789
43602.4733 | 1.3298 | 1.6018 | 1.4968 | 1.1003 | 0.97623 | 0.86149 | 0.82086 | 0.74821
43602.4735 | 1.3357 | 1.6041 | 1.4984 | 1.1029 | 0.97717 | 0.86241 | 0.8226 | 0.74891
43602.4735 | 1.3369 | 1.6033 | 1.4971 | 1.1015 | 0.97702 | 0.8623 | 0.82104 | 0.74842
43602.4735 | 1.34 | 1.6035 | 1.4961 | 1.1009 | 0.97685 | 0.86165 | 0.8209 | 0.74839
43602.4735 | 1.3398 | 1.6031 | 1.4958 | 1.1004 | 0.97625 | 0.86159 | 0.82049 | 0.7486
43602.4735 | 1.3321 | 1.6028 | 1.495 | 1.1001 | 0.97568 | 0.86149 | 0.82233 | 0.74842
43602.4735 | 1.3396 | 1.6038 | 1.4942 | 1.0999 | 0.97495 | 0.86063 | 0.82004 | 0.74819
43602.4735 | 1.3313 | 1.6015 | 1.4936 | 1.0991 | 0.97518 | 0.86077 | 0.81978 | 0.74823
43602.4736 | 1.3345 | 1.5995 | 1.4915 | 1.0982 | 0.9742 | 0.85994 | 0.81865 | 0.74787
43602.4735 | 1.3368 | 1.596 | 1.4892 | 1.0963 | 0.97237 | 0.85848 | 0.81868 | 0.7474
43602.4737 | 1.3239 | 1.5844 | 1.4794 | 1.0892 | 0.967 | 0.85413 | 0.81415 | 0.74569
43602.4737 | 1.3268 | 1.5839 | 1.4792 | 1.0893 | 0.9659 | 0.85349 | 0.81255 | 0.74557
43602.4737 | 1.3231 | 1.5838 | 1.4787 | 1.0892 | 0.96613 | 0.8531 | 0.81306 | 0.74527
43602.4737 | 1.3231 | 1.5827 | 1.4777 | 1.0888 | 0.96546 | 0.8525 | 0.81507 | 0.74531
43602.4737 | 1.3192 | 1.5805 | 1.4763 | 1.0873 | 0.9642 | 0.8516 | 0.81314 | 0.74465
43602.4737 | 1.3224 | 1.5829 | 1.4778 | 1.0894 | 0.96474 | 0.85206 | 0.81218 | 0.7448
43602.4737 | 1.3242 | 1.5832 | 1.4777 | 1.0889 | 0.96594 | 0.85312 | 0.81268 | 0.7453
43602.4737 | 1.3202 | 1.5813 | 1.477 | 1.0877 | 0.9645 | 0.85218 | 0.8117 | 0.74489
43602.4737 | 1.3283 | 1.5849 | 1.4776 | 1.0894 | 0.9652 | 0.85241 | 0.81213 | 0.74521
43602.4739 | 1.324 | 1.5859 | 1.4781 | 1.0907 | 0.96547 | 0.85279 | 0.81299 | 0.74542
43602.4739 | 1.318 | 1.5842 | 1.4765 | 1.0891 | 0.96581 | 0.85298 | 0.81186 | 0.74508
43602.4739 | 1.3302 | 1.5886 | 1.4784 | 1.0914 | 0.96568 | 0.85241 | 0.81323 | 0.74526
43602.4739 | 1.3273 | 1.5877 | 1.4783 | 1.0914 | 0.96625 | 0.85325 | 0.81481 | 0.74571
43602.4739 | 1.3321 | 1.5867 | 1.478 | 1.0912 | 0.96568 | 0.85307 | 0.81281 | 0.74529
43602.4739 | 1.3324 | 1.5863 | 1.4779 | 1.0914 | 0.96697 | 0.85399 | 0.81396 | 0.74606
43602.4739 | 1.3299 | 1.5871 | 1.4787 | 1.0912 | 0.96682 | 0.8534 | 0.8135 | 0.74586
43602.4739 | 1.3285 | 1.5867 | 1.4778 | 1.0908 | 0.96627 | 0.85306 | 0.81291 | 0.74516
43602.4739 | 1.3259 | 1.5883 | 1.4795 | 1.0922 | 0.9676 | 0.85428 | 0.81441 | 0.74603
43602.4741 | 1.3349 | 1.5926 | 1.483 | 1.0951 | 0.96975 | 0.85628 | 0.81542 | 0.74672
43602.4741 | 1.3275 | 1.5935 | 1.4825 | 1.0947 | 0.96874 | 0.85579 | 0.81633 | 0.74634
43602.4741 | 1.3354 | 1.5929 | 1.4829 | 1.0953 | 0.97026 | 0.85661 | 0.81842 | 0.74718
43602.4741 | 1.3374 | 1.5926 | 1.4831 | 1.0951 | 0.96881 | 0.85572 | 0.81585 | 0.74668
43602.4741 | 1.3326 | 1.5924 | 1.4822 | 1.0944 | 0.96966 | 0.85643 | 0.81636 | 0.74722
43602.4741 | 1.3307 | 1.5926 | 1.4828 | 1.0951 | 0.96906 | 0.85585 | 0.8155 | 0.7468
43602.4741 | 1.334 | 1.5906 | 1.4809 | 1.0939 | 0.96912 | 0.85594 | 0.81578 | 0.74703
43602.4741 | 1.332 | 1.5924 | 1.4826 | 1.095 | 0.9691 | 0.85509 | 0.81506 | 0.74668
43602.4741 | 1.3297 | 1.5899 | 1.4804 | 1.0935 | 0.96906 | 0.8557 | 0.81737 | 0.74661
43602.4743 | 1.322 | 1.5821 | 1.4755 | 1.0886 | 0.96418 | 0.85233 | 0.81417 | 0.74571
43602.4743 | 1.3207 | 1.5813 | 1.4755 | 1.0877 | 0.96362 | 0.85116 | 0.81186 | 0.74496
43602.4743 | 1.3215 | 1.5804 | 1.4745 | 1.087 | 0.96337 | 0.85148 | 0.81206 | 0.74551
43602.4743 | 1.3182 | 1.5794 | 1.4738 | 1.0873 | 0.96196 | 0.85042 | 0.81075 | 0.7449
43602.4743 | 1.3141 | 1.5774 | 1.4721 | 1.086 | 0.96243 | 0.85045 | 0.81074 | 0.74501
43602.4743 | 1.3223 | 1.5788 | 1.4723 | 1.0854 | 0.96111 | 0.84961 | 0.80983 | 0.74466
43602.4743 | 1.3184 | 1.5777 | 1.4715 | 1.0856 | 0.96124 | 0.84979 | 0.81282 | 0.74438
43602.4743 | 1.3183 | 1.5767 | 1.4711 | 1.0844 | 0.96011 | 0.84849 | 0.81067 | 0.74377
43602.4742 | 1.3194 | 1.5776 | 1.4718 | 1.0848 | 0.96072 | 0.84872 | 0.81001 | 0.74446
43602.4745 | 1.3175 | 1.5782 | 1.4721 | 1.085 | 0.96079 | 0.84893 | 0.81083 | 0.74386
43602.4745 | 1.3211 | 1.5786 | 1.4732 | 1.0862 | 0.96116 | 0.84939 | 0.81029 | 0.7441
43602.4745 | 1.318 | 1.5759 | 1.4716 | 1.0841 | 0.96189 | 0.84969 | 0.81038 | 0.74469
43602.4745 | 1.32 | 1.577 | 1.4727 | 1.0857 | 0.96108 | 0.8492 | 0.81175 | 0.74439
43602.4745 | 1.3193 | 1.5761 | 1.472 | 1.0848 | 0.96168 | 0.84977 | 0.81098 | 0.74496
43602.4745 | 1.3226 | 1.578 | 1.4725 | 1.0853 | 0.96091 | 0.84914 | 0.80998 | 0.74457
43602.4745 | 1.3143 | 1.5761 | 1.4716 | 1.085 | 0.96013 | 0.84887 | 0.80949 | 0.74406
43602.4745 | 1.3212 | 1.5777 | 1.4727 | 1.0852 | 0.96072 | 0.84931 | 0.8099 | 0.74453
43602.4745 | 1.3142 | 1.5784 | 1.4728 | 1.0861 | 0.96095 | 0.8495 | 0.81096 | 0.74443
43602.4747 | 1.3223 | 1.5779 | 1.4724 | 1.0865 | 0.96152 | 0.84964 | 0.8107 | 0.74492
43602.4747 | 1.3186 | 1.5775 | 1.4723 | 1.0864 | 0.96258 | 0.8508 | 0.81145 | 0.74552
43602.4747 | 1.3177 | 1.5775 | 1.4721 | 1.0858 | 0.96301 | 0.85105 | 0.81178 | 0.74626
43602.4747 | 1.3157 | 1.578 | 1.4726 | 1.0862 | 0.96128 | 0.85017 | 0.81124 | 0.74547
43602.4747 | 1.319 | 1.5769 | 1.4721 | 1.0853 | 0.9628 | 0.85109 | 0.81447 | 0.74639
43602.4747 | 1.3209 | 1.5778 | 1.4729 | 1.0867 | 0.96315 | 0.85132 | 0.81312 | 0.74677
43602.4747 | 1.3197 | 1.5762 | 1.4713 | 1.0848 | 0.96238 | 0.85034 | 0.81138 | 0.7458
43602.4747 | 1.3213 | 1.5775 | 1.4719 | 1.086 | 0.96148 | 0.85021 | 0.81087 | 0.7455
43602.4746 | 1.3152 | 1.5754 | 1.4707 | 1.0845 | 0.96094 | 0.84952 | 0.81032 | 0.74514
43602.4749 | 1.3141 | 1.5734 | 1.4676 | 1.0821 | 0.95936 | 0.84776 | 0.80884 | 0.74428
43602.4749 | 1.3113 | 1.5729 | 1.468 | 1.0819 | 0.95916 | 0.84807 | 0.80871 | 0.74421
43602.4749 | 1.3156 | 1.5716 | 1.4668 | 1.0818 | 0.95832 | 0.847 | 0.80789 | 0.74363
43602.4749 | 1.3099 | 1.5719 | 1.468 | 1.0813 | 0.95902 | 0.84785 | 0.80931 | 0.74437
43602.4749 | 1.3161 | 1.574 | 1.469 | 1.082 | 0.95906 | 0.84774 | 0.80985 | 0.74418
43602.4749 | 1.3133 | 1.5716 | 1.4677 | 1.0812 | 0.95905 | 0.84795 | 0.80887 | 0.74413
43602.4749 | 1.3198 | 1.5741 | 1.4687 | 1.0825 | 0.95898 | 0.84756 | 0.8081 | 0.74404
43602.4749 | 1.3169 | 1.5737 | 1.4683 | 1.0814 | 0.95974 | 0.84809 | 0.80956 | 0.74423
43602.4748 | 1.3112 | 1.5751 | 1.4698 | 1.0828 | 0.9603 | 0.84836 | 0.81127 | 0.7443
43602.4751 | 1.3176 | 1.5809 | 1.4748 | 1.0878 | 0.96294 | 0.85075 | 0.81085 | 0.74518
43602.4751 | 1.3194 | 1.5815 | 1.4753 | 1.0881 | 0.96398 | 0.85171 | 0.8128 | 0.74584
43602.4751 | 1.3194 | 1.5802 | 1.475 | 1.0869 | 0.96387 | 0.8518 | 0.8141 | 0.74594
43602.4751 | 1.3195 | 1.5817 | 1.4757 | 1.0876 | 0.96338 | 0.85109 | 0.81217 | 0.74532
43602.4751 | 1.3172 | 1.5799 | 1.4743 | 1.0863 | 0.96397 | 0.85173 | 0.81189 | 0.74601
43602.4751 | 1.3215 | 1.5815 | 1.4752 | 1.0872 | 0.96268 | 0.8513 | 0.81097 | 0.74584
43602.4751 | 1.3128 | 1.5805 | 1.4752 | 1.0864 | 0.96342 | 0.85157 | 0.81134 | 0.7456
43602.4751 | 1.3193 | 1.5821 | 1.4759 | 1.0878 | 0.96379 | 0.85123 | 0.81326 | 0.74513
43602.475 | 1.3193 | 1.5801 | 1.475 | 1.0871 | 0.96296 | 0.85141 | 0.81373 | 0.74622
43602.4753 | 1.3152 | 1.5755 | 1.4706 | 1.0837 | 0.96004 | 0.84863 | 0.80912 | 0.74487
43602.4753 | 1.3127 | 1.5762 | 1.4709 | 1.0836 | 0.96132 | 0.84993 | 0.81082 | 0.74614
43602.4753 | 1.312 | 1.5757 | 1.4712 | 1.0843 | 0.96076 | 0.84914 | 0.81006 | 0.74513
43602.4753 | 1.3195 | 1.5761 | 1.4713 | 1.084 | 0.96127 | 0.84924 | 0.80969 | 0.74528
43602.4753 | 1.3131 | 1.5743 | 1.4699 | 1.0831 | 0.96138 | 0.84922 | 0.81176 | 0.74545
43602.4753 | 1.3182 | 1.5742 | 1.4698 | 1.0837 | 0.96015 | 0.84881 | 0.81189 | 0.74557
43602.4753 | 1.3097 | 1.5733 | 1.4691 | 1.0821 | 0.95992 | 0.84834 | 0.80927 | 0.745
43602.4753 | 1.3163 | 1.5742 | 1.4687 | 1.0819 | 0.95898 | 0.84777 | 0.80883 | 0.74462
43602.4752 | 1.3132 | 1.572 | 1.4675 | 1.0813 | 0.95816 | 0.84708 | 0.8078 | 0.74451
43602.4755 | 1.3089 | 1.5636 | 1.4597 | 1.0754 | 0.95462 | 0.84429 | 0.80556 | 0.74356
43602.4755 | 1.3082 | 1.5634 | 1.4592 | 1.0758 | 0.95333 | 0.84316 | 0.8044 | 0.74321
43602.4755 | 1.3039 | 1.5626 | 1.4592 | 1.075 | 0.95454 | 0.84357 | 0.80484 | 0.74333
43602.4755 | 1.3062 | 1.5621 | 1.4579 | 1.075 | 0.954 | 0.84337 | 0.80535 | 0.74327
43602.4755 | 1.3033 | 1.5593 | 1.4566 | 1.073 | 0.9522 | 0.84228 | 0.80646 | 0.74285
43602.4755 | 1.3054 | 1.5607 | 1.4567 | 1.074 | 0.95246 | 0.84234 | 0.80468 | 0.74287
43602.4755 | 1.3034 | 1.5587 | 1.4554 | 1.0734 | 0.95161 | 0.8415 | 0.80334 | 0.74248
43602.4755 | 1.3001 | 1.5587 | 1.4556 | 1.0732 | 0.95158 | 0.84112 | 0.80296 | 0.74261
43602.4755 | 1.3042 | 1.559 | 1.456 | 1.0735 | 0.95176 | 0.8413 | 0.80285 | 0.74245
43602.4757 | 1.3003 | 1.5522 | 1.4484 | 1.0687 | 0.94804 | 0.83873 | 0.8015 | 0.74179
43602.4757 | 1.301 | 1.5522 | 1.4486 | 1.0684 | 0.94709 | 0.83798 | 0.80275 | 0.74132
43602.4757 | 1.3011 | 1.5525 | 1.4486 | 1.0701 | 0.94805 | 0.83885 | 0.80131 | 0.74189
43602.4757 | 1.2937 | 1.5502 | 1.4474 | 1.0676 | 0.94752 | 0.83854 | 0.80058 | 0.74132
43602.4757 | 1.3029 | 1.5522 | 1.4491 | 1.0703 | 0.94828 | 0.83876 | 0.80055 | 0.74185
43602.4757 | 1.2997 | 1.5514 | 1.4471 | 1.0682 | 0.94775 | 0.83811 | 0.80017 | 0.74154
43602.4757 | 1.3045 | 1.5503 | 1.447 | 1.0689 | 0.94695 | 0.83765 | 0.80088 | 0.74082
43602.4757 | 1.2978 | 1.5508 | 1.4466 | 1.0685 | 0.94784 | 0.83839 | 0.80025 | 0.74134
43602.4756 | 1.2993 | 1.5525 | 1.4473 | 1.0697 | 0.94755 | 0.83812 | 0.80063 | 0.74112
43602.4759 | 1.3092 | 1.5526 | 1.4458 | 1.0704 | 0.94889 | 0.83849 | 0.8017 | 0.74156
43602.4759 | 1.305 | 1.5532 | 1.4464 | 1.0712 | 0.94909 | 0.83915 | 0.80184 | 0.74176
43602.4759 | 1.308 | 1.5549 | 1.4487 | 1.072 | 0.94908 | 0.83893 | 0.80093 | 0.74146
43602.4759 | 1.3083 | 1.5548 | 1.449 | 1.072 | 0.95075 | 0.84071 | 0.80193 | 0.74241
43602.4759 | 1.3137 | 1.5591 | 1.4521 | 1.0754 | 0.95178 | 0.84122 | 0.80281 | 0.74259
43602.4759 | 1.3083 | 1.5574 | 1.451 | 1.0745 | 0.95222 | 0.84131 | 0.80476 | 0.7422
43602.4759 | 1.3092 | 1.5585 | 1.4522 | 1.0754 | 0.95276 | 0.84168 | 0.8034 | 0.74239
43602.4759 | 1.3162 | 1.5627 | 1.455 | 1.0785 | 0.95423 | 0.84313 | 0.8046 | 0.74309
43602.4758 | 1.3077 | 1.5627 | 1.4547 | 1.0781 | 0.95431 | 0.84345 | 0.80451 | 0.74272
43602.4761 | 1.316 | 1.5659 | 1.4571 | 1.0804 | 0.95603 | 0.84525 | 0.80637 | 0.74413
43602.4761 | 1.3034 | 1.5642 | 1.4558 | 1.0793 | 0.95523 | 0.84503 | 0.80565 | 0.7438
43602.4761 | 1.3151 | 1.5643 | 1.456 | 1.0797 | 0.95533 | 0.84417 | 0.8052 | 0.74369
43602.4761 | 1.309 | 1.5624 | 1.4549 | 1.0774 | 0.95507 | 0.84407 | 0.80809 | 0.74346
43602.4761 | 1.3175 | 1.5646 | 1.4566 | 1.0794 | 0.9548 | 0.84397 | 0.80681 | 0.74375
43602.4761 | 1.3151 | 1.562 | 1.4543 | 1.0772 | 0.95446 | 0.84364 | 0.80524 | 0.74351
43602.4761 | 1.3122 | 1.5627 | 1.4545 | 1.0781 | 0.95404 | 0.84322 | 0.80417 | 0.74289
43602.4761 | 1.3115 | 1.5614 | 1.4541 | 1.0774 | 0.9541 | 0.84354 | 0.80415 | 0.74352
43602.476 | 1.3107 | 1.5637 | 1.4552 | 1.0776 | 0.95366 | 0.8437 | 0.80556 | 0.74347
43602.4763 | 1.3163 | 1.5625 | 1.4546 | 1.0771 | 0.95411 | 0.84344 | 0.80471 | 0.74313
43602.4763 | 1.3059 | 1.5646 | 1.4567 | 1.0797 | 0.95391 | 0.84281 | 0.8039 | 0.74296
43602.4763 | 1.3157 | 1.5627 | 1.4541 | 1.0774 | 0.95509 | 0.84409 | 0.80512 | 0.74313
43602.4763 | 1.3143 | 1.5663 | 1.4564 | 1.0792 | 0.95353 | 0.84263 | 0.80616 | 0.74215
43602.4763 | 1.3125 | 1.5668 | 1.4566 | 1.0789 | 0.95569 | 0.84428 | 0.80646 | 0.74323
43602.4763 | 1.3194 | 1.5703 | 1.4593 | 1.0816 | 0.95574 | 0.84466 | 0.80534 | 0.74326
43602.4763 | 1.3232 | 1.572 | 1.4602 | 1.082 | 0.95749 | 0.84567 | 0.80607 | 0.74366
43602.4763 | 1.3206 | 1.5718 | 1.4612 | 1.082 | 0.95746 | 0.84605 | 0.80709 | 0.74389
43602.4763 | 1.3256 | 1.5782 | 1.4658 | 1.0857 | 0.96129 | 0.84905 | 0.81113 | 0.74464
43602.4765 | 1.3213 | 1.5797 | 1.4662 | 1.0858 | 0.96134 | 0.84896 | 0.80987 | 0.74516
43602.4765 | 1.3097 | 1.5808 | 1.467 | 1.0865 | 0.96097 | 0.84864 | 0.81018 | 0.74505
43602.4765 | 1.3214 | 1.577 | 1.4652 | 1.0839 | 0.96003 | 0.84805 | 0.80856 | 0.7442
43602.4765 | 1.3208 | 1.5781 | 1.466 | 1.0856 | 0.95984 | 0.8477 | 0.80801 | 0.74459
43602.4765 | 1.3215 | 1.5773 | 1.4657 | 1.0855 | 0.96081 | 0.84804 | 0.8076 | 0.74445
43602.4765 | 1.3156 | 1.5751 | 1.4638 | 1.0828 | 0.9595 | 0.84773 | 0.81104 | 0.745
43602.4765 | 1.315 | 1.5768 | 1.4652 | 1.0839 | 0.95882 | 0.84674 | 0.8087 | 0.7447
43602.4765 | 1.3135 | 1.575 | 1.4641 | 1.0831 | 0.95919 | 0.84725 | 0.80846 | 0.74437
43602.4765 | 1.3159 | 1.5727 | 1.4621 | 1.0817 | 0.95688 | 0.84473 | 0.80568 | 0.74348
43602.4767 | 1.309 | 1.5701 | 1.4608 | 1.0792 | 0.95584 | 0.84461 | 0.80632 | 0.7437
43602.4767 | 1.3085 | 1.5692 | 1.4609 | 1.0789 | 0.95543 | 0.84413 | 0.80539 | 0.74353
43602.4767 | 1.3147 | 1.5685 | 1.46 | 1.0781 | 0.95642 | 0.84503 | 0.80625 | 0.74457
43602.4767 | 1.3008 | 1.5681 | 1.4607 | 1.0787 | 0.95454 | 0.84391 | 0.80538 | 0.74382
43602.4767 | 1.3121 | 1.5689 | 1.4599 | 1.0786 | 0.95506 | 0.84419 | 0.80777 | 0.74391
43602.4767 | 1.311 | 1.5692 | 1.46 | 1.0784 | 0.95507 | 0.84352 | 0.80586 | 0.74326
43602.4767 | 1.313 | 1.5702 | 1.4616 | 1.0802 | 0.95614 | 0.84497 | 0.80671 | 0.74422
43602.4768 | 1.3088 | 1.567 | 1.4585 | 1.0763 | 0.95502 | 0.84374 | 0.80487 | 0.74318
43602.4767 | 1.3028 | 1.5657 | 1.4593 | 1.0766 | 0.9542 | 0.84343 | 0.80688 | 0.7438
43602.4769 | 1.3113 | 1.5682 | 1.4611 | 1.0775 | 0.95474 | 0.84377 | 0.80528 | 0.74336
43602.4769 | 1.3103 | 1.5671 | 1.461 | 1.0772 | 0.95518 | 0.84432 | 0.80629 | 0.74424
43602.4769 | 1.3112 | 1.567 | 1.4607 | 1.0776 | 0.95544 | 0.84472 | 0.80853 | 0.7439
43602.4769 | 1.3053 | 1.5661 | 1.4597 | 1.0768 | 0.95495 | 0.84379 | 0.80566 | 0.74355
43602.4769 | 1.3123 | 1.5677 | 1.4612 | 1.0782 | 0.95522 | 0.84441 | 0.80648 | 0.74456
43602.4769 | 1.3102 | 1.5675 | 1.4614 | 1.0785 | 0.95619 | 0.84487 | 0.80581 | 0.74452
43602.4769 | 1.3077 | 1.567 | 1.4608 | 1.077 | 0.95493 | 0.84407 | 0.80531 | 0.7437
43602.477 | 1.3059 | 1.5656 | 1.4596 | 1.0763 | 0.95422 | 0.84364 | 0.80493 | 0.74378
43602.4769 | 1.3059 | 1.5646 | 1.4592 | 1.0746 | 0.95282 | 0.84208 | 0.80356 | 0.74264
43602.4771 | 1.3039 | 1.5665 | 1.4613 | 1.0763 | 0.95375 | 0.84286 | 0.80465 | 0.7428
43602.4771 | 1.2962 | 1.5663 | 1.4604 | 1.0751 | 0.95267 | 0.84243 | 0.80334 | 0.74285
43602.4771 | 1.3051 | 1.5657 | 1.4604 | 1.076 | 0.95334 | 0.84242 | 0.80334 | 0.74273
43602.4771 | 1.3025 | 1.5665 | 1.4609 | 1.0765 | 0.95327 | 0.84242 | 0.80384 | 0.74265
43602.4771 | 1.3001 | 1.5659 | 1.4607 | 1.075 | 0.95349 | 0.84266 | 0.80551 | 0.74262
43602.4771 | 1.3072 | 1.5667 | 1.4608 | 1.0762 | 0.95294 | 0.84212 | 0.80354 | 0.7421
43602.4772 | 1.2985 | 1.5656 | 1.4609 | 1.0751 | 0.95276 | 0.84196 | 0.80283 | 0.74186
43602.4772 | 1.3047 | 1.5659 | 1.4607 | 1.075 | 0.95334 | 0.84308 | 0.80349 | 0.74341
43602.4771 | 1.2985 | 1.5635 | 1.458 | 1.0725 | 0.95096 | 0.8404 | 0.80479 | 0.7421
43602.4773 | 1.2996 | 1.5643 | 1.4592 | 1.073 | 0.95078 | 0.84066 | 0.80151 | 0.74135
43602.4773 | 1.2976 | 1.5634 | 1.4595 | 1.0725 | 0.95076 | 0.84055 | 0.80301 | 0.7416
43602.4773 | 1.2982 | 1.5635 | 1.4601 | 1.0714 | 0.95049 | 0.83999 | 0.80376 | 0.74088
43602.4773 | 1.3022 | 1.5666 | 1.4614 | 1.0737 | 0.95172 | 0.84115 | 0.80314 | 0.74148
43602.4773 | 1.3033 | 1.5664 | 1.4609 | 1.0736 | 0.95141 | 0.84083 | 0.80218 | 0.74125
43602.4773 | 1.3042 | 1.5674 | 1.4627 | 1.0754 | 0.95253 | 0.84141 | 0.80286 | 0.7419
43602.4774 | 1.3035 | 1.5662 | 1.4607 | 1.0736 | 0.95222 | 0.84144 | 0.80307 | 0.74174
43602.4773 | 1.2996 | 1.5636 | 1.4593 | 1.0721 | 0.95064 | 0.83997 | 0.80157 | 0.74118
43602.4775 | 1.285 | 1.5526 | 1.4497 | 1.0648 | 0.94503 | 0.83546 | 0.79799 | 0.73977
43602.4775 | 1.2865 | 1.5499 | 1.4481 | 1.0633 | 0.94347 | 0.83447 | 0.79661 | 0.73949
43602.4775 | 1.2861 | 1.5488 | 1.4465 | 1.0624 | 0.94295 | 0.83382 | 0.79621 | 0.73912
43602.4775 | 1.2776 | 1.5463 | 1.4448 | 1.0601 | 0.9415 | 0.8331 | 0.79544 | 0.73907
43602.4775 | 1.2736 | 1.5439 | 1.4427 | 1.0589 | 0.93981 | 0.83227 | 0.79487 | 0.73847
43602.4775 | 1.2813 | 1.5446 | 1.4413 | 1.0587 | 0.93874 | 0.83088 | 0.7952 | 0.73816
43602.4775 | 1.2812 | 1.5429 | 1.4408 | 1.058 | 0.93849 | 0.83048 | 0.79338 | 0.73798
43602.4776 | 1.2761 | 1.5404 | 1.4395 | 1.0566 | 0.93759 | 0.8299 | 0.79229 | 0.73769
43602.4775 | 1.2726 | 1.5391 | 1.4369 | 1.0553 | 0.93661 | 0.82916 | 0.79367 | 0.73714
43602.4777 | 1.2787 | 1.5382 | 1.4364 | 1.056 | 0.9362 | 0.82866 | 0.79233 | 0.7373
43602.4777 | 1.2839 | 1.5389 | 1.4353 | 1.0557 | 0.93515 | 0.82778 | 0.79069 | 0.73647
43602.4777 | 1.2808 | 1.5372 | 1.4347 | 1.0544 | 0.93554 | 0.82721 | 0.79042 | 0.73643
43602.4777 | 1.2785 | 1.5387 | 1.4355 | 1.0554 | 0.93569 | 0.82756 | 0.7907 | 0.73626
43602.4777 | 1.2802 | 1.5374 | 1.4339 | 1.0547 | 0.93576 | 0.82786 | 0.79375 | 0.73656
43602.4777 | 1.2836 | 1.5376 | 1.4351 | 1.0559 | 0.93572 | 0.82782 | 0.79131 | 0.73661
43602.4778 | 1.2809 | 1.5372 | 1.4348 | 1.0551 | 0.93511 | 0.82735 | 0.7905 | 0.73613
43602.4778 | 1.2828 | 1.5387 | 1.4359 | 1.0569 | 0.93605 | 0.82806 | 0.79029 | 0.73659
43602.4777 | 1.2918 | 1.5432 | 1.4383 | 1.0602 | 0.93893 | 0.83037 | 0.79356 | 0.73777
43602.4779 | 1.2991 | 1.5495 | 1.4434 | 1.0652 | 0.94298 | 0.83391 | 0.7976 | 0.7393
43602.4779 | 1.296 | 1.5474 | 1.4427 | 1.064 | 0.94339 | 0.83364 | 0.79654 | 0.73886
43602.4779 | 1.2957 | 1.5501 | 1.4443 | 1.066 | 0.94326 | 0.83393 | 0.79595 | 0.73928
43602.4779 | 1.2975 | 1.5506 | 1.444 | 1.0662 | 0.94474 | 0.8345 | 0.79623 | 0.7395
43602.4779 | 1.2981 | 1.5514 | 1.4444 | 1.0662 | 0.94444 | 0.83477 | 0.7964 | 0.73982
43602.4779 | 1.3019 | 1.5531 | 1.4469 | 1.0688 | 0.9458 | 0.83615 | 0.79862 | 0.74032
43602.478 | 1.3051 | 1.5528 | 1.4463 | 1.0683 | 0.94609 | 0.83628 | 0.79919 | 0.74048
43602.478 | 1.3033 | 1.5539 | 1.4464 | 1.0688 | 0.94623 | 0.83665 | 0.79873 | 0.74078
43602.4779 | 1.2995 | 1.5495 | 1.4422 | 1.0656 | 0.94427 | 0.83475 | 0.79753 | 0.7405
43602.4781 | 1.2931 | 1.5423 | 1.4365 | 1.0616 | 0.94037 | 0.83229 | 0.79455 | 0.73989
43602.4781 | 1.2836 | 1.539 | 1.4346 | 1.0594 | 0.93958 | 0.83081 | 0.79506 | 0.73895
43602.4781 | 1.2849 | 1.5395 | 1.4349 | 1.059 | 0.9387 | 0.83057 | 0.79383 | 0.73892
43602.4781 | 1.2853 | 1.5383 | 1.4337 | 1.0588 | 0.93845 | 0.83015 | 0.79285 | 0.73883
43602.4781 | 1.2849 | 1.5366 | 1.4322 | 1.0576 | 0.93834 | 0.83063 | 0.79315 | 0.73956
43602.4781 | 1.286 | 1.5355 | 1.4305 | 1.0563 | 0.9369 | 0.82873 | 0.79249 | 0.73809
43602.4782 | 1.2858 | 1.535 | 1.4308 | 1.0567 | 0.93596 | 0.82835 | 0.79375 | 0.73801
43602.4781 | 1.285 | 1.5332 | 1.429 | 1.0552 | 0.93513 | 0.8273 | 0.79073 | 0.73791
43602.4783 | 1.2791 | 1.5272 | 1.4241 | 1.0506 | 0.93202 | 0.82515 | 0.78892 | 0.7369
43602.4783 | 1.2764 | 1.5257 | 1.4233 | 1.0502 | 0.93029 | 0.82391 | 0.78788 | 0.73643
43602.4783 | 1.2821 | 1.5292 | 1.4255 | 1.0526 | 0.93195 | 0.82498 | 0.7882 | 0.73711
43602.4783 | 1.2716 | 1.5265 | 1.4236 | 1.0505 | 0.9334 | 0.82607 | 0.78904 | 0.73802
43602.4783 | 1.2831 | 1.5299 | 1.4265 | 1.0532 | 0.93241 | 0.82573 | 0.78969 | 0.73809
43602.4783 | 1.2773 | 1.528 | 1.4254 | 1.0512 | 0.93275 | 0.82539 | 0.79068 | 0.73715
43602.4783 | 1.2792 | 1.5283 | 1.4259 | 1.0509 | 0.93149 | 0.82457 | 0.78793 | 0.73654
43602.4784 | 1.2787 | 1.5301 | 1.4268 | 1.0529 | 0.93356 | 0.82586 | 0.78907 | 0.73749
43602.4783 | 1.2844 | 1.5336 | 1.4299 | 1.0558 | 0.93356 | 0.826 | 0.78969 | 0.73751
43602.4785 | 1.2818 | 1.5324 | 1.4285 | 1.054 | 0.9357 | 0.82833 | 0.79146 | 0.73847
43602.4785 | 1.2752 | 1.529 | 1.4255 | 1.0516 | 0.93234 | 0.82602 | 0.78914 | 0.73761
43602.4785 | 1.2814 | 1.5291 | 1.4252 | 1.0523 | 0.93287 | 0.82607 | 0.79007 | 0.73816
43602.4785 | 1.2708 | 1.5273 | 1.4243 | 1.0498 | 0.93182 | 0.82546 | 0.79033 | 0.73744
43602.4785 | 1.2789 | 1.5272 | 1.4239 | 1.0499 | 0.9312 | 0.82427 | 0.78773 | 0.7366
43602.4785 | 1.2739 | 1.5252 | 1.423 | 1.0491 | 0.93052 | 0.82376 | 0.78735 | 0.73698
43602.4785 | 1.2726 | 1.524 | 1.4216 | 1.0479 | 0.92999 | 0.82354 | 0.78725 | 0.73695
43602.4786 | 1.2719 | 1.5252 | 1.4224 | 1.0489 | 0.93004 | 0.82329 | 0.7896 | 0.7367
43602.4785 | 1.2742 | 1.5232 | 1.4213 | 1.0477 | 0.9285 | 0.82237 | 0.78585 | 0.73596
43602.4787 | 1.2708 | 1.5267 | 1.4232 | 1.0495 | 0.92912 | 0.8225 | 0.78614 | 0.73602
43602.4787 | 1.2789 | 1.5255 | 1.4224 | 1.0482 | 0.93029 | 0.82351 | 0.78637 | 0.73655
43602.4787 | 1.2754 | 1.5264 | 1.4235 | 1.0495 | 0.93089 | 0.82376 | 0.78726 | 0.73687
43602.4787 | 1.2729 | 1.5256 | 1.4232 | 1.0483 | 0.92964 | 0.82255 | 0.78858 | 0.73588
43602.4787 | 1.271 | 1.5261 | 1.424 | 1.0487 | 0.92981 | 0.8227 | 0.78672 | 0.73575
43602.4787 | 1.2753 | 1.5273 | 1.4244 | 1.0497 | 0.93063 | 0.82358 | 0.78682 | 0.73652
43602.4788 | 1.2711 | 1.5261 | 1.4236 | 1.0483 | 0.9303 | 0.82298 | 0.7865 | 0.73606
43602.4787 | 1.2779 | 1.5276 | 1.424 | 1.0498 | 0.93132 | 0.824 | 0.78711 | 0.73694
43602.4789 | 1.2744 | 1.5254 | 1.4221 | 1.0473 | 0.92942 | 0.82287 | 0.78621 | 0.73654
43602.4789 | 1.2714 | 1.5241 | 1.4213 | 1.0463 | 0.92857 | 0.82183 | 0.78572 | 0.73561
43602.4789 | 1.277 | 1.526 | 1.4229 | 1.0482 | 0.92925 | 0.82238 | 0.78605 | 0.73613
43602.4789 | 1.2657 | 1.5236 | 1.4212 | 1.0459 | 0.92877 | 0.82246 | 0.78825 | 0.73617
43602.4789 | 1.2707 | 1.5253 | 1.4225 | 1.0472 | 0.92814 | 0.82141 | 0.78547 | 0.73573
43602.4789 | 1.2713 | 1.5245 | 1.4209 | 1.0463 | 0.92793 | 0.82143 | 0.78489 | 0.7356
43602.4791 | 1.2674 | 1.5239 | 1.4193 | 1.0451 | 0.92704 | 0.8207 | 0.78525 | 0.73531
43602.4791 | 1.2716 | 1.5226 | 1.4188 | 1.0447 | 0.9258 | 0.81975 | 0.78347 | 0.73496
43602.4791 | 1.2719 | 1.5249 | 1.4202 | 1.046 | 0.92733 | 0.82093 | 0.78441 | 0.73544
43602.4791 | 1.2738 | 1.5265 | 1.4211 | 1.0466 | 0.92729 | 0.82059 | 0.78435 | 0.73536
43602.4791 | 1.2631 | 1.5238 | 1.4198 | 1.0451 | 0.92778 | 0.82147 | 0.78589 | 0.73527
43602.4791 | 1.2713 | 1.5265 | 1.4219 | 1.047 | 0.9284 | 0.82178 | 0.78787 | 0.73539
43602.4791 | 1.273 | 1.5278 | 1.4231 | 1.0489 | 0.93026 | 0.823 | 0.78674 | 0.73609
43602.4791 | 1.2623 | 1.5264 | 1.4223 | 1.0469 | 0.929 | 0.822 | 0.78558 | 0.73537
43602.479 | 1.2733 | 1.5268 | 1.422 | 1.0472 | 0.92997 | 0.82337 | 0.786 | 0.73612
43602.4793 | 1.2672 | 1.5215 | 1.4184 | 1.044 | 0.9267 | 0.82077 | 0.78444 | 0.73512
43602.4793 | 1.2655 | 1.5218 | 1.4179 | 1.0444 | 0.92705 | 0.82114 | 0.78481 | 0.73559
43602.4793 | 1.2662 | 1.5203 | 1.4166 | 1.0429 | 0.92621 | 0.81988 | 0.78361 | 0.73501
43602.4793 | 1.2657 | 1.5187 | 1.4152 | 1.0434 | 0.92489 | 0.81965 | 0.78365 | 0.73552
43602.4793 | 1.2615 | 1.5173 | 1.414 | 1.0412 | 0.92433 | 0.81891 | 0.78563 | 0.73496
43602.4793 | 1.2644 | 1.5166 | 1.4135 | 1.0409 | 0.92349 | 0.81854 | 0.78336 | 0.73445
43602.4793 | 1.263 | 1.5137 | 1.4108 | 1.0391 | 0.92278 | 0.81756 | 0.78184 | 0.73432
43602.4793 | 1.2624 | 1.5132 | 1.4108 | 1.0398 | 0.92221 | 0.81692 | 0.78131 | 0.73435
43602.4793 | 1.2565 | 1.5091 | 1.4069 | 1.0356 | 0.91911 | 0.81443 | 0.77886 | 0.73304
43602.4795 | 1.2527 | 1.5063 | 1.4042 | 1.033 | 0.91719 | 0.81301 | 0.77725 | 0.73237
43602.4795 | 1.2617 | 1.5102 | 1.4067 | 1.0369 | 0.91878 | 0.81413 | 0.7786 | 0.73336
43602.4795 | 1.2573 | 1.507 | 1.4047 | 1.0352 | 0.91958 | 0.81502 | 0.78156 | 0.73343
43602.4795 | 1.2583 | 1.5081 | 1.4056 | 1.0355 | 0.9194 | 0.81471 | 0.77976 | 0.73341
43602.4795 | 1.2569 | 1.5073 | 1.4044 | 1.0341 | 0.91859 | 0.81449 | 0.77896 | 0.73305
43602.4795 | 1.2579 | 1.5081 | 1.4057 | 1.036 | 0.91809 | 0.81388 | 0.77833 | 0.7331
43602.4795 | 1.2563 | 1.5098 | 1.4065 | 1.0366 | 0.91917 | 0.81447 | 0.77944 | 0.73338
43602.4795 | 1.2634 | 1.5105 | 1.4069 | 1.0377 | 0.92014 | 0.8153 | 0.77946 | 0.73335
43602.4795 | 1.2576 | 1.5086 | 1.4051 | 1.0356 | 0.9189 | 0.81419 | 0.77966 | 0.7326
43602.4797 | 1.2588 | 1.5051 | 1.402 | 1.0339 | 0.91731 | 0.81291 | 0.77797 | 0.73236
43602.4797 | 1.2589 | 1.5062 | 1.4034 | 1.0357 | 0.9182 | 0.81413 | 0.77855 | 0.73298
43602.4797 | 1.2602 | 1.5061 | 1.403 | 1.0351 | 0.91818 | 0.81359 | 0.77801 | 0.73259
43602.4797 | 1.2553 | 1.5039 | 1.4011 | 1.0337 | 0.91743 | 0.81331 | 0.78046 | 0.73269
43602.4797 | 1.2558 | 1.5063 | 1.4028 | 1.0357 | 0.91768 | 0.81368 | 0.77932 | 0.73289
43602.4797 | 1.2577 | 1.5045 | 1.4021 | 1.0354 | 0.91855 | 0.81387 | 0.77908 | 0.73264
43602.4797 | 1.2573 | 1.5048 | 1.4028 | 1.0353 | 0.91845 | 0.81424 | 0.77848 | 0.73344
43602.4797 | 1.2615 | 1.5081 | 1.4048 | 1.0376 | 0.92041 | 0.8157 | 0.77962 | 0.7339
43602.4799 | 1.2625 | 1.509 | 1.4059 | 1.0386 | 0.92086 | 0.81574 | 0.78166 | 0.73357
43602.4799 | 1.2646 | 1.5091 | 1.4056 | 1.0375 | 0.91973 | 0.8151 | 0.7808 | 0.7331
43602.4799 | 1.2678 | 1.5106 | 1.4062 | 1.0393 | 0.92114 | 0.81634 | 0.78067 | 0.7338
43602.4799 | 1.2602 | 1.5081 | 1.4055 | 1.0383 | 0.92163 | 0.81677 | 0.78077 | 0.7344
43602.4799 | 1.2566 | 1.5075 | 1.4049 | 1.0373 | 0.91986 | 0.81527 | 0.77977 | 0.73355
43602.4799 | 1.2638 | 1.5084 | 1.4043 | 1.0379 | 0.92019 | 0.81561 | 0.77967 | 0.73341
43602.4799 | 1.2662 | 1.5084 | 1.4049 | 1.0381 | 0.92058 | 0.81529 | 0.78004 | 0.73327
43602.4799 | 1.2685 | 1.5085 | 1.405 | 1.0384 | 0.92079 | 0.81576 | 0.78033 | 0.73364
43602.4801 | 1.2707 | 1.5116 | 1.4078 | 1.0404 | 0.92279 | 0.81751 | 0.78326 | 0.73382
43602.4801 | 1.2685 | 1.5118 | 1.4083 | 1.041 | 0.92351 | 0.81767 | 0.78273 | 0.73461
43602.4801 | 1.2655 | 1.5131 | 1.4085 | 1.041 | 0.92224 | 0.81722 | 0.78125 | 0.73443
43602.4801 | 1.2777 | 1.5155 | 1.4104 | 1.0437 | 0.92378 | 0.81766 | 0.78172 | 0.73419
43602.4801 | 1.2674 | 1.5128 | 1.4086 | 1.042 | 0.92393 | 0.81779 | 0.78223 | 0.73424
43602.4801 | 1.2662 | 1.5136 | 1.4092 | 1.0423 | 0.92483 | 0.81857 | 0.78338 | 0.73488
43602.4801 | 1.2704 | 1.5135 | 1.4092 | 1.0419 | 0.92326 | 0.81785 | 0.78278 | 0.73455
43602.48 | 1.2666 | 1.5117 | 1.4076 | 1.0408 | 0.92289 | 0.81711 | 0.78184 | 0.73406
43602.4803 | 1.2607 | 1.5058 | 1.4026 | 1.0377 | 0.92038 | 0.81545 | 0.78195 | 0.73434
43602.4803 | 1.2605 | 1.5054 | 1.4017 | 1.0371 | 0.92028 | 0.81484 | 0.77987 | 0.73409
43602.4803 | 1.258 | 1.5033 | 1.4008 | 1.036 | 0.91766 | 0.8135 | 0.77799 | 0.73345
43602.4803 | 1.257 | 1.5026 | 1.3995 | 1.035 | 0.91961 | 0.81445 | 0.77877 | 0.734
43602.4803 | 1.2622 | 1.5026 | 1.3988 | 1.0345 | 0.91789 | 0.81329 | 0.7791 | 0.73332
43602.4803 | 1.2594 | 1.5008 | 1.3982 | 1.0332 | 0.91676 | 0.81263 | 0.77859 | 0.7332
43602.4803 | 1.2577 | 1.4992 | 1.3969 | 1.0325 | 0.91627 | 0.81152 | 0.7769 | 0.73201
43602.4802 | 1.2637 | 1.5005 | 1.397 | 1.0337 | 0.9157 | 0.81187 | 0.77668 | 0.73271
43602.4804 | 1.2527 | 1.503 | 1.3986 | 1.035 | 0.91717 | 0.81296 | 0.77819 | 0.73324
43602.4805 | 1.2617 | 1.5046 | 1.4002 | 1.0368 | 0.91822 | 0.81376 | 0.77879 | 0.73336
43602.4805 | 1.2616 | 1.5044 | 1.4001 | 1.0376 | 0.9192 | 0.81436 | 0.77916 | 0.73347
43602.4805 | 1.2671 | 1.5066 | 1.4017 | 1.0383 | 0.91938 | 0.81442 | 0.77906 | 0.73389
43602.4805 | 1.2591 | 1.5052 | 1.4008 | 1.0382 | 0.92051 | 0.81575 | 0.78187 | 0.73459
43602.4805 | 1.2626 | 1.5064 | 1.4024 | 1.039 | 0.91991 | 0.81587 | 0.78119 | 0.73462
43602.4805 | 1.2618 | 1.506 | 1.4012 | 1.0381 | 0.91984 | 0.81559 | 0.78054 | 0.73425
43602.4804 | 1.2652 | 1.509 | 1.4039 | 1.0406 | 0.92109 | 0.81648 | 0.78149 | 0.73418
43602.4806 | 1.2651 | 1.5099 | 1.4048 | 1.0423 | 0.92139 | 0.81684 | 0.78407 | 0.7349
43602.4806 | 1.2725 | 1.5107 | 1.4048 | 1.0421 | 0.9218 | 0.81667 | 0.78167 | 0.73429
43602.4807 | 1.2727 | 1.5102 | 1.4052 | 1.0416 | 0.92197 | 0.81688 | 0.7815 | 0.73424
43602.4807 | 1.2728 | 1.5119 | 1.4053 | 1.0422 | 0.92252 | 0.81705 | 0.78164 | 0.73446
43602.4807 | 1.274 | 1.511 | 1.4058 | 1.043 | 0.92336 | 0.81783 | 0.78244 | 0.73537
43602.4807 | 1.2628 | 1.509 | 1.4043 | 1.0412 | 0.92245 | 0.81734 | 0.78421 | 0.73513
43602.4807 | 1.2667 | 1.5102 | 1.405 | 1.0416 | 0.92166 | 0.81729 | 0.78231 | 0.73467
43602.4807 | 1.2733 | 1.5106 | 1.4056 | 1.0421 | 0.92225 | 0.81742 | 0.78182 | 0.73459
43602.4806 | 1.2695 | 1.513 | 1.4067 | 1.0434 | 0.92226 | 0.81728 | 0.78399 | 0.73497
43602.4808 | 1.2716 | 1.5086 | 1.4025 | 1.0393 | 0.91937 | 0.81513 | 0.78032 | 0.73348
43602.4809 | 1.2686 | 1.5069 | 1.4024 | 1.0393 | 0.92127 | 0.81655 | 0.78324 | 0.73491
43602.4809 | 1.261 | 1.5061 | 1.4015 | 1.0389 | 0.91997 | 0.81539 | 0.78024 | 0.73382
43602.4809 | 1.2672 | 1.5047 | 1.3993 | 1.0371 | 0.91912 | 0.81471 | 0.77968 | 0.73396
43602.4809 | 1.2619 | 1.504 | 1.3985 | 1.0367 | 0.91785 | 0.81399 | 0.77877 | 0.73345
43602.4809 | 1.2626 | 1.5045 | 1.3994 | 1.0371 | 0.91863 | 0.81452 | 0.77961 | 0.73373
43602.4809 | 1.261 | 1.501 | 1.3965 | 1.0343 | 0.91721 | 0.81302 | 0.77785 | 0.73321
43602.4808 | 1.2581 | 1.497 | 1.3932 | 1.0322 | 0.91443 | 0.8111 | 0.77799 | 0.73202
43602.481 | 1.2455 | 1.4861 | 1.3841 | 1.0265 | 0.90909 | 0.80663 | 0.7752 | 0.73061
43602.4811 | 1.2499 | 1.4859 | 1.3826 | 1.0257 | 0.90789 | 0.80583 | 0.77274 | 0.73002
43602.4811 | 1.2467 | 1.4855 | 1.3823 | 1.0253 | 0.90829 | 0.80585 | 0.7722 | 0.73069
43602.4811 | 1.2464 | 1.4835 | 1.3808 | 1.0249 | 0.90747 | 0.80542 | 0.77132 | 0.73026
43602.4811 | 1.2487 | 1.4831 | 1.3807 | 1.0246 | 0.90689 | 0.80473 | 0.77042 | 0.72977
43602.4811 | 1.2466 | 1.4834 | 1.3803 | 1.0243 | 0.90726 | 0.80522 | 0.77257 | 0.73018
43602.4811 | 1.2489 | 1.4829 | 1.3797 | 1.0243 | 0.90629 | 0.80404 | 0.77146 | 0.72895
43602.481 | 1.2531 | 1.4856 | 1.3811 | 1.0257 | 0.90791 | 0.80566 | 0.773 | 0.72988
43602.4812 | 1.2464 | 1.4928 | 1.3863 | 1.0308 | 0.912 | 0.80881 | 0.77397 | 0.73094
43602.4812 | 1.2623 | 1.4947 | 1.3882 | 1.0338 | 0.91376 | 0.81016 | 0.77595 | 0.73113
43602.4813 | 1.2641 | 1.4936 | 1.3876 | 1.0334 | 0.91305 | 0.80919 | 0.77777 | 0.73112
43602.4813 | 1.2639 | 1.4952 | 1.388 | 1.0331 | 0.91492 | 0.81023 | 0.77594 | 0.73117
43602.4813 | 1.2529 | 1.4933 | 1.3864 | 1.0327 | 0.91294 | 0.80955 | 0.7749 | 0.73099
43602.4813 | 1.2458 | 1.4928 | 1.3866 | 1.0315 | 0.91321 | 0.81003 | 0.77517 | 0.73116
43602.4813 | 1.2576 | 1.4946 | 1.3863 | 1.033 | 0.91287 | 0.8101 | 0.77627 | 0.73086
43602.4812 | 1.2491 | 1.4879 | 1.382 | 1.0286 | 0.90934 | 0.80655 | 0.77267 | 0.72989
43602.4814 | 1.2552 | 1.4801 | 1.3744 | 1.0249 | 0.90586 | 0.80317 | 0.76914 | 0.72866
43602.4814 | 1.2419 | 1.4757 | 1.3714 | 1.0211 | 0.90453 | 0.80244 | 0.76828 | 0.72849
43602.4814 | 1.2439 | 1.4796 | 1.3734 | 1.0237 | 0.90271 | 0.80174 | 0.76735 | 0.72834
43602.4815 | 1.2374 | 1.475 | 1.3698 | 1.0201 | 0.90263 | 0.80128 | 0.76979 | 0.72758
43602.4815 | 1.2358 | 1.4782 | 1.3719 | 1.0221 | 0.90305 | 0.80192 | 0.76905 | 0.72826
43602.4815 | 1.2516 | 1.477 | 1.3714 | 1.0223 | 0.90287 | 0.80172 | 0.76788 | 0.7281
43602.4815 | 1.2475 | 1.4732 | 1.3689 | 1.0208 | 0.90355 | 0.8018 | 0.76754 | 0.72861
43602.4814 | 1.251 | 1.4729 | 1.3669 | 1.0207 | 0.90107 | 0.79976 | 0.76608 | 0.72774
43602.4816 | 1.2424 | 1.4699 | 1.3632 | 1.0183 | 0.89938 | 0.79837 | 0.76467 | 0.72683
43602.4816 | 1.2311 | 1.4688 | 1.3628 | 1.0179 | 0.89915 | 0.79818 | 0.76453 | 0.72647
43602.4816 | 1.2518 | 1.4734 | 1.3655 | 1.0205 | 0.89982 | 0.79877 | 0.76553 | 0.72685
43602.4817 | 1.2515 | 1.4724 | 1.3655 | 1.0211 | 0.90061 | 0.79928 | 0.7682 | 0.72702
43602.4817 | 1.2416 | 1.47 | 1.3638 | 1.0194 | 0.90056 | 0.79927 | 0.76602 | 0.72679
43602.4817 | 1.2414 | 1.4719 | 1.3658 | 1.0222 | 0.90114 | 0.80009 | 0.76658 | 0.72752
43602.4817 | 1.2379 | 1.4719 | 1.3647 | 1.0207 | 0.90184 | 0.80101 | 0.76674 | 0.72761
43602.4816 | 1.2475 | 1.4725 | 1.3651 | 1.0229 | 0.90172 | 0.80042 | 0.7665 | 0.72737
43602.4818 | 1.2491 | 1.4679 | 1.3603 | 1.0199 | 0.89913 | 0.79769 | 0.76437 | 0.72642
43602.4818 | 1.2387 | 1.4631 | 1.3563 | 1.0163 | 0.89785 | 0.79716 | 0.76613 | 0.72618
43602.4818 | 1.238 | 1.4655 | 1.3584 | 1.0186 | 0.89716 | 0.79705 | 0.76451 | 0.72572
43602.4818 | 1.2401 | 1.4674 | 1.3585 | 1.019 | 0.89885 | 0.79871 | 0.76488 | 0.72632
43602.4819 | 1.2467 | 1.4672 | 1.359 | 1.0195 | 0.89788 | 0.79735 | 0.76349 | 0.72614
43602.4819 | 1.2468 | 1.4639 | 1.3563 | 1.0173 | 0.89757 | 0.797 | 0.76572 | 0.72628
43602.4819 | 1.2358 | 1.4644 | 1.356 | 1.0175 | 0.89677 | 0.79621 | 0.76357 | 0.72551
43602.4818 | 1.2485 | 1.4678 | 1.3588 | 1.0203 | 0.89858 | 0.79775 | 0.76529 | 0.726
43602.482 | 1.2625 | 1.4788 | 1.3672 | 1.0273 | 0.90499 | 0.80271 | 0.76953 | 0.72791
43602.482 | 1.262 | 1.477 | 1.3668 | 1.0274 | 0.90403 | 0.80206 | 0.76776 | 0.7277
43602.482 | 1.2571 | 1.4783 | 1.3671 | 1.0271 | 0.90429 | 0.80278 | 0.76787 | 0.72769
43602.482 | 1.2567 | 1.4776 | 1.3678 | 1.0286 | 0.90429 | 0.80267 | 0.76784 | 0.72823
43602.482 | 1.2646 | 1.4808 | 1.3698 | 1.0299 | 0.90614 | 0.80389 | 0.77073 | 0.72824
43602.4821 | 1.2601 | 1.4807 | 1.37 | 1.0295 | 0.907 | 0.80429 | 0.77018 | 0.72816
43602.4821 | 1.2634 | 1.4826 | 1.3705 | 1.0304 | 0.9069 | 0.80402 | 0.7695 | 0.72819
43602.482 | 1.2593 | 1.479 | 1.3681 | 1.0266 | 0.90627 | 0.80373 | 0.77195 | 0.72822
43602.4822 | 1.2454 | 1.468 | 1.3614 | 1.0204 | 0.90018 | 0.79877 | 0.76549 | 0.72701
43602.4822 | 1.2475 | 1.4692 | 1.3616 | 1.0209 | 0.90116 | 0.79954 | 0.7658 | 0.72681
43602.4822 | 1.2491 | 1.467 | 1.3594 | 1.0184 | 0.89766 | 0.79686 | 0.76368 | 0.72621
43602.4822 | 1.2424 | 1.4647 | 1.3559 | 1.0157 | 0.89736 | 0.79707 | 0.76533 | 0.72596
43602.4822 | 1.2302 | 1.4653 | 1.3579 | 1.0169 | 0.89661 | 0.7964 | 0.76431 | 0.72497
43602.4823 | 1.2394 | 1.4634 | 1.3573 | 1.0163 | 0.8972 | 0.797 | 0.76399 | 0.72586
43602.4823 | 1.2388 | 1.4603 | 1.3545 | 1.0138 | 0.89516 | 0.79483 | 0.7617 | 0.72541
43602.4822 | 1.2301 | 1.4547 | 1.3501 | 1.0099 | 0.89112 | 0.79175 | 0.75949 | 0.72381
43602.4824 | 1.2149 | 1.4426 | 1.341 | 1.0014 | 0.88429 | 0.78551 | 0.75355 | 0.72117
43602.4824 | 1.2162 | 1.4456 | 1.3429 | 1.0033 | 0.88398 | 0.78595 | 0.75324 | 0.72157
43602.4824 | 1.2225 | 1.4455 | 1.3431 | 1.0037 | 0.88412 | 0.786 | 0.75689 | 0.72102
43602.4824 | 1.2227 | 1.4441 | 1.3419 | 1.002 | 0.8848 | 0.78604 | 0.75498 | 0.72151
43602.4824 | 1.2253 | 1.445 | 1.3429 | 1.0036 | 0.88468 | 0.78609 | 0.75408 | 0.7215
43602.4825 | 1.227 | 1.4465 | 1.3439 | 1.0042 | 0.88546 | 0.78642 | 0.75406 | 0.72171
43602.4825 | 1.2135 | 1.4442 | 1.3425 | 1.0018 | 0.88427 | 0.7858 | 0.75422 | 0.72106
43602.4824 | 1.2294 | 1.4454 | 1.3431 | 1.0038 | 0.88497 | 0.78611 | 0.75389 | 0.72113
43602.4826 | 1.2185 | 1.4418 | 1.3397 | 1.0003 | 0.8821 | 0.784 | 0.75218 | 0.71965
43602.4826 | 1.2146 | 1.4409 | 1.3392 | 0.99972 | 0.88123 | 0.78308 | 0.75164 | 0.72004
43602.4826 | 1.2121 | 1.4394 | 1.3376 | 0.99824 | 0.88238 | 0.78424 | 0.7529 | 0.71999
43602.4826 | 1.2133 | 1.4396 | 1.338 | 0.99837 | 0.87858 | 0.78138 | 0.75271 | 0.71886
43602.4826 | 1.2118 | 1.4387 | 1.3375 | 0.99784 | 0.88067 | 0.78241 | 0.75148 | 0.71928
43602.4826 | 1.2056 | 1.4357 | 1.3354 | 0.99533 | 0.87889 | 0.78127 | 0.74953 | 0.71846
43602.4827 | 1.218 | 1.4356 | 1.3346 | 0.9958 | 0.87803 | 0.78099 | 0.74887 | 0.71866
43602.4826 | 1.2052 | 1.4325 | 1.3323 | 0.99408 | 0.87658 | 0.77905 | 0.74802 | 0.71823
43602.4828 | 1.206 | 1.4272 | 1.3274 | 0.99093 | 0.8734 | 0.77633 | 0.7451 | 0.71702
43602.4828 | 1.1964 | 1.4237 | 1.3245 | 0.98842 | 0.87275 | 0.77618 | 0.74795 | 0.71713
43602.4828 | 1.2021 | 1.4241 | 1.3247 | 0.98859 | 0.87164 | 0.77566 | 0.74485 | 0.71662
43602.4828 | 1.2055 | 1.4274 | 1.3264 | 0.99068 | 0.87233 | 0.7764 | 0.74536 | 0.71746
43602.4828 | 1.1953 | 1.4253 | 1.3258 | 0.98985 | 0.87291 | 0.7759 | 0.7451 | 0.71698
43602.4828 | 1.2018 | 1.4255 | 1.326 | 0.98909 | 0.87256 | 0.77633 | 0.7452 | 0.71699
43602.4828 | 1.2074 | 1.4238 | 1.3247 | 0.98915 | 0.8722 | 0.77512 | 0.74598 | 0.71682
43602.483 | 1.1972 | 1.4167 | 1.3183 | 0.98416 | 0.86814 | 0.77253 | 0.74248 | 0.71584
43602.483 | 1.1995 | 1.4152 | 1.3165 | 0.98378 | 0.8667 | 0.7713 | 0.74369 | 0.71515
43602.483 | 1.2005 | 1.4139 | 1.3155 | 0.9822 | 0.86646 | 0.77079 | 0.74154 | 0.71487
43602.483 | 1.1991 | 1.4157 | 1.3171 | 0.98486 | 0.86603 | 0.7706 | 0.74096 | 0.71533
43602.483 | 1.1857 | 1.4078 | 1.3116 | 0.97892 | 0.86631 | 0.77077 | 0.74071 | 0.71513
43602.483 | 1.1845 | 1.4085 | 1.3109 | 0.97962 | 0.86349 | 0.76904 | 0.7395 | 0.71491
43602.483 | 1.1939 | 1.4061 | 1.3093 | 0.97844 | 0.86308 | 0.76832 | 0.73892 | 0.71471
43602.483 | 1.1819 | 1.4002 | 1.3038 | 0.97463 | 0.86001 | 0.7661 | 0.73965 | 0.71383
43602.4832 | 1.1724 | 1.393 | 1.2965 | 0.97081 | 0.85567 | 0.76306 | 0.73462 | 0.71248
43602.4832 | 1.183 | 1.3913 | 1.2946 | 0.96937 | 0.85493 | 0.76246 | 0.73401 | 0.71261
43602.4832 | 1.1794 | 1.3898 | 1.2934 | 0.96905 | 0.85516 | 0.76222 | 0.73489 | 0.71234
43602.4832 | 1.1782 | 1.3918 | 1.2942 | 0.96977 | 0.85404 | 0.76165 | 0.73562 | 0.7122
43602.4832 | 1.1739 | 1.388 | 1.2919 | 0.96783 | 0.85423 | 0.76149 | 0.73321 | 0.71205
43602.4832 | 1.1814 | 1.3924 | 1.2946 | 0.97051 | 0.85414 | 0.76193 | 0.73384 | 0.71264
43602.4832 | 1.1749 | 1.3937 | 1.2959 | 0.97158 | 0.85512 | 0.76249 | 0.73363 | 0.7117
43602.4831 | 1.1849 | 1.3946 | 1.2967 | 0.97284 | 0.85879 | 0.76507 | 0.73722 | 0.71348
43602.4834 | 1.1949 | 1.401 | 1.3016 | 0.9782 | 0.86097 | 0.76691 | 0.73844 | 0.71381
43602.4834 | 1.1837 | 1.4 | 1.3001 | 0.9772 | 0.86141 | 0.76734 | 0.73835 | 0.71404
43602.4834 | 1.1926 | 1.4031 | 1.3018 | 0.98003 | 0.86159 | 0.76764 | 0.73804 | 0.71418
43602.4834 | 1.1913 | 1.3983 | 1.2985 | 0.97625 | 0.86219 | 0.76813 | 0.73996 | 0.71428
43602.4834 | 1.1869 | 1.3982 | 1.2972 | 0.97568 | 0.8597 | 0.76597 | 0.7392 | 0.7137
43602.4834 | 1.1926 | 1.3968 | 1.2972 | 0.97552 | 0.85969 | 0.76567 | 0.73725 | 0.71348
43602.4834 | 1.1842 | 1.395 | 1.2957 | 0.97484 | 0.85875 | 0.76515 | 0.7357 | 0.71333
43602.4833 | 1.1833 | 1.3885 | 1.2909 | 0.97033 | 0.8562 | 0.76352 | 0.73486 | 0.71311
43602.4835 | 1.1781 | 1.3838 | 1.2861 | 0.96574 | 0.85195 | 0.75991 | 0.73175 | 0.71169
43602.4836 | 1.1799 | 1.386 | 1.2876 | 0.96815 | 0.85387 | 0.76123 | 0.73255 | 0.71227
43602.4836 | 1.1755 | 1.384 | 1.2867 | 0.96658 | 0.85179 | 0.7601 | 0.73341 | 0.71172
43602.4836 | 1.1754 | 1.386 | 1.2872 | 0.96725 | 0.85205 | 0.75981 | 0.73201 | 0.71151
43602.4836 | 1.1716 | 1.3855 | 1.2874 | 0.96721 | 0.85314 | 0.76123 | 0.73205 | 0.71193
43602.4836 | 1.1766 | 1.385 | 1.2877 | 0.96749 | 0.85186 | 0.76016 | 0.73297 | 0.71149
43602.4836 | 1.1747 | 1.3825 | 1.2859 | 0.96555 | 0.85203 | 0.76032 | 0.73454 | 0.71188
43602.4835 | 1.1723 | 1.3796 | 1.2829 | 0.96377 | 0.84969 | 0.75901 | 0.73337 | 0.71147
43602.4837 | 1.1668 | 1.3712 | 1.2763 | 0.95893 | 0.84625 | 0.75618 | 0.72955 | 0.71061
43602.4838 | 1.1668 | 1.3719 | 1.2767 | 0.95971 | 0.84597 | 0.75582 | 0.72791 | 0.71037
43602.4838 | 1.1606 | 1.3687 | 1.2743 | 0.9575 | 0.84443 | 0.7547 | 0.72689 | 0.70978
43602.4838 | 1.1654 | 1.3726 | 1.2767 | 0.95982 | 0.84512 | 0.75538 | 0.72939 | 0.71052
43602.4838 | 1.1566 | 1.3643 | 1.2706 | 0.95429 | 0.84394 | 0.75473 | 0.72784 | 0.71039
43602.4838 | 1.1634 | 1.3671 | 1.2724 | 0.95646 | 0.8415 | 0.75287 | 0.72592 | 0.70945
43602.4838 | 1.1572 | 1.3653 | 1.2708 | 0.95501 | 0.84324 | 0.75395 | 0.72684 | 0.70985
43602.4837 | 1.1601 | 1.3666 | 1.2717 | 0.95559 | 0.84203 | 0.75321 | 0.7258 | 0.70936
43602.4839 | 1.1639 | 1.371 | 1.2764 | 0.95845 | 0.84709 | 0.75618 | 0.72918 | 0.71036
43602.4839 | 1.1636 | 1.3706 | 1.2761 | 0.95825 | 0.84413 | 0.75439 | 0.72695 | 0.70972
43602.484 | 1.1654 | 1.3719 | 1.2776 | 0.96008 | 0.84687 | 0.75622 | 0.72865 | 0.71031
43602.484 | 1.1603 | 1.3729 | 1.2785 | 0.96012 | 0.84655 | 0.75641 | 0.72992 | 0.71022
43602.484 | 1.1665 | 1.3737 | 1.2779 | 0.95973 | 0.84691 | 0.7565 | 0.7304 | 0.71022
43602.484 | 1.1618 | 1.3707 | 1.2756 | 0.9576 | 0.84646 | 0.75587 | 0.72821 | 0.70988
43602.4839 | 1.1595 | 1.3698 | 1.2748 | 0.95745 | 0.84419 | 0.75498 | 0.7274 | 0.70975
43602.4841 | 1.1535 | 1.3613 | 1.2682 | 0.95225 | 0.83961 | 0.75134 | 0.724 | 0.70882
43602.4841 | 1.1493 | 1.3595 | 1.2671 | 0.95043 | 0.83989 | 0.7511 | 0.72565 | 0.70848
43602.4841 | 1.1478 | 1.3594 | 1.2673 | 0.95114 | 0.83995 | 0.75099 | 0.72585 | 0.70881
43602.4842 | 1.1432 | 1.3554 | 1.2649 | 0.94811 | 0.83792 | 0.74985 | 0.72349 | 0.7083
43602.4842 | 1.148 | 1.3564 | 1.2656 | 0.94907 | 0.83868 | 0.75004 | 0.72348 | 0.70858
43602.4842 | 1.1428 | 1.3545 | 1.2645 | 0.94849 | 0.83718 | 0.74907 | 0.72282 | 0.70794
43602.4842 | 1.1471 | 1.3571 | 1.2656 | 0.95013 | 0.83802 | 0.74948 | 0.72302 | 0.70808
43602.4841 | 1.1416 | 1.3532 | 1.2615 | 0.9462 | 0.83521 | 0.74763 | 0.72235 | 0.70702
43602.4843 | 1.1441 | 1.3555 | 1.2635 | 0.9483 | 0.83639 | 0.74801 | 0.72347 | 0.70704
43602.4843 | 1.1383 | 1.3523 | 1.2623 | 0.94595 | 0.83603 | 0.74781 | 0.72135 | 0.70721
43602.4843 | 1.1366 | 1.3526 | 1.2627 | 0.94625 | 0.83411 | 0.74694 | 0.72026 | 0.70667
43602.4843 | 1.1393 | 1.353 | 1.2627 | 0.94649 | 0.83526 | 0.74759 | 0.72074 | 0.70685
43602.4844 | 1.1429 | 1.3569 | 1.2648 | 0.9495 | 0.8365 | 0.74847 | 0.72405 | 0.70767
43602.4844 | 1.1376 | 1.3509 | 1.2612 | 0.94465 | 0.83593 | 0.74822 | 0.72393 | 0.70715
43602.4844 | 1.1417 | 1.3552 | 1.2634 | 0.94785 | 0.83469 | 0.74722 | 0.72148 | 0.70692
43602.4843 | 1.1388 | 1.3511 | 1.2617 | 0.9449 | 0.8359 | 0.74777 | 0.72141 | 0.70691
43602.4845 | 1.1416 | 1.3532 | 1.2624 | 0.94533 | 0.83385 | 0.74608 | 0.71998 | 0.70663
43602.4845 | 1.1447 | 1.3547 | 1.264 | 0.94728 | 0.83481 | 0.74707 | 0.72108 | 0.70733
43602.4845 | 1.1378 | 1.3527 | 1.2629 | 0.94597 | 0.83582 | 0.74791 | 0.72228 | 0.70728
43602.4845 | 1.1387 | 1.3535 | 1.2635 | 0.94683 | 0.83462 | 0.74753 | 0.72134 | 0.70728
43602.4846 | 1.14 | 1.3546 | 1.2639 | 0.94769 | 0.83598 | 0.74808 | 0.72279 | 0.70769
43602.4846 | 1.1359 | 1.3509 | 1.2623 | 0.94555 | 0.83517 | 0.74765 | 0.72132 | 0.70724
43602.4845 | 1.1417 | 1.3552 | 1.2638 | 0.94712 | 0.83425 | 0.7476 | 0.72158 | 0.70738
43602.4847 | 1.1433 | 1.3612 | 1.2714 | 0.95088 | 0.8382 | 0.75086 | 0.7247 | 0.70857
43602.4847 | 1.1417 | 1.3625 | 1.2725 | 0.95118 | 0.83902 | 0.75161 | 0.72672 | 0.70915
43602.4847 | 1.1436 | 1.3637 | 1.2743 | 0.95286 | 0.84061 | 0.7526 | 0.72645 | 0.70958
43602.4847 | 1.1484 | 1.3661 | 1.2757 | 0.9539 | 0.84061 | 0.75309 | 0.72618 | 0.70961
43602.4847 | 1.1503 | 1.3649 | 1.2758 | 0.9531 | 0.84177 | 0.75358 | 0.72686 | 0.70978
43602.4847 | 1.148 | 1.3654 | 1.2761 | 0.95261 | 0.84035 | 0.75294 | 0.72869 | 0.70946
43602.4848 | 1.1455 | 1.3687 | 1.2788 | 0.95545 | 0.84252 | 0.75444 | 0.72995 | 0.7102
43602.4847 | 1.1447 | 1.3667 | 1.2758 | 0.95311 | 0.84031 | 0.75322 | 0.7272 | 0.71015
43602.4849 | 1.126 | 1.3538 | 1.2688 | 0.94508 | 0.83472 | 0.75009 | 0.72533 | 0.70886
43602.4849 | 1.1258 | 1.353 | 1.2677 | 0.94465 | 0.83422 | 0.74997 | 0.72567 | 0.70892
43602.4849 | 1.1281 | 1.3529 | 1.2662 | 0.94324 | 0.83351 | 0.74929 | 0.72411 | 0.7088
43602.4849 | 1.122 | 1.3501 | 1.2657 | 0.94171 | 0.83241 | 0.74848 | 0.72252 | 0.70854
43602.4849 | 1.1174 | 1.3493 | 1.2642 | 0.94069 | 0.83134 | 0.74782 | 0.72421 | 0.70837
43602.4849 | 1.1211 | 1.3486 | 1.2638 | 0.93998 | 0.8309 | 0.74716 | 0.72422 | 0.70773
43602.4849 | 1.1142 | 1.3471 | 1.2637 | 0.93997 | 0.83072 | 0.74724 | 0.72149 | 0.70826
43602.4849 | 1.1125 | 1.3422 | 1.2592 | 0.936 | 0.82792 | 0.74482 | 0.719 | 0.70742
43602.4851 | 1.104 | 1.3318 | 1.2496 | 0.92828 | 0.82204 | 0.74012 | 0.71572 | 0.70568
43602.4851 | 1.1016 | 1.3312 | 1.2494 | 0.92892 | 0.82132 | 0.7395 | 0.71723 | 0.70519
43602.4851 | 1.1046 | 1.3305 | 1.2475 | 0.92764 | 0.82048 | 0.73877 | 0.7144 | 0.705
43602.4851 | 1.0979 | 1.3264 | 1.2448 | 0.92591 | 0.81951 | 0.73784 | 0.7133 | 0.70434
43602.4851 | 1.1038 | 1.3272 | 1.245 | 0.92583 | 0.81873 | 0.73725 | 0.71257 | 0.7044
43602.4851 | 1.096 | 1.3236 | 1.2426 | 0.92435 | 0.81753 | 0.73649 | 0.71427 | 0.70399
43602.4851 | 1.0992 | 1.3263 | 1.2445 | 0.92528 | 0.81815 | 0.73626 | 0.71374 | 0.70374
43602.4853 | 1.1246 | 1.3486 | 1.2611 | 0.93869 | 0.82818 | 0.74343 | 0.71786 | 0.70492
43602.4853 | 1.131 | 1.3533 | 1.2646 | 0.94254 | 0.82995 | 0.74478 | 0.71927 | 0.70555
43602.4853 | 1.1377 | 1.357 | 1.267 | 0.94497 | 0.83276 | 0.74677 | 0.72005 | 0.7062
43602.4853 | 1.1332 | 1.3612 | 1.2707 | 0.94776 | 0.8346 | 0.74828 | 0.72442 | 0.70674
43602.4853 | 1.1454 | 1.3657 | 1.2738 | 0.95168 | 0.83733 | 0.75071 | 0.72538 | 0.70762
43602.4853 | 1.1468 | 1.3672 | 1.2751 | 0.95232 | 0.83913 | 0.75178 | 0.72517 | 0.7076
43602.4853 | 1.1512 | 1.3688 | 1.2764 | 0.95343 | 0.8402 | 0.7529 | 0.72599 | 0.70835
43602.4852 | 1.1534 | 1.3727 | 1.28 | 0.95715 | 0.84455 | 0.75609 | 0.72894 | 0.70952
43602.4855 | 1.1481 | 1.3676 | 1.2772 | 0.95628 | 0.84303 | 0.75618 | 0.73114 | 0.70967
43602.4855 | 1.1534 | 1.3684 | 1.2775 | 0.9562 | 0.84403 | 0.7562 | 0.73055 | 0.71014
43602.4855 | 1.1443 | 1.366 | 1.2759 | 0.9537 | 0.84181 | 0.75519 | 0.72803 | 0.70907
43602.4855 | 1.1525 | 1.3691 | 1.2771 | 0.95654 | 0.84254 | 0.75558 | 0.72844 | 0.70946
43602.4855 | 1.1494 | 1.3657 | 1.275 | 0.95357 | 0.84175 | 0.75496 | 0.72773 | 0.70945
43602.4855 | 1.1519 | 1.3664 | 1.2755 | 0.9546 | 0.84192 | 0.75496 | 0.72901 | 0.70936
43602.4854 | 1.1446 | 1.3617 | 1.2721 | 0.9516 | 0.83994 | 0.7537 | 0.72873 | 0.70937
43602.4856 | 1.1285 | 1.3522 | 1.2655 | 0.94424 | 0.83522 | 0.75089 | 0.72634 | 0.70855
43602.4856 | 1.1317 | 1.3508 | 1.2637 | 0.94232 | 0.83307 | 0.74922 | 0.72281 | 0.70808
43602.4857 | 1.1296 | 1.3516 | 1.2651 | 0.94371 | 0.83332 | 0.74931 | 0.7239 | 0.70829
43602.4857 | 1.134 | 1.3545 | 1.2663 | 0.94506 | 0.83458 | 0.75004 | 0.72387 | 0.70855
43602.4857 | 1.1307 | 1.3525 | 1.2648 | 0.94454 | 0.83486 | 0.75004 | 0.72356 | 0.70818
43602.4857 | 1.1317 | 1.3514 | 1.2652 | 0.9442 | 0.83367 | 0.74987 | 0.7257 | 0.70849
43602.4857 | 1.1283 | 1.3525 | 1.2656 | 0.94487 | 0.83407 | 0.74967 | 0.72396 | 0.70825
43602.4856 | 1.1258 | 1.3529 | 1.2668 | 0.9449 | 0.83426 | 0.74961 | 0.72342 | 0.70866
43602.4858 | 1.113 | 1.3425 | 1.2602 | 0.93856 | 0.83106 | 0.74722 | 0.72157 | 0.70783
43602.4858 | 1.1253 | 1.3438 | 1.26 | 0.9391 | 0.83022 | 0.74692 | 0.72185 | 0.7075
43602.4859 | 1.1115 | 1.3394 | 1.2573 | 0.9358 | 0.82972 | 0.74594 | 0.72285 | 0.7069
43602.4859 | 1.1168 | 1.3399 | 1.2564 | 0.93633 | 0.82823 | 0.74561 | 0.72001 | 0.70708
43602.4859 | 1.1054 | 1.3361 | 1.255 | 0.93363 | 0.82807 | 0.74513 | 0.71936 | 0.70713
43602.4859 | 1.1091 | 1.3357 | 1.2536 | 0.93341 | 0.82601 | 0.74391 | 0.7187 | 0.70675
43602.4858 | 1.1059 | 1.3328 | 1.2509 | 0.93144 | 0.8254 | 0.74307 | 0.71829 | 0.70609
43602.486 | 1.1068 | 1.3319 | 1.2501 | 0.93057 | 0.82386 | 0.74186 | 0.71711 | 0.70604
43602.486 | 1.1098 | 1.3324 | 1.2502 | 0.93072 | 0.82415 | 0.74205 | 0.71894 | 0.70565
43602.486 | 1.111 | 1.3327 | 1.251 | 0.93183 | 0.82399 | 0.74162 | 0.7184 | 0.70546
43602.486 | 1.101 | 1.3298 | 1.2502 | 0.9302 | 0.82363 | 0.74121 | 0.71622 | 0.7051
43602.4861 | 1.108 | 1.3317 | 1.2503 | 0.93038 | 0.8236 | 0.74133 | 0.71596 | 0.70527
43602.4861 | 1.1086 | 1.332 | 1.2504 | 0.93078 | 0.82433 | 0.74176 | 0.71684 | 0.70524
43602.486 | 1.1098 | 1.334 | 1.2525 | 0.93148 | 0.82452 | 0.74216 | 0.71679 | 0.70535
43602.4862 | 1.1124 | 1.3398 | 1.2579 | 0.93511 | 0.82645 | 0.7439 | 0.71899 | 0.70601
43602.4862 | 1.1114 | 1.342 | 1.2599 | 0.93742 | 0.82833 | 0.74548 | 0.71975 | 0.7064
43602.4862 | 1.1108 | 1.3385 | 1.2584 | 0.93512 | 0.82845 | 0.74532 | 0.71898 | 0.70618
43602.4862 | 1.1134 | 1.3381 | 1.2569 | 0.93407 | 0.82717 | 0.74414 | 0.72059 | 0.70556
43602.4862 | 1.1107 | 1.3382 | 1.2571 | 0.93478 | 0.82755 | 0.74468 | 0.72016 | 0.70631
43602.4862 | 1.1094 | 1.3378 | 1.2569 | 0.93451 | 0.82739 | 0.74451 | 0.7192 | 0.70616
43602.4863 | 1.1085 | 1.3354 | 1.2549 | 0.93339 | 0.82701 | 0.74442 | 0.7193 | 0.70625
43602.4862 | 1.1042 | 1.3336 | 1.2535 | 0.93191 | 0.82558 | 0.74298 | 0.71831 | 0.70562
43602.4864 | 1.098 | 1.3276 | 1.2504 | 0.92858 | 0.82314 | 0.74181 | 0.71784 | 0.70529
43602.4864 | 1.1063 | 1.3295 | 1.2509 | 0.92918 | 0.82315 | 0.7414 | 0.71593 | 0.70475
43602.4864 | 1.1032 | 1.3301 | 1.2514 | 0.92962 | 0.82322 | 0.74139 | 0.71575 | 0.70462
43602.4864 | 1.1013 | 1.3278 | 1.2495 | 0.92841 | 0.82317 | 0.74124 | 0.71795 | 0.70479
43602.4864 | 1.106 | 1.3286 | 1.249 | 0.92707 | 0.82191 | 0.74046 | 0.71568 | 0.70431
43602.4864 | 1.1046 | 1.3281 | 1.2499 | 0.92832 | 0.82226 | 0.74073 | 0.71555 | 0.70418
43602.4864 | 1.1076 | 1.3319 | 1.2528 | 0.93069 | 0.82383 | 0.74146 | 0.71609 | 0.7049
43602.4866 | 1.1066 | 1.3367 | 1.2579 | 0.93319 | 0.8281 | 0.74539 | 0.72126 | 0.70634
43602.4866 | 1.1114 | 1.3381 | 1.2593 | 0.93412 | 0.8282 | 0.74533 | 0.72013 | 0.7061
43602.4866 | 1.11 | 1.3389 | 1.2602 | 0.93543 | 0.82807 | 0.74521 | 0.71938 | 0.70612
43602.4866 | 1.1106 | 1.3376 | 1.2591 | 0.93461 | 0.82875 | 0.74592 | 0.72003 | 0.70664
43602.4866 | 1.1125 | 1.3356 | 1.2567 | 0.93374 | 0.82832 | 0.7453 | 0.72063 | 0.70662
43602.4866 | 1.1076 | 1.3343 | 1.2562 | 0.93216 | 0.82642 | 0.74391 | 0.71845 | 0.70571
43602.4865 | 1.1004 | 1.3349 | 1.257 | 0.93251 | 0.82662 | 0.74415 | 0.71985 | 0.70601
43602.4867 | 1.1145 | 1.3446 | 1.2648 | 0.93824 | 0.8315 | 0.74796 | 0.72504 | 0.70744
43602.4868 | 1.1187 | 1.3484 | 1.268 | 0.94019 | 0.8313 | 0.74747 | 0.72194 | 0.70673
43602.4868 | 1.1264 | 1.3517 | 1.2705 | 0.94263 | 0.83268 | 0.74875 | 0.72271 | 0.70675
43602.4868 | 1.1272 | 1.3543 | 1.2725 | 0.94449 | 0.83494 | 0.75016 | 0.7238 | 0.70749
43602.4868 | 1.1237 | 1.3528 | 1.2722 | 0.94308 | 0.83593 | 0.75104 | 0.72509 | 0.70777
43602.4868 | 1.1237 | 1.3525 | 1.2723 | 0.9432 | 0.83459 | 0.75061 | 0.72425 | 0.70788
43602.4867 | 1.1197 | 1.3541 | 1.2741 | 0.94479 | 0.83569 | 0.75184 | 0.72592 | 0.7083
43602.4869 | 1.1204 | 1.3513 | 1.272 | 0.94419 | 0.83635 | 0.75269 | 0.72854 | 0.70881
43602.4869 | 1.1228 | 1.3526 | 1.272 | 0.94374 | 0.83537 | 0.75158 | 0.72585 | 0.70803
43602.4869 | 1.123 | 1.352 | 1.2716 | 0.94384 | 0.83543 | 0.75156 | 0.72522 | 0.70852
43602.487 | 1.1292 | 1.3519 | 1.2713 | 0.9434 | 0.8351 | 0.75118 | 0.72443 | 0.7081
43602.487 | 1.1281 | 1.3511 | 1.271 | 0.94321 | 0.83521 | 0.75105 | 0.72573 | 0.70835
43602.487 | 1.1237 | 1.3507 | 1.2708 | 0.94313 | 0.83502 | 0.75097 | 0.72501 | 0.70822
43602.4869 | 1.127 | 1.3498 | 1.27 | 0.94291 | 0.83449 | 0.75091 | 0.72409 | 0.70781
43602.4871 | 1.1256 | 1.3499 | 1.269 | 0.94321 | 0.8342 | 0.75052 | 0.72609 | 0.70733
43602.4871 | 1.1286 | 1.3507 | 1.269 | 0.94327 | 0.83457 | 0.75121 | 0.72508 | 0.70854
43602.4871 | 1.1278 | 1.3508 | 1.2692 | 0.94354 | 0.83509 | 0.75104 | 0.72441 | 0.70792
43602.4871 | 1.1249 | 1.3523 | 1.2702 | 0.94553 | 0.8353 | 0.75161 | 0.72767 | 0.7081
43602.4871 | 1.127 | 1.3515 | 1.2696 | 0.94483 | 0.83676 | 0.75279 | 0.72764 | 0.70884
43602.4872 | 1.1324 | 1.3528 | 1.2703 | 0.94427 | 0.83563 | 0.75189 | 0.72557 | 0.70787
43602.4871 | 1.1292 | 1.3569 | 1.2745 | 0.9485 | 0.83793 | 0.7534 | 0.72674 | 0.70872
43602.4873 | 1.1563 | 1.3729 | 1.2868 | 0.95948 | 0.84662 | 0.75967 | 0.73185 | 0.7107
43602.4873 | 1.1528 | 1.3726 | 1.2875 | 0.96022 | 0.8479 | 0.76091 | 0.73302 | 0.71105
43602.4873 | 1.1573 | 1.3752 | 1.2893 | 0.96186 | 0.84872 | 0.7617 | 0.73427 | 0.7112
43602.4873 | 1.1577 | 1.378 | 1.2914 | 0.96355 | 0.84998 | 0.76223 | 0.73682 | 0.71165
43602.4873 | 1.1565 | 1.3781 | 1.2917 | 0.96354 | 0.85148 | 0.76343 | 0.73542 | 0.71207
43602.4873 | 1.1564 | 1.377 | 1.291 | 0.96343 | 0.85081 | 0.76318 | 0.73498 | 0.71166
43602.4873 | 1.1548 | 1.3771 | 1.2917 | 0.96338 | 0.85102 | 0.76334 | 0.73558 | 0.71176
43602.4875 | 1.1477 | 1.3702 | 1.2861 | 0.96043 | 0.84892 | 0.76209 | 0.73437 | 0.71246
43602.4875 | 1.1498 | 1.3692 | 1.2843 | 0.95891 | 0.84774 | 0.76153 | 0.73603 | 0.71207
43602.4875 | 1.1537 | 1.3691 | 1.284 | 0.95842 | 0.84716 | 0.76073 | 0.73441 | 0.71172
43602.4875 | 1.1472 | 1.3673 | 1.2826 | 0.95767 | 0.84706 | 0.76092 | 0.73352 | 0.71227
43602.4875 | 1.1406 | 1.3667 | 1.2828 | 0.9577 | 0.84605 | 0.76018 | 0.73301 | 0.71148
43602.4875 | 1.1437 | 1.3664 | 1.2826 | 0.95765 | 0.84626 | 0.76037 | 0.73566 | 0.71214
43602.4875 | 1.141 | 1.3654 | 1.2831 | 0.95709 | 0.84643 | 0.76043 | 0.73358 | 0.71179
43602.4876 | 1.1381 | 1.3683 | 1.2858 | 0.95841 | 0.84745 | 0.76144 | 0.73408 | 0.71216
43602.4877 | 1.1484 | 1.3719 | 1.2871 | 0.96007 | 0.84827 | 0.76155 | 0.73725 | 0.71214
43602.4877 | 1.1465 | 1.3716 | 1.2874 | 0.96018 | 0.84945 | 0.76248 | 0.73606 | 0.71254
43602.4877 | 1.1547 | 1.3733 | 1.2892 | 0.9616 | 0.85035 | 0.76347 | 0.73623 | 0.71288
43602.4877 | 1.1506 | 1.3717 | 1.2883 | 0.96048 | 0.8498 | 0.76292 | 0.73524 | 0.71273
43602.4877 | 1.1534 | 1.3747 | 1.2911 | 0.96227 | 0.85011 | 0.76319 | 0.73604 | 0.71276
43602.4876 | 1.1583 | 1.3779 | 1.2933 | 0.96472 | 0.85224 | 0.76512 | 0.73776 | 0.71354
43602.4878 | 1.1583 | 1.3836 | 1.2991 | 0.96791 | 0.85662 | 0.76839 | 0.74029 | 0.71525
43602.4878 | 1.1624 | 1.3836 | 1.2989 | 0.96802 | 0.85567 | 0.76781 | 0.74124 | 0.7145
43602.4879 | 1.1618 | 1.3828 | 1.2986 | 0.96818 | 0.85572 | 0.76814 | 0.7403 | 0.71504
43602.4879 | 1.1534 | 1.3828 | 1.2998 | 0.96893 | 0.85641 | 0.76873 | 0.7402 | 0.71507
43602.4879 | 1.1597 | 1.3862 | 1.3012 | 0.97019 | 0.85728 | 0.76886 | 0.74219 | 0.71509
43602.4879 | 1.156 | 1.3832 | 1.2989 | 0.96835 | 0.85757 | 0.7693 | 0.74335 | 0.71534
43602.4878 | 1.155 | 1.3832 | 1.3001 | 0.96735 | 0.85583 | 0.76789 | 0.74113 | 0.71468
43602.488 | 1.1606 | 1.3895 | 1.3056 | 0.9721 | 0.85873 | 0.77009 | 0.74277 | 0.71502
43602.488 | 1.1635 | 1.3916 | 1.3076 | 0.97284 | 0.86031 | 0.77089 | 0.74275 | 0.71535
43602.488 | 1.167 | 1.392 | 1.3069 | 0.97233 | 0.85971 | 0.77095 | 0.74241 | 0.71557
43602.488 | 1.1589 | 1.3912 | 1.3071 | 0.97197 | 0.86088 | 0.77161 | 0.7447 | 0.71568
43602.4881 | 1.1652 | 1.3946 | 1.3097 | 0.97459 | 0.86154 | 0.77208 | 0.74406 | 0.71561
43602.4881 | 1.1647 | 1.3937 | 1.3097 | 0.97333 | 0.86202 | 0.77229 | 0.74402 | 0.71598
43602.488 | 1.1578 | 1.3921 | 1.3098 | 0.9731 | 0.86149 | 0.77236 | 0.74357 | 0.71608
43602.4882 | 1.1631 | 1.3915 | 1.3084 | 0.9726 | 0.86036 | 0.77165 | 0.74303 | 0.71579
43602.4882 | 1.1505 | 1.3906 | 1.3093 | 0.97161 | 0.86092 | 0.77178 | 0.74595 | 0.71544
43602.4882 | 1.1597 | 1.3916 | 1.3091 | 0.97142 | 0.85944 | 0.77099 | 0.74338 | 0.71464
43602.4882 | 1.1561 | 1.3912 | 1.3089 | 0.97222 | 0.86057 | 0.77172 | 0.74292 | 0.71545
43602.4882 | 1.1566 | 1.3914 | 1.3092 | 0.97143 | 0.85957 | 0.77063 | 0.74167 | 0.71484
43602.4883 | 1.1585 | 1.3919 | 1.3096 | 0.97251 | 0.86013 | 0.77114 | 0.74237 | 0.71456
43602.4882 | 1.1583 | 1.3947 | 1.3114 | 0.97285 | 0.86093 | 0.77158 | 0.74489 | 0.71517
43602.4884 | 1.1659 | 1.3974 | 1.3147 | 0.9742 | 0.8625 | 0.77277 | 0.74472 | 0.71504
43602.4884 | 1.1671 | 1.4001 | 1.3165 | 0.97664 | 0.86263 | 0.77337 | 0.74367 | 0.71511
43602.4884 | 1.1658 | 1.4013 | 1.3175 | 0.97679 | 0.86382 | 0.77396 | 0.74526 | 0.71533
43602.4884 | 1.1688 | 1.4023 | 1.319 | 0.97747 | 0.86401 | 0.77451 | 0.74827 | 0.71531
43602.4884 | 1.1716 | 1.405 | 1.3211 | 0.97877 | 0.8648 | 0.77452 | 0.74595 | 0.71474
43602.4884 | 1.172 | 1.4075 | 1.323 | 0.9807 | 0.86621 | 0.77556 | 0.74642 | 0.71498
43602.4884 | 1.173 | 1.4092 | 1.3253 | 0.98231 | 0.86808 | 0.77721 | 0.74818 | 0.71586
43602.4886 | 1.1763 | 1.4136 | 1.3285 | 0.9849 | 0.8706 | 0.77923 | 0.7494 | 0.71671
43602.4886 | 1.179 | 1.4152 | 1.3297 | 0.98598 | 0.87179 | 0.78004 | 0.74996 | 0.717
43602.4886 | 1.1785 | 1.415 | 1.3296 | 0.98572 | 0.87162 | 0.77972 | 0.75335 | 0.71708
43602.4886 | 1.176 | 1.415 | 1.3294 | 0.98567 | 0.87138 | 0.78006 | 0.75111 | 0.71705
43602.4886 | 1.1825 | 1.4144 | 1.3292 | 0.98569 | 0.87182 | 0.78008 | 0.75049 | 0.71701
43602.4886 | 1.176 | 1.4124 | 1.3275 | 0.98305 | 0.87165 | 0.77995 | 0.74999 | 0.71721
43602.4885 | 1.1788 | 1.4122 | 1.3273 | 0.9837 | 0.87057 | 0.77923 | 0.74947 | 0.71668
43602.4887 | 1.1815 | 1.415 | 1.3293 | 0.9859 | 0.87123 | 0.78028 | 0.75069 | 0.71755
43602.4888 | 1.1871 | 1.4155 | 1.3294 | 0.98596 | 0.87194 | 0.7805 | 0.75028 | 0.717
43602.4888 | 1.1756 | 1.4147 | 1.3295 | 0.98586 | 0.87124 | 0.77991 | 0.74981 | 0.71671
43602.4888 | 1.1804 | 1.4161 | 1.3301 | 0.98726 | 0.87107 | 0.77969 | 0.75141 | 0.71674
43602.4888 | 1.1821 | 1.4151 | 1.3293 | 0.98651 | 0.87244 | 0.78101 | 0.7517 | 0.71769
43602.4888 | 1.181 | 1.4152 | 1.3299 | 0.9873 | 0.87199 | 0.78069 | 0.75044 | 0.71744
43602.4887 | 1.1828 | 1.4156 | 1.3301 | 0.9869 | 0.87128 | 0.77999 | 0.75139 | 0.7166
43602.4889 | 1.1944 | 1.4237 | 1.3368 | 0.9938 | 0.87667 | 0.78396 | 0.75379 | 0.71866
43602.4889 | 1.2007 | 1.4254 | 1.3374 | 0.99544 | 0.87925 | 0.78567 | 0.7554 | 0.71957
43602.489 | 1.1915 | 1.4257 | 1.3376 | 0.99433 | 0.87829 | 0.78509 | 0.75469 | 0.71866
43602.489 | 1.1949 | 1.4266 | 1.3401 | 0.99679 | 0.87895 | 0.78558 | 0.7577 | 0.71945
43602.489 | 1.1966 | 1.4282 | 1.3408 | 0.99733 | 0.88056 | 0.78688 | 0.75699 | 0.71977
43602.489 | 1.1984 | 1.4278 | 1.3402 | 0.99619 | 0.8806 | 0.78669 | 0.75625 | 0.71951
43602.4889 | 1.2085 | 1.4377 | 1.3484 | 1.0039 | 0.88562 | 0.79068 | 0.76143 | 0.72088
43602.4891 | 1.2159 | 1.4433 | 1.3536 | 1.0072 | 0.88922 | 0.79348 | 0.76453 | 0.72233
43602.4891 | 1.2092 | 1.4429 | 1.3537 | 1.0071 | 0.88943 | 0.79373 | 0.76311 | 0.72256
43602.4891 | 1.2119 | 1.4451 | 1.3548 | 1.0083 | 0.89035 | 0.79415 | 0.76256 | 0.7225
43602.4891 | 1.2092 | 1.4435 | 1.3543 | 1.0078 | 0.89069 | 0.79451 | 0.76295 | 0.72297
43602.4892 | 1.2093 | 1.4417 | 1.3525 | 1.0069 | 0.88942 | 0.7938 | 0.76517 | 0.72262
43602.4892 | 1.2079 | 1.4416 | 1.3522 | 1.0067 | 0.88871 | 0.79322 | 0.76313 | 0.72222
43602.4891 | 1.2032 | 1.4399 | 1.3514 | 1.0052 | 0.88915 | 0.79376 | 0.7627 | 0.72274
43602.4893 | 1.2011 | 1.4352 | 1.3477 | 1.0025 | 0.8862 | 0.79244 | 0.76156 | 0.72276
43602.4893 | 1.1964 | 1.4337 | 1.3472 | 1.0009 | 0.88653 | 0.79193 | 0.76068 | 0.72282
43602.4893 | 1.1975 | 1.4329 | 1.3471 | 1.0013 | 0.88573 | 0.79154 | 0.76088 | 0.72258
43602.4893 | 1.1967 | 1.4342 | 1.3476 | 1.0008 | 0.88592 | 0.79166 | 0.76333 | 0.72242
43602.4893 | 1.1934 | 1.4331 | 1.3473 | 1.0014 | 0.8853 | 0.79106 | 0.76087 | 0.72202
43602.4894 | 1.189 | 1.4327 | 1.3468 | 1 | 0.88557 | 0.79124 | 0.76066 | 0.72235
43602.4893 | 1.1957 | 1.4322 | 1.3464 | 0.9986 | 0.88422 | 0.79014 | 0.75967 | 0.72182
43602.4895 | 1.1938 | 1.4335 | 1.3476 | 1.0002 | 0.88433 | 0.79048 | 0.76088 | 0.72171
43602.4895 | 1.1939 | 1.4339 | 1.3488 | 1.0014 | 0.88555 | 0.79116 | 0.76137 | 0.7218
43602.4895 | 1.1922 | 1.4336 | 1.3481 | 1.0005 | 0.88626 | 0.79135 | 0.76082 | 0.72189
43602.4895 | 1.1972 | 1.4338 | 1.3479 | 1.0014 | 0.88406 | 0.78972 | 0.75935 | 0.72072
43602.4895 | 1.1962 | 1.4362 | 1.3506 | 1.0023 | 0.88605 | 0.79133 | 0.76258 | 0.72153
43602.4895 | 1.199 | 1.4385 | 1.3514 | 1.0042 | 0.88698 | 0.79212 | 0.76238 | 0.72198
43602.4895 | 1.2059 | 1.4411 | 1.3544 | 1.0057 | 0.88888 | 0.79327 | 0.7625 | 0.72179
43602.4897 | 1.2184 | 1.4607 | 1.3718 | 1.0176 | 0.89791 | 0.80024 | 0.7683 | 0.72399
43602.4897 | 1.2226 | 1.4621 | 1.3732 | 1.0189 | 0.89983 | 0.80183 | 0.77226 | 0.72443
43602.4897 | 1.222 | 1.464 | 1.3742 | 1.0204 | 0.90052 | 0.80264 | 0.77074 | 0.72476
43602.4897 | 1.2233 | 1.4664 | 1.3762 | 1.0225 | 0.90168 | 0.80362 | 0.77107 | 0.72547
43602.4897 | 1.2309 | 1.4735 | 1.3835 | 1.0267 | 0.90648 | 0.80745 | 0.776 | 0.72671
43602.4898 | 1.2277 | 1.4752 | 1.3858 | 1.0276 | 0.9075 | 0.80811 | 0.77543 | 0.72698
43602.4899 | 1.2298 | 1.4762 | 1.3867 | 1.0275 | 0.90824 | 0.80882 | 0.77576 | 0.72756
43602.4899 | 1.2345 | 1.4766 | 1.3869 | 1.0291 | 0.90903 | 0.80953 | 0.77952 | 0.72849
43602.4898 | 1.2218 | 1.469 | 1.3805 | 1.0226 | 0.90483 | 0.80693 | 0.77441 | 0.72791
43602.49 | 1.2163 | 1.4617 | 1.3752 | 1.0185 | 0.90067 | 0.8032 | 0.7705 | 0.72619
43602.49 | 1.2167 | 1.4603 | 1.3743 | 1.0179 | 0.90074 | 0.80366 | 0.77334 | 0.72645
43602.49 | 1.2096 | 1.4587 | 1.3738 | 1.0163 | 0.90061 | 0.80334 | 0.77409 | 0.72622
43602.49 | 1.2166 | 1.4594 | 1.3721 | 1.0159 | 0.89768 | 0.80063 | 0.77053 | 0.72441
43602.4902 | 1.2117 | 1.4567 | 1.3712 | 1.0155 | 0.89708 | 0.80043 | 0.76889 | 0.72423
43602.4902 | 1.2147 | 1.457 | 1.3707 | 1.0151 | 0.89728 | 0.80032 | 0.76875 | 0.72372
43602.4902 | 1.2109 | 1.4571 | 1.372 | 1.0152 | 0.89827 | 0.80091 | 0.76845 | 0.72423
43602.4902 | 1.2195 | 1.4596 | 1.3724 | 1.0165 | 0.89884 | 0.80153 | 0.7714 | 0.72465
43602.4902 | 1.223 | 1.462 | 1.3743 | 1.0174 | 0.89924 | 0.80141 | 0.77052 | 0.72418
43602.4902 | 1.2205 | 1.4618 | 1.3744 | 1.0178 | 0.8996 | 0.80198 | 0.77007 | 0.7243
43602.4902 | 1.2257 | 1.4681 | 1.3797 | 1.0226 | 0.90234 | 0.80409 | 0.77156 | 0.72471
43602.4904 | 1.2376 | 1.4774 | 1.3872 | 1.029 | 0.90853 | 0.80861 | 0.77557 | 0.72603
43602.4904 | 1.2366 | 1.477 | 1.3874 | 1.0291 | 0.90934 | 0.80939 | 0.77884 | 0.72635
43602.4904 | 1.2401 | 1.4785 | 1.3893 | 1.0314 | 0.90973 | 0.80936 | 0.77686 | 0.72632
43602.4904 | 1.2395 | 1.4809 | 1.3904 | 1.0321 | 0.91121 | 0.81055 | 0.77747 | 0.72709
43602.4904 | 1.2402 | 1.4827 | 1.3923 | 1.0334 | 0.91246 | 0.81144 | 0.77784 | 0.72738
43602.4904 | 1.2466 | 1.4834 | 1.3926 | 1.0334 | 0.91226 | 0.81194 | 0.77802 | 0.72732
43602.4904 | 1.247 | 1.4864 | 1.395 | 1.0372 | 0.91515 | 0.81511 | 0.78114 | 0.72893
43602.4906 | 1.2503 | 1.4893 | 1.397 | 1.0404 | 0.91719 | 0.81678 | 0.78279 | 0.72996
43602.4906 | 1.2566 | 1.4898 | 1.3971 | 1.0405 | 0.91787 | 0.81695 | 0.78342 | 0.73031
43602.4906 | 1.2458 | 1.4895 | 1.3969 | 1.0403 | 0.91848 | 0.81724 | 0.7832 | 0.7303
43602.4906 | 1.2523 | 1.4902 | 1.3976 | 1.0407 | 0.91749 | 0.81652 | 0.7824 | 0.72954
43602.4906 | 1.2569 | 1.4908 | 1.3984 | 1.0411 | 0.91863 | 0.81749 | 0.7868 | 0.73057
43602.4906 | 1.2564 | 1.4915 | 1.3985 | 1.0423 | 0.91922 | 0.81839 | 0.78715 | 0.73085
43602.4905 | 1.2523 | 1.4914 | 1.3989 | 1.0427 | 0.91985 | 0.81841 | 0.7846 | 0.73107
43602.4907 | 1.2542 | 1.4874 | 1.3956 | 1.0404 | 0.91848 | 0.81811 | 0.78399 | 0.7319
43602.4907 | 1.2537 | 1.4867 | 1.3948 | 1.0399 | 0.91827 | 0.81788 | 0.78438 | 0.73216
43602.4908 | 1.2553 | 1.4873 | 1.3955 | 1.0402 | 0.91814 | 0.81783 | 0.78402 | 0.7322
43602.4908 | 1.2506 | 1.4864 | 1.3951 | 1.0398 | 0.91848 | 0.81794 | 0.78402 | 0.73163
43602.4908 | 1.251 | 1.485 | 1.3946 | 1.0389 | 0.91808 | 0.81818 | 0.78752 | 0.73234
43602.4908 | 1.2421 | 1.4844 | 1.3934 | 1.0383 | 0.91665 | 0.81672 | 0.78384 | 0.73125
43602.4907 | 1.2468 | 1.4863 | 1.393 | 1.0372 | 0.91519 | 0.81501 | 0.78109 | 0.73
43602.4909 | 1.2475 | 1.4864 | 1.3936 | 1.0388 | 0.91672 | 0.81641 | 0.78331 | 0.73126
43602.4909 | 1.2444 | 1.4847 | 1.3927 | 1.0369 | 0.91774 | 0.81669 | 0.78316 | 0.73145
43602.4909 | 1.2479 | 1.4855 | 1.3936 | 1.0373 | 0.91577 | 0.81562 | 0.782 | 0.73086
43602.491 | 1.2445 | 1.4847 | 1.3929 | 1.037 | 0.91588 | 0.8159 | 0.78177 | 0.73099
43602.491 | 1.2451 | 1.4857 | 1.3925 | 1.0363 | 0.91719 | 0.81701 | 0.7836 | 0.73175
43602.491 | 1.2432 | 1.4845 | 1.3916 | 1.0352 | 0.91565 | 0.81581 | 0.7845 | 0.73075
43602.4909 | 1.2427 | 1.4823 | 1.3907 | 1.0352 | 0.91465 | 0.81485 | 0.78277 | 0.73092
43602.4911 | 1.2362 | 1.4736 | 1.3823 | 1.0297 | 0.91085 | 0.81149 | 0.77856 | 0.72978
43602.4911 | 1.2306 | 1.4731 | 1.3827 | 1.0301 | 0.91006 | 0.81032 | 0.77801 | 0.72937
43602.4911 | 1.2377 | 1.4727 | 1.3822 | 1.0297 | 0.91109 | 0.81127 | 0.78017 | 0.72967
43602.4911 | 1.2376 | 1.4725 | 1.3821 | 1.03 | 0.91052 | 0.81143 | 0.77915 | 0.73009
43602.4911 | 1.2338 | 1.4729 | 1.3828 | 1.0298 | 0.90997 | 0.81079 | 0.77762 | 0.72934
43602.4912 | 1.2373 | 1.4738 | 1.3828 | 1.0305 | 0.91068 | 0.81153 | 0.77843 | 0.72998
43602.4911 | 1.2424 | 1.4785 | 1.3863 | 1.0341 | 0.91231 | 0.81284 | 0.77949 | 0.73002
43602.4913 | 1.243 | 1.4807 | 1.3887 | 1.0359 | 0.9154 | 0.8152 | 0.78265 | 0.73072
43602.4913 | 1.249 | 1.4809 | 1.3883 | 1.0358 | 0.91522 | 0.81547 | 0.78215 | 0.73134
43602.4913 | 1.2445 | 1.4788 | 1.3867 | 1.0346 | 0.91469 | 0.81479 | 0.78236 | 0.73118
43602.4913 | 1.2434 | 1.4793 | 1.3872 | 1.0347 | 0.9138 | 0.81395 | 0.78077 | 0.7304
43602.4913 | 1.2504 | 1.4807 | 1.3876 | 1.0356 | 0.91508 | 0.81523 | 0.78166 | 0.73142
43602.4913 | 1.2462 | 1.4779 | 1.3863 | 1.0352 | 0.91412 | 0.81454 | 0.78216 | 0.73045
43602.4913 | 1.2455 | 1.4746 | 1.3816 | 1.0328 | 0.91252 | 0.81306 | 0.7827 | 0.73025
43602.4915 | 1.2454 | 1.4723 | 1.3795 | 1.0333 | 0.9123 | 0.81262 | 0.78099 | 0.73037
43602.4915 | 1.2409 | 1.4703 | 1.3791 | 1.0317 | 0.91225 | 0.81295 | 0.7801 | 0.73111
43602.4915 | 1.2341 | 1.4681 | 1.3778 | 1.0308 | 0.91095 | 0.81182 | 0.7789 | 0.72982
43602.4915 | 1.2418 | 1.4701 | 1.3777 | 1.0321 | 0.91176 | 0.81248 | 0.7797 | 0.73061
43602.4915 | 1.2442 | 1.4708 | 1.3781 | 1.0329 | 0.9109 | 0.81133 | 0.77814 | 0.72929
43602.4915 | 1.2429 | 1.4697 | 1.3777 | 1.0318 | 0.91205 | 0.81255 | 0.78168 | 0.73021
43602.4915 | 1.2445 | 1.4732 | 1.3802 | 1.0358 | 0.91402 | 0.814 | 0.78157 | 0.73059
43602.4917 | 1.2413 | 1.4716 | 1.379 | 1.0357 | 0.91404 | 0.81417 | 0.78175 | 0.73087
43602.4917 | 1.2497 | 1.4728 | 1.3793 | 1.0352 | 0.91333 | 0.81368 | 0.78061 | 0.73037
43602.4917 | 1.2482 | 1.4745 | 1.38 | 1.0368 | 0.91448 | 0.81441 | 0.78095 | 0.73073
43602.4917 | 1.2441 | 1.471 | 1.3783 | 1.0358 | 0.91385 | 0.81424 | 0.78101 | 0.73047
43602.4917 | 1.2505 | 1.4713 | 1.3784 | 1.0351 | 0.91372 | 0.81419 | 0.78275 | 0.73054
43602.4917 | 1.2486 | 1.474 | 1.3797 | 1.0376 | 0.9135 | 0.81355 | 0.78148 | 0.73027
43602.4917 | 1.2504 | 1.4727 | 1.378 | 1.0362 | 0.91368 | 0.81469 | 0.78136 | 0.73113
43602.4918 | 1.2457 | 1.471 | 1.3769 | 1.0353 | 0.9127 | 0.81339 | 0.78027 | 0.73032
43602.4919 | 1.2442 | 1.468 | 1.3752 | 1.0332 | 0.91323 | 0.81374 | 0.7817 | 0.73104
43602.4919 | 1.2451 | 1.4671 | 1.3744 | 1.0336 | 0.91136 | 0.81225 | 0.78124 | 0.73027
43602.4919 | 1.2422 | 1.4671 | 1.3746 | 1.0333 | 0.91165 | 0.8125 | 0.77984 | 0.73049
43602.4919 | 1.2412 | 1.4664 | 1.3738 | 1.033 | 0.91128 | 0.81206 | 0.78091 | 0.73018
43602.4919 | 1.2431 | 1.4662 | 1.3733 | 1.0325 | 0.911 | 0.81208 | 0.78093 | 0.73042
43602.4918 | 1.2414 | 1.459 | 1.3678 | 1.0284 | 0.90573 | 0.8079 | 0.77609 | 0.72855
43602.492 | 1.2271 | 1.4566 | 1.3657 | 1.0253 | 0.90392 | 0.8065 | 0.77462 | 0.72755
43602.492 | 1.2293 | 1.4563 | 1.3654 | 1.0254 | 0.90447 | 0.80666 | 0.77393 | 0.72786
43602.4921 | 1.233 | 1.457 | 1.366 | 1.0256 | 0.9036 | 0.80617 | 0.77565 | 0.72693
43602.4921 | 1.2329 | 1.4566 | 1.3657 | 1.0255 | 0.90425 | 0.80652 | 0.77831 | 0.72772
43602.4921 | 1.2341 | 1.4565 | 1.3651 | 1.0251 | 0.90419 | 0.80639 | 0.77509 | 0.72711
43602.4921 | 1.235 | 1.4561 | 1.3657 | 1.0258 | 0.90436 | 0.80641 | 0.77471 | 0.72717
43602.492 | 1.2278 | 1.4573 | 1.3661 | 1.025 | 0.90416 | 0.80572 | 0.77359 | 0.72657
43602.4922 | 1.2343 | 1.4602 | 1.3688 | 1.0266 | 0.90545 | 0.80681 | 0.77575 | 0.72705
43602.4922 | 1.2337 | 1.4582 | 1.3684 | 1.0253 | 0.90513 | 0.80654 | 0.77462 | 0.72708
43602.4922 | 1.2341 | 1.4612 | 1.3697 | 1.0275 | 0.90462 | 0.80613 | 0.77322 | 0.72637
43602.4923 | 1.23 | 1.4594 | 1.369 | 1.0262 | 0.90507 | 0.80658 | 0.77423 | 0.72699
43602.4923 | 1.2345 | 1.4601 | 1.3687 | 1.0262 | 0.90433 | 0.80627 | 0.7743 | 0.72638
43602.4923 | 1.2283 | 1.4587 | 1.3684 | 1.0253 | 0.90407 | 0.80593 | 0.77578 | 0.72624
43602.4922 | 1.232 | 1.4565 | 1.3666 | 1.0235 | 0.90321 | 0.80522 | 0.77314 | 0.72625
43602.4924 | 1.2262 | 1.455 | 1.3654 | 1.023 | 0.90197 | 0.8038 | 0.77139 | 0.72538
43602.4924 | 1.2225 | 1.4543 | 1.3645 | 1.0223 | 0.90124 | 0.80372 | 0.77363 | 0.72558
43602.4924 | 1.2282 | 1.4547 | 1.3649 | 1.0227 | 0.90133 | 0.80348 | 0.77464 | 0.72547
43602.4924 | 1.2252 | 1.4544 | 1.3649 | 1.022 | 0.90006 | 0.8028 | 0.77138 | 0.72471
43602.4925 | 1.2274 | 1.453 | 1.3637 | 1.022 | 0.89999 | 0.80243 | 0.77085 | 0.72468
43602.4925 | 1.2196 | 1.4519 | 1.363 | 1.0197 | 0.90001 | 0.80265 | 0.77109 | 0.72505
43602.4924 | 1.2255 | 1.4524 | 1.3637 | 1.0207 | 0.90017 | 0.80222 | 0.77064 | 0.72469
43602.4926 | 1.2285 | 1.4552 | 1.3658 | 1.0227 | 0.90099 | 0.80307 | 0.77244 | 0.72528
43602.4926 | 1.2244 | 1.4554 | 1.3661 | 1.0224 | 0.90099 | 0.80278 | 0.77096 | 0.72471
43602.4926 | 1.2275 | 1.456 | 1.3666 | 1.0224 | 0.9017 | 0.80331 | 0.77156 | 0.72489
43602.4926 | 1.2273 | 1.4533 | 1.3651 | 1.0205 | 0.90028 | 0.80235 | 0.77092 | 0.72411
43602.4926 | 1.2236 | 1.4542 | 1.3649 | 1.0209 | 0.90022 | 0.80208 | 0.77129 | 0.72452
43602.4927 | 1.2267 | 1.4548 | 1.3659 | 1.0227 | 0.90099 | 0.80256 | 0.77133 | 0.72458
43602.4926 | 1.22 | 1.4474 | 1.3594 | 1.0166 | 0.89727 | 0.79984 | 0.76953 | 0.72353
43602.4928 | 1.2134 | 1.4414 | 1.3542 | 1.0128 | 0.89268 | 0.79686 | 0.76641 | 0.72267
43602.4928 | 1.2119 | 1.4386 | 1.3525 | 1.011 | 0.89237 | 0.79627 | 0.76508 | 0.72248
43602.4928 | 1.2112 | 1.4395 | 1.3524 | 1.0114 | 0.89135 | 0.79532 | 0.76508 | 0.72199
43602.4928 | 1.2152 | 1.44 | 1.3525 | 1.0113 | 0.89194 | 0.7956 | 0.76456 | 0.72189
43602.4928 | 1.2094 | 1.4382 | 1.3511 | 1.0106 | 0.89188 | 0.79599 | 0.76631 | 0.72248
43602.4928 | 1.2129 | 1.4399 | 1.3523 | 1.012 | 0.89134 | 0.79545 | 0.76804 | 0.72196
43602.4928 | 1.2204 | 1.4401 | 1.3524 | 1.0122 | 0.89178 | 0.79575 | 0.7649 | 0.72156
43602.493 | 1.2106 | 1.438 | 1.3514 | 1.0122 | 0.89243 | 0.79621 | 0.76538 | 0.72232
43602.493 | 1.2163 | 1.4397 | 1.3515 | 1.0124 | 0.89221 | 0.79599 | 0.76555 | 0.72215
43602.493 | 1.2162 | 1.4386 | 1.3512 | 1.012 | 0.89221 | 0.79602 | 0.76744 | 0.72209
43602.493 | 1.215 | 1.4391 | 1.3513 | 1.0122 | 0.89248 | 0.79595 | 0.76582 | 0.72228
43602.493 | 1.2135 | 1.4401 | 1.3527 | 1.0134 | 0.8922 | 0.79545 | 0.76492 | 0.72125
43602.493 | 1.2208 | 1.4413 | 1.3531 | 1.0148 | 0.89341 | 0.79647 | 0.76552 | 0.72224
43602.493 | 1.2191 | 1.4441 | 1.355 | 1.0155 | 0.89497 | 0.7975 | 0.76781 | 0.72217
43602.4932 | 1.2234 | 1.4477 | 1.3586 | 1.019 | 0.8984 | 0.80028 | 0.76925 | 0.72341
43602.4932 | 1.228 | 1.4486 | 1.3592 | 1.019 | 0.89798 | 0.80015 | 0.76862 | 0.72307
43602.4932 | 1.2251 | 1.4494 | 1.3602 | 1.0204 | 0.89903 | 0.80103 | 0.76877 | 0.72337
43602.4932 | 1.2222 | 1.4486 | 1.3602 | 1.02 | 0.89886 | 0.80107 | 0.76936 | 0.72384
43602.4932 | 1.234 | 1.4528 | 1.3624 | 1.0229 | 0.89983 | 0.80144 | 0.77021 | 0.72381
43602.4932 | 1.2342 | 1.4545 | 1.3639 | 1.0241 | 0.90128 | 0.8024 | 0.77294 | 0.7242
43602.4932 | 1.2353 | 1.4589 | 1.3684 | 1.0262 | 0.90451 | 0.80551 | 0.77295 | 0.7255
43602.4934 | 1.2382 | 1.4665 | 1.3747 | 1.0312 | 0.90704 | 0.80764 | 0.77499 | 0.72668
43602.4934 | 1.2367 | 1.4658 | 1.3757 | 1.0304 | 0.90828 | 0.80825 | 0.77724 | 0.72637
43602.4934 | 1.2345 | 1.4655 | 1.3754 | 1.0305 | 0.90866 | 0.80887 | 0.7774 | 0.72647
43602.4934 | 1.2419 | 1.4653 | 1.3759 | 1.0303 | 0.90777 | 0.80817 | 0.77597 | 0.72639
43602.4934 | 1.2373 | 1.4675 | 1.3763 | 1.0306 | 0.90848 | 0.80879 | 0.77718 | 0.72669
43602.4934 | 1.2401 | 1.4694 | 1.3783 | 1.0327 | 0.90888 | 0.80896 | 0.77752 | 0.7263
43602.4933 | 1.2326 | 1.4692 | 1.3794 | 1.0316 | 0.90948 | 0.80956 | 0.77661 | 0.72655
43602.4935 | 1.2371 | 1.4696 | 1.3803 | 1.0318 | 0.90942 | 0.80955 | 0.7764 | 0.72681
43602.4936 | 1.2374 | 1.4709 | 1.3801 | 1.031 | 0.9102 | 0.81039 | 0.77706 | 0.72751
43602.4936 | 1.2324 | 1.4694 | 1.3797 | 1.0307 | 0.91039 | 0.81015 | 0.77969 | 0.72747
43602.4936 | 1.2387 | 1.471 | 1.3799 | 1.0315 | 0.90931 | 0.80935 | 0.77843 | 0.72664
43602.4936 | 1.2341 | 1.4701 | 1.3805 | 1.031 | 0.90961 | 0.80952 | 0.77714 | 0.72659
43602.4936 | 1.2414 | 1.4722 | 1.3818 | 1.0319 | 0.90989 | 0.81011 | 0.77725 | 0.72716
43602.4935 | 1.2379 | 1.4727 | 1.3839 | 1.0322 | 0.91065 | 0.81083 | 0.77788 | 0.72712
43602.4937 | 1.2369 | 1.475 | 1.3862 | 1.0337 | 0.91112 | 0.81128 | 0.77998 | 0.72717
43602.4937 | 1.2424 | 1.4745 | 1.3868 | 1.034 | 0.91262 | 0.81168 | 0.77977 | 0.72741
43602.4938 | 1.2346 | 1.4732 | 1.3857 | 1.0329 | 0.91138 | 0.81126 | 0.77841 | 0.72721
43602.4938 | 1.241 | 1.4753 | 1.3872 | 1.0333 | 0.91181 | 0.81177 | 0.7784 | 0.72784
43602.4938 | 1.2353 | 1.4738 | 1.3863 | 1.0331 | 0.91213 | 0.81161 | 0.77997 | 0.72741
43602.4938 | 1.2337 | 1.4726 | 1.3852 | 1.0316 | 0.91102 | 0.81075 | 0.7797 | 0.72739
43602.4937 | 1.2369 | 1.4766 | 1.3887 | 1.0333 | 0.91245 | 0.81225 | 0.77965 | 0.72768
43602.4939 | 1.2355 | 1.4761 | 1.3899 | 1.0332 | 0.91215 | 0.81197 | 0.77929 | 0.72762
43602.4939 | 1.2336 | 1.4764 | 1.3898 | 1.0338 | 0.9117 | 0.8121 | 0.77887 | 0.72739
43602.4939 | 1.2313 | 1.4765 | 1.3898 | 1.0336 | 0.91287 | 0.81355 | 0.78015 | 0.72841
43602.494 | 1.2392 | 1.4782 | 1.3906 | 1.0348 | 0.91236 | 0.81225 | 0.77963 | 0.7276
43602.494 | 1.2286 | 1.477 | 1.3908 | 1.0341 | 0.91182 | 0.81218 | 0.78094 | 0.72746
43602.494 | 1.2354 | 1.478 | 1.3911 | 1.0345 | 0.9129 | 0.81316 | 0.7806 | 0.72821
43602.4939 | 1.2377 | 1.4782 | 1.3911 | 1.0332 | 0.91217 | 0.813 | 0.77931 | 0.72778
43602.4941 | 1.2325 | 1.4778 | 1.3916 | 1.0333 | 0.91165 | 0.81218 | 0.77892 | 0.72735
43602.4941 | 1.2304 | 1.4762 | 1.3902 | 1.0312 | 0.91129 | 0.81201 | 0.77808 | 0.72722
43602.4941 | 1.2322 | 1.4773 | 1.3914 | 1.0325 | 0.91128 | 0.81242 | 0.77881 | 0.72753
43602.4941 | 1.2325 | 1.4775 | 1.3913 | 1.0325 | 0.91185 | 0.81244 | 0.78092 | 0.72784
43602.4942 | 1.23 | 1.476 | 1.3905 | 1.0313 | 0.91084 | 0.8116 | 0.78124 | 0.72707
43602.4942 | 1.2323 | 1.4778 | 1.3905 | 1.0311 | 0.91083 | 0.81185 | 0.77914 | 0.72765
43602.4941 | 1.2202 | 1.475 | 1.3884 | 1.0287 | 0.91002 | 0.81092 | 0.77836 | 0.72663
43602.4943 | 1.2235 | 1.4727 | 1.3864 | 1.0273 | 0.90744 | 0.80907 | 0.77645 | 0.72593
43602.4943 | 1.217 | 1.473 | 1.3868 | 1.0264 | 0.90728 | 0.80905 | 0.77624 | 0.726
43602.4943 | 1.2254 | 1.473 | 1.3855 | 1.0263 | 0.90654 | 0.80784 | 0.77442 | 0.72452
43602.4943 | 1.2216 | 1.4722 | 1.3854 | 1.026 | 0.90639 | 0.80756 | 0.77414 | 0.72477
43602.4943 | 1.2239 | 1.4725 | 1.3856 | 1.026 | 0.90743 | 0.8092 | 0.77852 | 0.72563
43602.4944 | 1.2221 | 1.471 | 1.3841 | 1.0257 | 0.90631 | 0.80796 | 0.77686 | 0.72493
43602.4943 | 1.2157 | 1.4673 | 1.3826 | 1.0235 | 0.90589 | 0.80761 | 0.77506 | 0.72539
43602.4945 | 1.2205 | 1.4677 | 1.3816 | 1.0234 | 0.90556 | 0.80693 | 0.77386 | 0.72416
43602.4945 | 1.2197 | 1.4659 | 1.3811 | 1.0224 | 0.9042 | 0.80579 | 0.77355 | 0.72395
43602.4945 | 1.2149 | 1.4675 | 1.382 | 1.0239 | 0.90464 | 0.80605 | 0.77556 | 0.72393
43602.4945 | 1.2219 | 1.4676 | 1.3814 | 1.0228 | 0.9049 | 0.80646 | 0.7742 | 0.72437
43602.4945 | 1.2215 | 1.4669 | 1.381 | 1.0228 | 0.90423 | 0.80566 | 0.77267 | 0.72364
43602.4945 | 1.2168 | 1.4644 | 1.3791 | 1.0217 | 0.90329 | 0.80509 | 0.77165 | 0.72339
43602.4945 | 1.22 | 1.4621 | 1.3771 | 1.0199 | 0.90168 | 0.80435 | 0.7712 | 0.72311
43602.4947 | 1.219 | 1.4591 | 1.3739 | 1.0184 | 0.90122 | 0.8033 | 0.7697 | 0.72296
43602.4947 | 1.2153 | 1.4593 | 1.3746 | 1.0183 | 0.90036 | 0.8028 | 0.77153 | 0.72251
43602.4947 | 1.2148 | 1.4586 | 1.3734 | 1.0183 | 0.9007 | 0.80341 | 0.77099 | 0.72328
43602.4947 | 1.2139 | 1.4595 | 1.3732 | 1.0181 | 0.89981 | 0.80211 | 0.76976 | 0.72177
43602.4947 | 1.2182 | 1.46 | 1.3745 | 1.0186 | 0.90019 | 0.80204 | 0.76961 | 0.72187
43602.4947 | 1.2208 | 1.4619 | 1.375 | 1.0196 | 0.90096 | 0.80281 | 0.77084 | 0.72234
43602.4947 | 1.2167 | 1.4651 | 1.3795 | 1.0231 | 0.90344 | 0.80455 | 0.77191 | 0.72217
43602.4949 | 1.2326 | 1.475 | 1.3863 | 1.0296 | 0.90749 | 0.80664 | 0.77575 | 0.72255
43602.4949 | 1.2342 | 1.4756 | 1.388 | 1.0301 | 0.9093 | 0.80751 | 0.77496 | 0.72263
43602.4949 | 1.2349 | 1.4776 | 1.3891 | 1.0311 | 0.90967 | 0.80791 | 0.77468 | 0.72284
43602.4949 | 1.2428 | 1.4805 | 1.3912 | 1.0335 | 0.91141 | 0.80964 | 0.77606 | 0.72386
43602.4949 | 1.2415 | 1.4806 | 1.3915 | 1.0339 | 0.91234 | 0.8108 | 0.77725 | 0.72468
43602.4949 | 1.241 | 1.4801 | 1.3912 | 1.0336 | 0.91197 | 0.81042 | 0.77947 | 0.72438
43602.4949 | 1.245 | 1.4803 | 1.3915 | 1.0349 | 0.91338 | 0.81176 | 0.77879 | 0.72524
43602.4951 | 1.2466 | 1.4813 | 1.3921 | 1.0359 | 0.9135 | 0.81213 | 0.78088 | 0.72512
43602.4951 | 1.2473 | 1.483 | 1.3936 | 1.0371 | 0.91403 | 0.8129 | 0.78002 | 0.72548
43602.4951 | 1.2429 | 1.4817 | 1.3936 | 1.0366 | 0.91538 | 0.81393 | 0.78014 | 0.72613
43602.4951 | 1.2469 | 1.4832 | 1.3942 | 1.0374 | 0.91448 | 0.81337 | 0.77953 | 0.72595
43602.4951 | 1.2452 | 1.4846 | 1.3953 | 1.0389 | 0.91559 | 0.81415 | 0.77999 | 0.72615
43602.4951 | 1.2464 | 1.4859 | 1.3964 | 1.0391 | 0.91608 | 0.81457 | 0.78025 | 0.72603
43602.4951 | 1.2433 | 1.4867 | 1.3978 | 1.0408 | 0.91912 | 0.81686 | 0.78332 | 0.72735
43602.4953 | 1.2489 | 1.4859 | 1.3971 | 1.0399 | 0.91835 | 0.81633 | 0.78198 | 0.72696
43602.4953 | 1.2491 | 1.4861 | 1.3973 | 1.0407 | 0.91786 | 0.81603 | 0.7816 | 0.72714
43602.4953 | 1.2481 | 1.4861 | 1.3971 | 1.0402 | 0.91868 | 0.81674 | 0.78311 | 0.72804
43602.4953 | 1.2445 | 1.4864 | 1.3975 | 1.0411 | 0.91729 | 0.81574 | 0.78273 | 0.72701
43602.4953 | 1.251 | 1.4879 | 1.3981 | 1.041 | 0.91882 | 0.81708 | 0.78602 | 0.72805
43602.4953 | 1.2452 | 1.4853 | 1.3966 | 1.0397 | 0.91781 | 0.8161 | 0.78292 | 0.72742
43602.4952 | 1.2493 | 1.4892 | 1.4004 | 1.041 | 0.91853 | 0.81668 | 0.78369 | 0.72765
43602.4954 | 1.2456 | 1.4911 | 1.4026 | 1.0424 | 0.91925 | 0.81801 | 0.7859 | 0.72783
43602.4955 | 1.2485 | 1.4908 | 1.4028 | 1.0424 | 0.91992 | 0.81841 | 0.78483 | 0.72792
43602.4955 | 1.2432 | 1.4897 | 1.4018 | 1.0408 | 0.91877 | 0.81764 | 0.78322 | 0.72757
43602.4955 | 1.2442 | 1.4899 | 1.4019 | 1.0408 | 0.91776 | 0.81672 | 0.78244 | 0.72691
43602.4955 | 1.2397 | 1.4897 | 1.4013 | 1.0398 | 0.91757 | 0.81657 | 0.78204 | 0.72691
43602.4955 | 1.2449 | 1.4906 | 1.4016 | 1.0406 | 0.91827 | 0.81724 | 0.78371 | 0.72722
43602.4954 | 1.2311 | 1.479 | 1.3932 | 1.0329 | 0.91263 | 0.81252 | 0.77909 | 0.72541
43602.4956 | 1.2278 | 1.4742 | 1.3879 | 1.0287 | 0.90941 | 0.81006 | 0.77875 | 0.72469
43602.4956 | 1.2277 | 1.4739 | 1.3882 | 1.0286 | 0.90936 | 0.80993 | 0.77893 | 0.72483
43602.4957 | 1.2256 | 1.4729 | 1.3875 | 1.0277 | 0.90789 | 0.80827 | 0.77615 | 0.72321
43602.4957 | 1.2294 | 1.4723 | 1.3867 | 1.0279 | 0.90719 | 0.80759 | 0.7749 | 0.72294
43602.4956 | 1.2239 | 1.4703 | 1.3856 | 1.0267 | 0.9065 | 0.80768 | 0.77436 | 0.72323
43602.4958 | 1.2373 | 1.4805 | 1.3938 | 1.0329 | 0.90997 | 0.80949 | 0.77556 | 0.7224
43602.4958 | 1.2621 | 1.5016 | 1.4106 | 1.0497 | 0.92327 | 0.81976 | 0.78568 | 0.72652
43602.496 | 1.2643 | 1.5042 | 1.4128 | 1.052 | 0.92631 | 0.82281 | 0.78797 | 0.72886
43602.4961 | 1.2636 | 1.5037 | 1.4117 | 1.0516 | 0.92718 | 0.82365 | 0.78861 | 0.72871
43602.4961 | 1.2729 | 1.5068 | 1.4145 | 1.0542 | 0.9273 | 0.82342 | 0.78974 | 0.72863
43602.4961 | 1.2616 | 1.5052 | 1.4134 | 1.0526 | 0.92846 | 0.8245 | 0.79122 | 0.72927
43602.4961 | 1.2662 | 1.5059 | 1.4138 | 1.0537 | 0.92821 | 0.82436 | 0.78991 | 0.72948
43602.4961 | 1.2633 | 1.507 | 1.4145 | 1.0543 | 0.92809 | 0.82378 | 0.78901 | 0.72895
43602.496 | 1.2643 | 1.5038 | 1.4116 | 1.0522 | 0.92934 | 0.82531 | 0.79022 | 0.73033
43602.4962 | 1.2601 | 1.4993 | 1.4083 | 1.0498 | 0.92648 | 0.82309 | 0.78876 | 0.72965
43602.4962 | 1.2562 | 1.4992 | 1.4082 | 1.0503 | 0.9258 | 0.82277 | 0.78798 | 0.72974
43602.4963 | 1.2574 | 1.4978 | 1.4067 | 1.0486 | 0.92588 | 0.82327 | 0.7877 | 0.72976
43602.4963 | 1.2599 | 1.4975 | 1.4067 | 1.0486 | 0.925 | 0.82126 | 0.78658 | 0.7288
43602.4963 | 1.2641 | 1.4987 | 1.4064 | 1.0493 | 0.92479 | 0.82173 | 0.78719 | 0.72931
43602.4963 | 1.2549 | 1.4962 | 1.4055 | 1.048 | 0.92524 | 0.82204 | 0.78722 | 0.7298
43602.4962 | 1.2555 | 1.4943 | 1.4037 | 1.047 | 0.92423 | 0.82106 | 0.78846 | 0.72971
43602.4964 | 1.2505 | 1.4905 | 1.402 | 1.0453 | 0.92257 | 0.82012 | 0.78883 | 0.72939
43602.4964 | 1.2562 | 1.4935 | 1.4032 | 1.0452 | 0.92165 | 0.8187 | 0.78536 | 0.7282
43602.4964 | 1.2496 | 1.4913 | 1.402 | 1.0445 | 0.92246 | 0.81992 | 0.78563 | 0.72876
43602.4965 | 1.2461 | 1.4921 | 1.4021 | 1.0453 | 0.92156 | 0.81957 | 0.78542 | 0.72878
43602.4965 | 1.2556 | 1.4926 | 1.4027 | 1.0457 | 0.9224 | 0.81967 | 0.78535 | 0.72855
43602.4965 | 1.2482 | 1.4913 | 1.402 | 1.0451 | 0.92226 | 0.81915 | 0.78721 | 0.72841
43602.4964 | 1.2511 | 1.4929 | 1.4039 | 1.0449 | 0.92247 | 0.81958 | 0.78663 | 0.72864
43602.4966 | 1.2548 | 1.4981 | 1.4076 | 1.0481 | 0.92572 | 0.82258 | 0.78839 | 0.72935
43602.4966 | 1.2585 | 1.4967 | 1.4073 | 1.0478 | 0.92329 | 0.82075 | 0.78927 | 0.72837
43602.4966 | 1.2569 | 1.4982 | 1.4084 | 1.0475 | 0.92514 | 0.8221 | 0.78839 | 0.72964
43602.4966 | 1.2573 | 1.498 | 1.4085 | 1.0478 | 0.92502 | 0.82181 | 0.78719 | 0.72917
43602.4967 | 1.2588 | 1.4993 | 1.4091 | 1.0493 | 0.92517 | 0.82177 | 0.78695 | 0.72889
43602.4967 | 1.2582 | 1.5006 | 1.4098 | 1.0492 | 0.92578 | 0.82216 | 0.78694 | 0.72929
43602.4966 | 1.2639 | 1.5049 | 1.4136 | 1.052 | 0.92827 | 0.82437 | 0.7916 | 0.72975
43602.4968 | 1.2632 | 1.5068 | 1.4162 | 1.0542 | 0.93015 | 0.82622 | 0.79068 | 0.73061
43602.4968 | 1.269 | 1.507 | 1.416 | 1.0539 | 0.92912 | 0.82496 | 0.7913 | 0.72986
43602.4968 | 1.2651 | 1.5088 | 1.4173 | 1.054 | 0.93039 | 0.82581 | 0.79513 | 0.73022
43602.4968 | 1.2631 | 1.5084 | 1.417 | 1.0542 | 0.93083 | 0.82624 | 0.79197 | 0.73073
43602.4969 | 1.2643 | 1.5076 | 1.4166 | 1.0539 | 0.92921 | 0.82498 | 0.78984 | 0.72947
43602.4969 | 1.2628 | 1.5083 | 1.4173 | 1.054 | 0.92974 | 0.82605 | 0.79054 | 0.73048
43602.4968 | 1.2658 | 1.5096 | 1.4182 | 1.0542 | 0.93198 | 0.82722 | 0.79162 | 0.73111
43602.497 | 1.2643 | 1.5098 | 1.4193 | 1.0547 | 0.9305 | 0.826 | 0.79349 | 0.73043
43602.497 | 1.2609 | 1.5101 | 1.4195 | 1.0547 | 0.93102 | 0.82667 | 0.79134 | 0.73047
43602.497 | 1.2664 | 1.51 | 1.4197 | 1.0541 | 0.93018 | 0.82561 | 0.79024 | 0.72987
43602.497 | 1.2651 | 1.5113 | 1.4207 | 1.0562 | 0.93097 | 0.82662 | 0.79108 | 0.73052
43602.497 | 1.2631 | 1.5114 | 1.421 | 1.0542 | 0.93132 | 0.82638 | 0.79194 | 0.73032
43602.4971 | 1.2635 | 1.5114 | 1.4214 | 1.0558 | 0.93122 | 0.82697 | 0.7946 | 0.73099
43602.497 | 1.2596 | 1.5093 | 1.4198 | 1.0536 | 0.92971 | 0.82594 | 0.79068 | 0.72996
43602.4972 | 1.2653 | 1.5104 | 1.4205 | 1.0533 | 0.93046 | 0.82607 | 0.79121 | 0.72953
43602.4972 | 1.2616 | 1.511 | 1.4208 | 1.0533 | 0.92975 | 0.82543 | 0.79099 | 0.72947
43602.4972 | 1.2577 | 1.5097 | 1.4198 | 1.053 | 0.92991 | 0.82608 | 0.79073 | 0.72979
43602.4972 | 1.2629 | 1.5115 | 1.4223 | 1.0553 | 0.93042 | 0.82619 | 0.79097 | 0.73003
43602.4972 | 1.2647 | 1.5124 | 1.422 | 1.0552 | 0.93042 | 0.82618 | 0.79367 | 0.72991
43602.4972 | 1.2639 | 1.5113 | 1.4221 | 1.0546 | 0.93071 | 0.82679 | 0.79226 | 0.7301
43602.4972 | 1.2594 | 1.5127 | 1.423 | 1.0547 | 0.93061 | 0.82642 | 0.79318 | 0.72946
43602.4974 | 1.2607 | 1.5128 | 1.4231 | 1.0546 | 0.92948 | 0.82533 | 0.79145 | 0.72844
43602.4974 | 1.2622 | 1.511 | 1.4222 | 1.054 | 0.93124 | 0.82692 | 0.79365 | 0.72993
43602.4974 | 1.2568 | 1.5098 | 1.4213 | 1.0526 | 0.92862 | 0.82499 | 0.78992 | 0.72821
43602.4974 | 1.2519 | 1.5109 | 1.4226 | 1.0535 | 0.92927 | 0.82541 | 0.78989 | 0.72873
43602.4974 | 1.2581 | 1.509 | 1.4206 | 1.0522 | 0.92908 | 0.82521 | 0.78917 | 0.72879
43602.4974 | 1.2575 | 1.5089 | 1.4199 | 1.052 | 0.9287 | 0.82448 | 0.78914 | 0.72842
43602.4974 | 1.2477 | 1.4984 | 1.4112 | 1.0459 | 0.92286 | 0.82032 | 0.7869 | 0.72754
43602.4976 | 1.2406 | 1.4894 | 1.4032 | 1.0404 | 0.91888 | 0.81755 | 0.78608 | 0.72705
43602.4976 | 1.2405 | 1.4878 | 1.4016 | 1.0386 | 0.91701 | 0.81594 | 0.78263 | 0.72553
43602.4976 | 1.2359 | 1.4874 | 1.4012 | 1.0377 | 0.91632 | 0.81528 | 0.78154 | 0.72518
43602.4976 | 1.2429 | 1.4883 | 1.401 | 1.0373 | 0.91665 | 0.81556 | 0.78124 | 0.72556
43602.4976 | 1.2407 | 1.4866 | 1.3996 | 1.0371 | 0.91548 | 0.81465 | 0.78008 | 0.72507
43602.4976 | 1.237 | 1.4866 | 1.399 | 1.038 | 0.916 | 0.81474 | 0.78216 | 0.72541
43602.4978 | 1.2395 | 1.4903 | 1.4012 | 1.0398 | 0.91711 | 0.81557 | 0.78267 | 0.72552
43602.4978 | 1.2432 | 1.4916 | 1.4023 | 1.041 | 0.91758 | 0.81561 | 0.78136 | 0.72519
43602.4978 | 1.245 | 1.4915 | 1.4024 | 1.041 | 0.91799 | 0.81598 | 0.78165 | 0.72528
43602.4978 | 1.2464 | 1.4922 | 1.4035 | 1.0412 | 0.91839 | 0.81609 | 0.7836 | 0.72523
43602.4978 | 1.248 | 1.4946 | 1.4055 | 1.0441 | 0.91952 | 0.81701 | 0.78352 | 0.7258
43602.4978 | 1.2569 | 1.4969 | 1.4063 | 1.045 | 0.92126 | 0.818 | 0.78407 | 0.7262
43602.4977 | 1.2629 | 1.5068 | 1.4156 | 1.0514 | 0.92553 | 0.82259 | 0.787 | 0.72781
43602.498 | 1.2628 | 1.5111 | 1.42 | 1.0556 | 0.92923 | 0.82498 | 0.79263 | 0.72864
43602.498 | 1.2669 | 1.511 | 1.4185 | 1.0524 | 0.92936 | 0.82548 | 0.79164 | 0.72942
43602.498 | 1.2645 | 1.5119 | 1.4193 | 1.0542 | 0.92913 | 0.82504 | 0.79034 | 0.72854
43602.498 | 1.2594 | 1.5116 | 1.4199 | 1.0552 | 0.92961 | 0.82532 | 0.79029 | 0.72896
43602.498 | 1.2635 | 1.5134 | 1.421 | 1.0571 | 0.93046 | 0.82604 | 0.79048 | 0.72947
43602.4979 | 1.2688 | 1.5135 | 1.4208 | 1.0569 | 0.93115 | 0.82664 | 0.79341 | 0.72968
43602.4981 | 1.2641 | 1.5131 | 1.4209 | 1.0565 | 0.93063 | 0.8262 | 0.79095 | 0.72964
43602.4981 | 1.2644 | 1.5121 | 1.4212 | 1.0561 | 0.93133 | 0.82656 | 0.79069 | 0.72951
43602.4981 | 1.2686 | 1.5119 | 1.4205 | 1.0556 | 0.93045 | 0.82587 | 0.79181 | 0.72939
43602.4982 | 1.2678 | 1.5134 | 1.4215 | 1.0567 | 0.93136 | 0.82681 | 0.79268 | 0.72994
43602.4982 | 1.2628 | 1.5113 | 1.4205 | 1.0547 | 0.93055 | 0.8265 | 0.79078 | 0.72944
43602.4982 | 1.262 | 1.5112 | 1.421 | 1.0559 | 0.9299 | 0.82637 | 0.791 | 0.72975
43602.4981 | 1.2594 | 1.505 | 1.4157 | 1.0522 | 0.92742 | 0.82387 | 0.79014 | 0.72916
43602.4983 | 1.2472 | 1.4964 | 1.4093 | 1.0469 | 0.92451 | 0.82174 | 0.78685 | 0.72863
43602.4983 | 1.2512 | 1.4977 | 1.4096 | 1.0478 | 0.92398 | 0.82154 | 0.78782 | 0.72872
43602.4983 | 1.2453 | 1.4948 | 1.4083 | 1.0463 | 0.92438 | 0.82184 | 0.78763 | 0.72938
43602.4984 | 1.2542 | 1.4945 | 1.4068 | 1.0449 | 0.92255 | 0.8205 | 0.7851 | 0.72799
43602.4984 | 1.2473 | 1.4944 | 1.4073 | 1.0459 | 0.92324 | 0.82062 | 0.78623 | 0.72855
43602.4984 | 1.2508 | 1.4938 | 1.4066 | 1.0457 | 0.92305 | 0.82038 | 0.7899 | 0.72801
43602.4983 | 1.2522 | 1.4938 | 1.407 | 1.0464 | 0.92326 | 0.82059 | 0.78619 | 0.72888
43602.4985 | 1.2526 | 1.4916 | 1.4056 | 1.0465 | 0.92313 | 0.8206 | 0.78632 | 0.72828
43602.4985 | 1.2537 | 1.4946 | 1.4071 | 1.0465 | 0.92262 | 0.82021 | 0.78588 | 0.72794
43602.4985 | 1.2587 | 1.4949 | 1.4073 | 1.0475 | 0.9237 | 0.82058 | 0.78671 | 0.72803
43602.4985 | 1.258 | 1.4946 | 1.407 | 1.0469 | 0.9234 | 0.82095 | 0.78684 | 0.72823
43602.4986 | 1.2547 | 1.4963 | 1.4082 | 1.0481 | 0.92428 | 0.8216 | 0.79012 | 0.72888
43602.4986 | 1.2554 | 1.4959 | 1.4087 | 1.048 | 0.92503 | 0.82204 | 0.78826 | 0.72892
43602.4985 | 1.2626 | 1.5 | 1.4115 | 1.0515 | 0.92675 | 0.82371 | 0.7892 | 0.72947
43602.4987 | 1.2659 | 1.5017 | 1.4129 | 1.0537 | 0.92846 | 0.82496 | 0.79062 | 0.7308
43602.4987 | 1.2646 | 1.5011 | 1.4124 | 1.053 | 0.92832 | 0.82472 | 0.78987 | 0.73027
43602.4987 | 1.2568 | 1.5003 | 1.4128 | 1.0531 | 0.92712 | 0.82379 | 0.79268 | 0.72963
43602.4987 | 1.2622 | 1.5015 | 1.4126 | 1.0537 | 0.92785 | 0.82448 | 0.79192 | 0.73036
43602.4988 | 1.2635 | 1.5011 | 1.4131 | 1.0536 | 0.92778 | 0.82444 | 0.79107 | 0.73027
43602.4988 | 1.2574 | 1.5025 | 1.4138 | 1.054 | 0.92864 | 0.82518 | 0.79107 | 0.73043
43602.4987 | 1.269 | 1.5089 | 1.4199 | 1.0582 | 0.93185 | 0.82783 | 0.79324 | 0.7313
43602.4989 | 1.2712 | 1.5157 | 1.4255 | 1.0622 | 0.93551 | 0.831 | 0.79823 | 0.73272
43602.4989 | 1.2723 | 1.5159 | 1.4259 | 1.0628 | 0.93594 | 0.83109 | 0.79581 | 0.73238
43602.4989 | 1.2775 | 1.5177 | 1.4264 | 1.063 | 0.93715 | 0.83281 | 0.79707 | 0.73384
43602.4989 | 1.2741 | 1.5171 | 1.4276 | 1.0633 | 0.93672 | 0.83188 | 0.79599 | 0.73318
43602.499 | 1.267 | 1.5175 | 1.4279 | 1.0636 | 0.93779 | 0.83303 | 0.79678 | 0.73382
43602.499 | 1.2763 | 1.5181 | 1.429 | 1.0642 | 0.93729 | 0.83219 | 0.79621 | 0.73314
43602.4989 | 1.2767 | 1.5232 | 1.433 | 1.0668 | 0.941 | 0.83507 | 0.79979 | 0.73466
43602.4991 | 1.2723 | 1.5221 | 1.4328 | 1.0659 | 0.94015 | 0.8344 | 0.79892 | 0.73436
43602.4991 | 1.2762 | 1.5246 | 1.4342 | 1.0674 | 0.94136 | 0.83515 | 0.79974 | 0.73472
43602.4991 | 1.2775 | 1.524 | 1.4339 | 1.0669 | 0.94208 | 0.83629 | 0.8003 | 0.73557
43602.4991 | 1.2711 | 1.5213 | 1.4319 | 1.0643 | 0.93952 | 0.83456 | 0.7989 | 0.73427
43602.4991 | 1.2747 | 1.5223 | 1.4318 | 1.0656 | 0.93923 | 0.83407 | 0.79894 | 0.73434
43602.4991 | 1.275 | 1.5192 | 1.4302 | 1.0636 | 0.93811 | 0.83279 | 0.79721 | 0.73358
43602.4993 | 1.2642 | 1.5164 | 1.429 | 1.0609 | 0.93678 | 0.83226 | 0.79675 | 0.73321
43602.4993 | 1.2691 | 1.517 | 1.4287 | 1.061 | 0.93609 | 0.83108 | 0.796 | 0.73287
43602.4993 | 1.2645 | 1.5162 | 1.4288 | 1.0612 | 0.93717 | 0.83232 | 0.79721 | 0.73378
43602.4993 | 1.2671 | 1.5176 | 1.4286 | 1.0616 | 0.93749 | 0.83271 | 0.79827 | 0.73451
43602.4993 | 1.2699 | 1.5175 | 1.4294 | 1.0616 | 0.93728 | 0.83188 | 0.79941 | 0.73372
43602.4993 | 1.2697 | 1.5181 | 1.4292 | 1.0618 | 0.93696 | 0.83159 | 0.7968 | 0.73331
43602.4993 | 1.2708 | 1.5213 | 1.4335 | 1.0651 | 0.93947 | 0.83357 | 0.79835 | 0.73403
43602.4995 | 1.267 | 1.5196 | 1.432 | 1.0628 | 0.93926 | 0.83322 | 0.79741 | 0.73409
43602.4995 | 1.2676 | 1.5192 | 1.4313 | 1.0628 | 0.9393 | 0.83378 | 0.79882 | 0.73442
43602.4995 | 1.2725 | 1.5197 | 1.4314 | 1.0631 | 0.9391 | 0.83323 | 0.80213 | 0.73417
43602.4995 | 1.2623 | 1.5198 | 1.4322 | 1.063 | 0.93873 | 0.83354 | 0.79921 | 0.73425
43602.4995 | 1.2674 | 1.5208 | 1.433 | 1.0644 | 0.9402 | 0.83401 | 0.79853 | 0.73486
43602.4995 | 1.2708 | 1.5212 | 1.4325 | 1.0642 | 0.9399 | 0.83357 | 0.79825 | 0.73435
43602.4995 | 1.2636 | 1.5174 | 1.4305 | 1.0621 | 0.93804 | 0.83243 | 0.80044 | 0.73415
43602.4997 | 1.2637 | 1.5116 | 1.4248 | 1.0576 | 0.9347 | 0.83012 | 0.79549 | 0.7334
43602.4997 | 1.263 | 1.5106 | 1.4232 | 1.0566 | 0.93545 | 0.83034 | 0.79569 | 0.73382
43602.4997 | 1.2577 | 1.5086 | 1.4228 | 1.0557 | 0.9338 | 0.82938 | 0.79619 | 0.73311
43602.4997 | 1.2544 | 1.5088 | 1.4228 | 1.0562 | 0.93346 | 0.82891 | 0.7949 | 0.73284
43602.4997 | 1.265 | 1.508 | 1.4219 | 1.056 | 0.93409 | 0.82968 | 0.79461 | 0.73334
43602.4997 | 1.2553 | 1.5045 | 1.4199 | 1.0537 | 0.93307 | 0.8288 | 0.79537 | 0.73312
43602.4997 | 1.2549 | 1.5026 | 1.4153 | 1.0516 | 0.93184 | 0.8279 | 0.79406 | 0.73331
43602.4999 | 1.2554 | 1.5003 | 1.4144 | 1.0505 | 0.92884 | 0.82505 | 0.79143 | 0.73147
43602.4999 | 1.2552 | 1.5002 | 1.413 | 1.0499 | 0.92867 | 0.8251 | 0.79468 | 0.73179
43602.4999 | 1.2571 | 1.4993 | 1.4134 | 1.0504 | 0.92769 | 0.82434 | 0.79066 | 0.73103
43602.4999 | 1.2521 | 1.4999 | 1.413 | 1.0492 | 0.92868 | 0.82536 | 0.79093 | 0.73201
43602.4999 | 1.2582 | 1.501 | 1.4133 | 1.0508 | 0.92954 | 0.82607 | 0.79142 | 0.73262
43602.4999 | 1.2596 | 1.5008 | 1.4118 | 1.0504 | 0.92852 | 0.82498 | 0.79025 | 0.73163
43602.4999 | 1.2587 | 1.4988 | 1.4096 | 1.0505 | 0.92876 | 0.82503 | 0.7924 | 0.73243
43602.5001 | 1.261 | 1.499 | 1.4098 | 1.0521 | 0.92978 | 0.82639 | 0.79248 | 0.73247
43602.5001 | 1.2643 | 1.4979 | 1.4093 | 1.0524 | 0.92916 | 0.82558 | 0.79085 | 0.73188
43602.5001 | 1.2641 | 1.4999 | 1.4104 | 1.0531 | 0.92833 | 0.82517 | 0.79091 | 0.73155
43602.5001 | 1.2645 | 1.4992 | 1.4098 | 1.0533 | 0.9305 | 0.827 | 0.79447 | 0.7329
43602.5001 | 1.2624 | 1.4979 | 1.4086 | 1.0522 | 0.92982 | 0.82622 | 0.79231 | 0.73281
43602.5001 | 1.2607 | 1.4979 | 1.4084 | 1.0527 | 0.9291 | 0.82543 | 0.79146 | 0.73219
43602.5001 | 1.2668 | 1.5026 | 1.4116 | 1.0573 | 0.93268 | 0.82839 | 0.79364 | 0.73314
43602.5003 | 1.2782 | 1.5099 | 1.4162 | 1.0624 | 0.93639 | 0.83179 | 0.79601 | 0.73469
43602.5003 | 1.2836 | 1.5104 | 1.4163 | 1.063 | 0.93714 | 0.83229 | 0.79719 | 0.73479
43602.5003 | 1.2868 | 1.5131 | 1.4186 | 1.0652 | 0.93885 | 0.83326 | 0.80141 | 0.73537
43602.5003 | 1.2856 | 1.5148 | 1.4189 | 1.0652 | 0.9398 | 0.83429 | 0.79979 | 0.73616
43602.5003 | 1.2858 | 1.5158 | 1.4209 | 1.0682 | 0.94007 | 0.83451 | 0.79958 | 0.73566
43602.5002 | 1.2865 | 1.5164 | 1.4217 | 1.0697 | 0.94131 | 0.83565 | 0.80025 | 0.73638
43602.5004 | 1.2819 | 1.512 | 1.4175 | 1.0666 | 0.93927 | 0.83432 | 0.79966 | 0.73611
43602.5004 | 1.2865 | 1.5113 | 1.4174 | 1.067 | 0.94039 | 0.8351 | 0.80065 | 0.73683
43602.5005 | 1.2788 | 1.507 | 1.4144 | 1.0633 | 0.93814 | 0.83331 | 0.79866 | 0.73609
43602.5005 | 1.2797 | 1.5083 | 1.4148 | 1.0636 | 0.93761 | 0.83335 | 0.79874 | 0.73609
43602.5005 | 1.2793 | 1.508 | 1.4145 | 1.0632 | 0.93676 | 0.83257 | 0.79808 | 0.73555
43602.5004 | 1.2761 | 1.5043 | 1.4118 | 1.0621 | 0.93542 | 0.83179 | 0.79947 | 0.73561
43602.5006 | 1.2669 | 1.4949 | 1.4046 | 1.0555 | 0.93107 | 0.82727 | 0.79401 | 0.73398
43602.5006 | 1.2638 | 1.4929 | 1.4033 | 1.0536 | 0.93042 | 0.82744 | 0.79351 | 0.73425
43602.5006 | 1.2621 | 1.4924 | 1.4023 | 1.053 | 0.9293 | 0.8262 | 0.79245 | 0.73373
43602.5006 | 1.2651 | 1.492 | 1.4012 | 1.0525 | 0.92843 | 0.82581 | 0.79221 | 0.73357
43602.5007 | 1.2598 | 1.4887 | 1.4002 | 1.051 | 0.92808 | 0.82545 | 0.79194 | 0.73357
43602.5006 | 1.2586 | 1.4877 | 1.3988 | 1.05 | 0.92595 | 0.82393 | 0.79157 | 0.73285
43602.5008 | 1.2539 | 1.4882 | 1.3996 | 1.0499 | 0.92727 | 0.82451 | 0.79077 | 0.73313
43602.5008 | 1.2608 | 1.4888 | 1.4003 | 1.0506 | 0.92775 | 0.82564 | 0.79165 | 0.73395
43602.5008 | 1.2625 | 1.4884 | 1.3998 | 1.0503 | 0.92714 | 0.82471 | 0.7898 | 0.73291
43602.5008 | 1.2549 | 1.4889 | 1.3999 | 1.0507 | 0.92703 | 0.82491 | 0.79162 | 0.73353
43602.5008 | 1.2553 | 1.4888 | 1.4005 | 1.0509 | 0.92734 | 0.82535 | 0.79441 | 0.73355
43602.5008 | 1.2563 | 1.4926 | 1.4044 | 1.0534 | 0.92941 | 0.82676 | 0.79322 | 0.7341
43602.501 | 1.2714 | 1.5027 | 1.4123 | 1.0591 | 0.93397 | 0.82979 | 0.7957 | 0.73523
43602.501 | 1.2675 | 1.5037 | 1.413 | 1.0599 | 0.93485 | 0.83041 | 0.79617 | 0.73561
43602.501 | 1.2714 | 1.5045 | 1.4142 | 1.0603 | 0.93524 | 0.83119 | 0.79647 | 0.73552
43602.501 | 1.2725 | 1.5066 | 1.4161 | 1.0615 | 0.93598 | 0.8319 | 0.79957 | 0.736
43602.501 | 1.2763 | 1.5071 | 1.4162 | 1.0611 | 0.93622 | 0.83216 | 0.79889 | 0.73571
43602.5009 | 1.2754 | 1.5066 | 1.4168 | 1.0619 | 0.93647 | 0.83238 | 0.79848 | 0.7362
43602.5011 | 1.2709 | 1.505 | 1.4152 | 1.0602 | 0.93587 | 0.83128 | 0.797 | 0.73548
43602.5011 | 1.2657 | 1.5031 | 1.4141 | 1.059 | 0.93432 | 0.8305 | 0.79598 | 0.73553
43602.5012 | 1.2703 | 1.5023 | 1.4133 | 1.0583 | 0.9339 | 0.82999 | 0.79581 | 0.73516
43602.5012 | 1.2627 | 1.503 | 1.4137 | 1.059 | 0.93426 | 0.83019 | 0.79728 | 0.73561
43602.5012 | 1.2708 | 1.5028 | 1.4128 | 1.0584 | 0.93397 | 0.82982 | 0.79815 | 0.73553
43602.5012 | 1.2622 | 1.5001 | 1.4113 | 1.0568 | 0.9332 | 0.82932 | 0.79514 | 0.73535
43602.5011 | 1.2546 | 1.4919 | 1.4035 | 1.0503 | 0.92795 | 0.82514 | 0.79119 | 0.73347
43602.5013 | 1.2519 | 1.484 | 1.3966 | 1.0455 | 0.92278 | 0.82127 | 0.7895 | 0.73223
43602.5013 | 1.2534 | 1.4827 | 1.395 | 1.0455 | 0.92228 | 0.8204 | 0.78708 | 0.73146
43602.5014 | 1.2402 | 1.48 | 1.3937 | 1.0434 | 0.92202 | 0.82033 | 0.7869 | 0.73181
43602.5014 | 1.249 | 1.4804 | 1.3931 | 1.0435 | 0.92063 | 0.81949 | 0.7866 | 0.73135
43602.5014 | 1.2458 | 1.4801 | 1.3922 | 1.0435 | 0.92057 | 0.8191 | 0.78685 | 0.73109
43602.5013 | 1.2432 | 1.4746 | 1.3877 | 1.04 | 0.91849 | 0.81745 | 0.78611 | 0.73034
43602.5015 | 1.2422 | 1.4675 | 1.3811 | 1.0359 | 0.91495 | 0.81437 | 0.7828 | 0.72941
43602.5015 | 1.2449 | 1.4684 | 1.3812 | 1.0371 | 0.91486 | 0.81428 | 0.78216 | 0.72906
43602.5015 | 1.2408 | 1.4675 | 1.3806 | 1.0371 | 0.9153 | 0.8144 | 0.78239 | 0.72918
43602.5015 | 1.2392 | 1.4648 | 1.3794 | 1.0352 | 0.91477 | 0.81402 | 0.78204 | 0.72906
43602.5015 | 1.2372 | 1.4655 | 1.3788 | 1.0359 | 0.91426 | 0.81374 | 0.78559 | 0.72888
43602.5015 | 1.2391 | 1.4672 | 1.3803 | 1.0377 | 0.9156 | 0.81441 | 0.78242 | 0.72873
43602.5017 | 1.2477 | 1.4703 | 1.3805 | 1.0403 | 0.91706 | 0.81543 | 0.7824 | 0.72911
43602.5017 | 1.2419 | 1.4707 | 1.3816 | 1.0402 | 0.91695 | 0.81605 | 0.78389 | 0.72896
43602.5017 | 1.2543 | 1.472 | 1.3825 | 1.0427 | 0.91751 | 0.81539 | 0.78695 | 0.72868
43602.5017 | 1.246 | 1.4727 | 1.3825 | 1.0419 | 0.91801 | 0.81644 | 0.78426 | 0.72898
43602.5017 | 1.2506 | 1.4701 | 1.3808 | 1.0406 | 0.91756 | 0.8158 | 0.78299 | 0.72882
43602.5017 | 1.256 | 1.4734 | 1.3829 | 1.0428 | 0.92006 | 0.81753 | 0.78455 | 0.7293
43602.5019 | 1.2595 | 1.4788 | 1.3868 | 1.0468 | 0.92217 | 0.81917 | 0.78904 | 0.72958
43602.5019 | 1.2503 | 1.4813 | 1.3883 | 1.049 | 0.92232 | 0.81917 | 0.78745 | 0.72976
43602.5019 | 1.261 | 1.4813 | 1.3886 | 1.0481 | 0.92325 | 0.82023 | 0.78692 | 0.72984
43602.5019 | 1.2584 | 1.4825 | 1.3897 | 1.0496 | 0.92367 | 0.8201 | 0.78657 | 0.72984
43602.5019 | 1.2606 | 1.4853 | 1.3908 | 1.0507 | 0.92421 | 0.82124 | 0.78743 | 0.73031
43602.5018 | 1.2665 | 1.4839 | 1.3908 | 1.0507 | 0.92524 | 0.82179 | 0.78817 | 0.73077
43602.502 | 1.2599 | 1.4839 | 1.39 | 1.0501 | 0.9246 | 0.8214 | 0.78748 | 0.73027
43602.502 | 1.2611 | 1.4829 | 1.3894 | 1.0493 | 0.92313 | 0.82042 | 0.78653 | 0.73013
43602.5021 | 1.2596 | 1.4852 | 1.3911 | 1.0506 | 0.92329 | 0.82026 | 0.78649 | 0.73001
43602.5021 | 1.2604 | 1.4823 | 1.3893 | 1.049 | 0.92399 | 0.82109 | 0.78736 | 0.7304
43602.5021 | 1.2642 | 1.4846 | 1.3913 | 1.0511 | 0.92477 | 0.82104 | 0.78958 | 0.73065
43602.502 | 1.2611 | 1.4862 | 1.3922 | 1.0519 | 0.92592 | 0.82244 | 0.79198 | 0.7311
43602.5022 | 1.2652 | 1.4838 | 1.3912 | 1.0506 | 0.92453 | 0.82194 | 0.78818 | 0.73062
43602.5022 | 1.2611 | 1.4842 | 1.3908 | 1.0506 | 0.92428 | 0.82096 | 0.78701 | 0.73049
43602.5022 | 1.2607 | 1.4833 | 1.3904 | 1.0498 | 0.92427 | 0.8211 | 0.78758 | 0.73023
43602.5022 | 1.2614 | 1.4826 | 1.3891 | 1.0485 | 0.92444 | 0.82115 | 0.79078 | 0.7304
43602.5023 | 1.2598 | 1.4813 | 1.3882 | 1.0479 | 0.92253 | 0.8196 | 0.78817 | 0.72996
43602.5022 | 1.2585 | 1.4795 | 1.386 | 1.0468 | 0.92262 | 0.81928 | 0.78655 | 0.73009
43602.5024 | 1.255 | 1.4779 | 1.385 | 1.0464 | 0.92173 | 0.81914 | 0.78619 | 0.72973
43602.5024 | 1.2466 | 1.478 | 1.3847 | 1.0458 | 0.92026 | 0.81832 | 0.78495 | 0.72957
43602.5024 | 1.2557 | 1.4776 | 1.3852 | 1.0461 | 0.92141 | 0.8189 | 0.78556 | 0.73032
43602.5024 | 1.2658 | 1.4813 | 1.3871 | 1.0481 | 0.92294 | 0.81998 | 0.78646 | 0.73029
43602.5024 | 1.2563 | 1.4786 | 1.3867 | 1.0471 | 0.92212 | 0.81944 | 0.78561 | 0.73017
43602.5024 | 1.2554 | 1.4806 | 1.3878 | 1.0485 | 0.92302 | 0.81969 | 0.78638 | 0.73032
43602.5026 | 1.2553 | 1.4765 | 1.3829 | 1.0449 | 0.92151 | 0.81899 | 0.78844 | 0.73018
43602.5026 | 1.2551 | 1.4773 | 1.3834 | 1.0455 | 0.91967 | 0.81799 | 0.78558 | 0.72947
43602.5026 | 1.258 | 1.4792 | 1.3842 | 1.0473 | 0.92085 | 0.81848 | 0.78547 | 0.72953
43602.5026 | 1.2528 | 1.4754 | 1.3806 | 1.0433 | 0.91981 | 0.81795 | 0.78461 | 0.72956
43602.5026 | 1.2533 | 1.4756 | 1.3815 | 1.0442 | 0.91898 | 0.81735 | 0.78406 | 0.72912
43602.5025 | 1.2528 | 1.4702 | 1.3777 | 1.0415 | 0.91653 | 0.81508 | 0.78439 | 0.72873
43602.5027 | 1.2352 | 1.4574 | 1.3683 | 1.034 | 0.91262 | 0.81232 | 0.77951 | 0.7278
43602.5027 | 1.2432 | 1.4596 | 1.3689 | 1.0351 | 0.91076 | 0.81063 | 0.77856 | 0.72708
43602.5028 | 1.2378 | 1.4552 | 1.3661 | 1.032 | 0.91002 | 0.81015 | 0.77828 | 0.72656
43602.5028 | 1.2415 | 1.4572 | 1.3668 | 1.0337 | 0.90973 | 0.80936 | 0.77723 | 0.72672
43602.5028 | 1.2309 | 1.4546 | 1.3648 | 1.0309 | 0.90822 | 0.80866 | 0.77935 | 0.72656
43602.5027 | 1.2356 | 1.4469 | 1.3572 | 1.0274 | 0.90326 | 0.80458 | 0.77378 | 0.72472
43602.5029 | 1.2235 | 1.433 | 1.3446 | 1.0186 | 0.89677 | 0.79908 | 0.77131 | 0.72244
43602.5029 | 1.2215 | 1.4324 | 1.344 | 1.0182 | 0.89629 | 0.79859 | 0.76911 | 0.72189
43602.5029 | 1.2198 | 1.4304 | 1.3423 | 1.0172 | 0.89554 | 0.7977 | 0.76766 | 0.72189
43602.5029 | 1.2138 | 1.4284 | 1.3408 | 1.0157 | 0.89438 | 0.79683 | 0.7671 | 0.72135
43602.503 | 1.2093 | 1.4272 | 1.3391 | 1.0146 | 0.89299 | 0.7959 | 0.7648 | 0.72085
43602.5029 | 1.2136 | 1.4214 | 1.3326 | 1.0119 | 0.88899 | 0.79233 | 0.76507 | 0.71913
43602.5031 | 1.2114 | 1.4161 | 1.3252 | 1.0083 | 0.88755 | 0.79107 | 0.76253 | 0.7183
43602.5031 | 1.2016 | 1.4132 | 1.3238 | 1.0075 | 0.88505 | 0.78875 | 0.75977 | 0.71681
43602.5031 | 1.2105 | 1.4133 | 1.3232 | 1.0073 | 0.88512 | 0.78892 | 0.76031 | 0.71713
43602.5031 | 1.2063 | 1.4107 | 1.3217 | 1.0061 | 0.88585 | 0.78942 | 0.76468 | 0.71719
43602.5031 | 1.2066 | 1.4116 | 1.3225 | 1.0076 | 0.885 | 0.78872 | 0.76163 | 0.71682
43602.5031 | 1.1968 | 1.4093 | 1.3182 | 1.0062 | 0.88158 | 0.7865 | 0.75808 | 0.71489
43602.5033 | 1.2104 | 1.4041 | 1.3114 | 1.0029 | 0.88222 | 0.78607 | 0.75719 | 0.71473
43602.5033 | 1.207 | 1.4011 | 1.3086 | 1.001 | 0.88054 | 0.78484 | 0.75568 | 0.71431
43602.5033 | 1.2138 | 1.4052 | 1.3112 | 1.0043 | 0.8809 | 0.78501 | 0.75528 | 0.71437
43602.5033 | 1.2057 | 1.403 | 1.3095 | 1.0029 | 0.8809 | 0.78565 | 0.75607 | 0.71439
43602.5033 | 1.2043 | 1.4049 | 1.3108 | 1.0036 | 0.88132 | 0.78573 | 0.75896 | 0.71435
43602.5033 | 1.2073 | 1.4111 | 1.3124 | 1.0075 | 0.88304 | 0.78713 | 0.75834 | 0.71414
43602.5034 | 1.2199 | 1.4104 | 1.3123 | 1.0083 | 0.8847 | 0.78815 | 0.75805 | 0.71456
43602.5035 | 1.2181 | 1.4121 | 1.3126 | 1.0081 | 0.8844 | 0.78787 | 0.76112 | 0.71425
43602.5035 | 1.2048 | 1.4112 | 1.3133 | 1.0075 | 0.8843 | 0.7889 | 0.76008 | 0.71492
43602.5035 | 1.2201 | 1.4172 | 1.3177 | 1.0123 | 0.88753 | 0.79067 | 0.76079 | 0.71574
43602.5035 | 1.2275 | 1.4136 | 1.3144 | 1.0101 | 0.88511 | 0.78876 | 0.75911 | 0.71502
43602.5034 | 1.212 | 1.4073 | 1.3119 | 1.0066 | 0.88635 | 0.78996 | 0.75985 | 0.71494
43602.5036 | 1.2188 | 1.4084 | 1.3112 | 1.0067 | 0.88214 | 0.78673 | 0.759 | 0.71427
43602.5036 | 1.1984 | 1.4056 | 1.3101 | 1.0048 | 0.88009 | 0.78509 | 0.75628 | 0.71324
43602.5036 | 1.2096 | 1.4074 | 1.3104 | 1.0055 | 0.88133 | 0.78613 | 0.75666 | 0.71426
43602.5037 | 1.2158 | 1.4066 | 1.3106 | 1.0053 | 0.88169 | 0.78587 | 0.75599 | 0.71446
43602.5037 | 1.217 | 1.4047 | 1.3088 | 1.0032 | 0.8793 | 0.78379 | 0.75758 | 0.71312
43602.5036 | 1.2022 | 1.4025 | 1.3089 | 1.0021 | 0.87811 | 0.78282 | 0.75364 | 0.71386
43602.5038 | 1.2058 | 1.3993 | 1.306 | 0.99873 | 0.87599 | 0.78083 | 0.75276 | 0.71346
43602.5038 | 1.2004 | 1.3987 | 1.3059 | 0.999 | 0.87705 | 0.78163 | 0.75319 | 0.71362
43602.5038 | 1.1905 | 1.3999 | 1.3064 | 0.99943 | 0.8753 | 0.78039 | 0.75253 | 0.71266
43602.5038 | 1.2015 | 1.3995 | 1.306 | 0.9988 | 0.87672 | 0.78167 | 0.75285 | 0.71347
43602.5038 | 1.1856 | 1.4 | 1.3066 | 0.99883 | 0.87408 | 0.78018 | 0.75173 | 0.71286
43602.5038 | 1.1919 | 1.3922 | 1.3024 | 0.99425 | 0.87592 | 0.78067 | 0.7527 | 0.7132
43602.504 | 1.1677 | 1.3894 | 1.3015 | 0.99163 | 0.87009 | 0.77744 | 0.74937 | 0.71291
43602.504 | 1.1792 | 1.3944 | 1.3044 | 0.99511 | 0.87122 | 0.77753 | 0.74942 | 0.71269
43602.504 | 1.1743 | 1.3872 | 1.2998 | 0.99011 | 0.87069 | 0.77732 | 0.7494 | 0.71234
43602.504 | 1.1791 | 1.3857 | 1.299 | 0.98989 | 0.86922 | 0.77568 | 0.74823 | 0.71179
43602.504 | 1.1893 | 1.3884 | 1.3 | 0.99098 | 0.86881 | 0.77569 | 0.74738 | 0.71242
43602.504 | 1.164 | 1.3764 | 1.2925 | 0.98258 | 0.86396 | 0.77226 | 0.74471 | 0.71101
43602.5042 | 1.176 | 1.3765 | 1.2909 | 0.9824 | 0.86076 | 0.76887 | 0.74209 | 0.71026
43602.5042 | 1.154 | 1.3658 | 1.2844 | 0.97436 | 0.85891 | 0.76817 | 0.74102 | 0.70984
43602.5042 | 1.1582 | 1.3689 | 1.2856 | 0.97635 | 0.8567 | 0.7666 | 0.74287 | 0.70957
43602.5042 | 1.1636 | 1.3679 | 1.2852 | 0.97686 | 0.85715 | 0.76668 | 0.74234 | 0.70962
43602.5042 | 1.1561 | 1.3662 | 1.2841 | 0.9747 | 0.85658 | 0.76638 | 0.74055 | 0.70931
43602.5042 | 1.1539 | 1.361 | 1.2794 | 0.97103 | 0.85376 | 0.76407 | 0.73747 | 0.70891
43602.5043 | 1.1446 | 1.3515 | 1.2703 | 0.96517 | 0.84743 | 0.75847 | 0.73273 | 0.70694
43602.5043 | 1.1413 | 1.3484 | 1.2678 | 0.96267 | 0.84662 | 0.75826 | 0.73285 | 0.70658
43602.5044 | 1.139 | 1.3468 | 1.2673 | 0.96229 | 0.84543 | 0.75747 | 0.73618 | 0.70643
43602.5044 | 1.1454 | 1.3476 | 1.2668 | 0.96324 | 0.84528 | 0.75719 | 0.73288 | 0.70619
43602.5044 | 1.1411 | 1.3441 | 1.2648 | 0.96052 | 0.84413 | 0.75639 | 0.73105 | 0.70582
43602.5043 | 1.1393 | 1.3423 | 1.2619 | 0.95926 | 0.84285 | 0.75538 | 0.72988 | 0.70524
43602.5045 | 1.1402 | 1.3427 | 1.2617 | 0.96098 | 0.84584 | 0.75644 | 0.7309 | 0.70546
43602.5045 | 1.1369 | 1.3427 | 1.2613 | 0.96131 | 0.84243 | 0.75451 | 0.7302 | 0.70433
43602.5045 | 1.1436 | 1.3445 | 1.2625 | 0.96272 | 0.84422 | 0.75555 | 0.72992 | 0.70493
43602.5046 | 1.1437 | 1.3453 | 1.2631 | 0.96381 | 0.84632 | 0.75707 | 0.73201 | 0.70522
43602.5046 | 1.1374 | 1.3421 | 1.2614 | 0.96174 | 0.84416 | 0.75571 | 0.73098 | 0.70463
43602.5045 | 1.1495 | 1.3444 | 1.2616 | 0.96367 | 0.84706 | 0.75754 | 0.7323 | 0.70512
43602.5047 | 1.1445 | 1.3469 | 1.2635 | 0.96576 | 0.84682 | 0.75718 | 0.73191 | 0.70454
43602.5047 | 1.153 | 1.3461 | 1.2623 | 0.96503 | 0.84715 | 0.75785 | 0.73189 | 0.70447
43602.5047 | 1.1536 | 1.3455 | 1.2611 | 0.96462 | 0.84602 | 0.75696 | 0.73102 | 0.70449
43602.5047 | 1.1584 | 1.3471 | 1.263 | 0.96671 | 0.84655 | 0.75688 | 0.73127 | 0.70456
43602.5047 | 1.1539 | 1.3468 | 1.263 | 0.96602 | 0.84853 | 0.75835 | 0.73245 | 0.70488
43602.5047 | 1.1497 | 1.3449 | 1.2611 | 0.96458 | 0.84737 | 0.75771 | 0.73385 | 0.70466
43602.5049 | 1.1497 | 1.3405 | 1.2569 | 0.96116 | 0.84327 | 0.75453 | 0.72867 | 0.70412
43602.5049 | 1.1547 | 1.3445 | 1.26 | 0.96469 | 0.84466 | 0.75543 | 0.73033 | 0.70424
43602.5049 | 1.1371 | 1.3348 | 1.2536 | 0.95694 | 0.84399 | 0.7552 | 0.73052 | 0.70381
43602.5049 | 1.143 | 1.3409 | 1.2573 | 0.96153 | 0.84236 | 0.7539 | 0.72826 | 0.70361
43602.5049 | 1.1452 | 1.3395 | 1.2567 | 0.96103 | 0.844 | 0.75497 | 0.73004 | 0.70373
43602.5049 | 1.1402 | 1.3355 | 1.2529 | 0.95733 | 0.84021 | 0.75229 | 0.72804 | 0.70272
43602.505 | 1.1355 | 1.3286 | 1.2476 | 0.95264 | 0.83599 | 0.74923 | 0.72485 | 0.70208
43602.5051 | 1.1319 | 1.3278 | 1.2469 | 0.95263 | 0.83552 | 0.74876 | 0.72357 | 0.70176
43602.5051 | 1.1327 | 1.3281 | 1.247 | 0.9534 | 0.83634 | 0.74887 | 0.72346 | 0.70175
43602.505 | 1.1253 | 1.3246 | 1.2444 | 0.94963 | 0.83407 | 0.74787 | 0.72771 | 0.7013
43602.5052 | 1.1151 | 1.318 | 1.2404 | 0.94535 | 0.82897 | 0.74372 | 0.72051 | 0.70005
43602.5052 | 1.1202 | 1.325 | 1.2431 | 0.94878 | 0.8291 | 0.74387 | 0.72003 | 0.69997
43602.5052 | 1.1175 | 1.3218 | 1.2423 | 0.94732 | 0.83161 | 0.7456 | 0.72138 | 0.70073
43602.5052 | 1.1175 | 1.3224 | 1.2425 | 0.94726 | 0.82973 | 0.74428 | 0.72282 | 0.70023
43602.5052 | 1.127 | 1.3247 | 1.2446 | 0.94959 | 0.83103 | 0.74489 | 0.72136 | 0.70057
43602.5054 | 1.1182 | 1.3216 | 1.2432 | 0.94674 | 0.82911 | 0.74333 | 0.71976 | 0.69978
43602.5054 | 1.1198 | 1.3208 | 1.2429 | 0.94542 | 0.83019 | 0.74428 | 0.71928 | 0.70001
43602.5054 | 1.1206 | 1.3207 | 1.2423 | 0.94568 | 0.82776 | 0.74262 | 0.72158 | 0.69938
43602.5054 | 1.1192 | 1.3205 | 1.2422 | 0.94551 | 0.82952 | 0.74355 | 0.71955 | 0.69972
43602.5054 | 1.1165 | 1.3184 | 1.2409 | 0.94376 | 0.8271 | 0.74233 | 0.71815 | 0.69917
43602.5054 | 1.1073 | 1.3124 | 1.2363 | 0.93933 | 0.82379 | 0.73974 | 0.71561 | 0.69847
43602.5055 | 1.1006 | 1.309 | 1.2328 | 0.93471 | 0.82091 | 0.73681 | 0.71327 | 0.69732
43602.5056 | 1.1023 | 1.3086 | 1.2328 | 0.93522 | 0.81983 | 0.73623 | 0.71252 | 0.69704
43602.5056 | 1.1035 | 1.3089 | 1.2331 | 0.93644 | 0.82033 | 0.73649 | 0.71217 | 0.69714
43602.5056 | 1.1017 | 1.3078 | 1.2319 | 0.93403 | 0.82022 | 0.73607 | 0.71471 | 0.69728
43602.5056 | 1.1029 | 1.3081 | 1.2319 | 0.93522 | 0.81875 | 0.73523 | 0.71224 | 0.69682
43602.5055 | 1.0989 | 1.3061 | 1.2304 | 0.9324 | 0.81745 | 0.73425 | 0.71269 | 0.69608
43602.5057 | 1.0997 | 1.3048 | 1.2293 | 0.9323 | 0.81679 | 0.73326 | 0.70993 | 0.6958
43602.5057 | 1.0971 | 1.3036 | 1.2286 | 0.93178 | 0.81686 | 0.73335 | 0.70937 | 0.69588
43602.5057 | 1.0914 | 1.3004 | 1.2265 | 0.92966 | 0.81538 | 0.73286 | 0.70843 | 0.69522
43602.5058 | 1.0882 | 1.2998 | 1.2264 | 0.92831 | 0.81425 | 0.73196 | 0.71241 | 0.69517
43602.5058 | 1.0927 | 1.3016 | 1.2264 | 0.92982 | 0.81443 | 0.73181 | 0.70975 | 0.69493
43602.5057 | 1.0932 | 1.2993 | 1.2242 | 0.92806 | 0.81324 | 0.73053 | 0.70702 | 0.69439
43602.5059 | 1.0905 | 1.2945 | 1.2202 | 0.92591 | 0.81119 | 0.72911 | 0.70579 | 0.69395
43602.5059 | 1.0838 | 1.2946 | 1.2208 | 0.92604 | 0.81174 | 0.72946 | 0.70622 | 0.69408
43602.5059 | 1.0943 | 1.296 | 1.2207 | 0.92705 | 0.81193 | 0.72932 | 0.70704 | 0.69421
43602.5059 | 1.0876 | 1.2919 | 1.2182 | 0.92491 | 0.81153 | 0.72893 | 0.70916 | 0.69411
43602.5059 | 1.0878 | 1.2899 | 1.2167 | 0.92326 | 0.81001 | 0.72818 | 0.70524 | 0.69366
43602.5059 | 1.088 | 1.2895 | 1.2142 | 0.92409 | 0.80915 | 0.72712 | 0.70428 | 0.69363
43602.5061 | 1.088 | 1.2882 | 1.2123 | 0.92378 | 0.80972 | 0.72738 | 0.7045 | 0.69317
43602.5061 | 1.0878 | 1.2859 | 1.2107 | 0.92183 | 0.8078 | 0.72636 | 0.70351 | 0.69252
43602.5061 | 1.0851 | 1.2851 | 1.2105 | 0.92139 | 0.80816 | 0.72624 | 0.70371 | 0.69293
43602.5061 | 1.0894 | 1.2886 | 1.2119 | 0.92404 | 0.80828 | 0.72622 | 0.70358 | 0.6928
43602.5061 | 1.0929 | 1.2896 | 1.212 | 0.92471 | 0.80974 | 0.72719 | 0.70365 | 0.69292
43602.5061 | 1.0915 | 1.2884 | 1.2096 | 0.92468 | 0.80942 | 0.72679 | 0.70446 | 0.69238
43602.5063 | 1.0862 | 1.2857 | 1.2068 | 0.92382 | 0.80904 | 0.72654 | 0.70413 | 0.6923
43602.5063 | 1.0892 | 1.2866 | 1.2075 | 0.92449 | 0.80928 | 0.72698 | 0.70384 | 0.69254
43602.5063 | 1.0892 | 1.2841 | 1.2057 | 0.92288 | 0.80747 | 0.72606 | 0.7056 | 0.69209
43602.5063 | 1.0876 | 1.2846 | 1.2056 | 0.92317 | 0.80871 | 0.72653 | 0.70516 | 0.69236
43602.5063 | 1.0876 | 1.285 | 1.2054 | 0.92318 | 0.80812 | 0.7266 | 0.70359 | 0.69259
43602.5063 | 1.0987 | 1.2859 | 1.2052 | 0.92461 | 0.80878 | 0.72669 | 0.70447 | 0.69286
43602.5064 | 1.0944 | 1.2849 | 1.205 | 0.92545 | 0.8111 | 0.72801 | 0.70741 | 0.69337
43602.5065 | 1.0944 | 1.2847 | 1.204 | 0.92413 | 0.80844 | 0.72682 | 0.70607 | 0.69253
43602.5065 | 1.0995 | 1.2892 | 1.2074 | 0.92809 | 0.81126 | 0.72802 | 0.70618 | 0.69283
43602.5065 | 1.0911 | 1.2856 | 1.2058 | 0.9248 | 0.81173 | 0.72843 | 0.70671 | 0.69322
43602.5065 | 1.0888 | 1.2849 | 1.2054 | 0.92491 | 0.81045 | 0.728 | 0.70559 | 0.69317
43602.5064 | 1.0954 | 1.2838 | 1.2046 | 0.92597 | 0.81049 | 0.72726 | 0.70561 | 0.69332
43602.5066 | 1.0879 | 1.2803 | 1.2017 | 0.9229 | 0.80959 | 0.72647 | 0.70516 | 0.6935
43602.5066 | 1.0885 | 1.2782 | 1.2004 | 0.92155 | 0.80715 | 0.72544 | 0.7035 | 0.69257
43602.5067 | 1.0834 | 1.2771 | 1.1995 | 0.92131 | 0.80674 | 0.72503 | 0.70341 | 0.69271
43602.5067 | 1.0795 | 1.2757 | 1.1976 | 0.91934 | 0.80533 | 0.72389 | 0.70486 | 0.69207
43602.5067 | 1.0745 | 1.2751 | 1.1987 | 0.91969 | 0.80604 | 0.72442 | 0.70354 | 0.69247
43602.5066 | 1.0708 | 1.2704 | 1.1942 | 0.91636 | 0.80236 | 0.7223 | 0.702 | 0.69192
43602.5068 | 1.0761 | 1.2676 | 1.1908 | 0.91429 | 0.80239 | 0.72162 | 0.70022 | 0.69132
43602.5068 | 1.0788 | 1.2689 | 1.1912 | 0.91497 | 0.80019 | 0.72018 | 0.69809 | 0.69069
43602.5068 | 1.0757 | 1.2685 | 1.1915 | 0.91477 | 0.80203 | 0.7212 | 0.70342 | 0.69115
43602.5068 | 1.0706 | 1.2667 | 1.191 | 0.91416 | 0.80122 | 0.72087 | 0.70037 | 0.69075
43602.5069 | 1.0705 | 1.2665 | 1.1911 | 0.91374 | 0.8004 | 0.72032 | 0.69871 | 0.69122
43602.5068 | 1.0707 | 1.2665 | 1.1901 | 0.91402 | 0.80075 | 0.72028 | 0.69903 | 0.6911
43602.507 | 1.0657 | 1.2632 | 1.1866 | 0.91207 | 0.79925 | 0.71954 | 0.69891 | 0.691
43602.507 | 1.0712 | 1.2636 | 1.1866 | 0.91239 | 0.79933 | 0.7191 | 0.69814 | 0.69112
43602.507 | 1.0751 | 1.2652 | 1.1885 | 0.91451 | 0.80035 | 0.71986 | 0.70004 | 0.69157
43602.507 | 1.0706 | 1.2628 | 1.187 | 0.91158 | 0.80089 | 0.72042 | 0.69882 | 0.69137
43602.507 | 1.0715 | 1.2631 | 1.1867 | 0.9125 | 0.79942 | 0.71923 | 0.69935 | 0.69116
43602.507 | 1.0659 | 1.2605 | 1.184 | 0.90972 | 0.79855 | 0.71865 | 0.69776 | 0.69054
43602.5072 | 1.0675 | 1.2598 | 1.1832 | 0.9102 | 0.79784 | 0.71785 | 0.70012 | 0.69051
43602.5072 | 1.0734 | 1.2614 | 1.1838 | 0.91183 | 0.79961 | 0.71861 | 0.69804 | 0.69075
43602.5072 | 1.0656 | 1.2587 | 1.1817 | 0.90875 | 0.79706 | 0.71749 | 0.69688 | 0.69005
43602.5072 | 1.0656 | 1.2582 | 1.1815 | 0.90922 | 0.79823 | 0.71779 | 0.6968 | 0.69073
43602.5072 | 1.0589 | 1.257 | 1.1821 | 0.90942 | 0.79711 | 0.7172 | 0.69684 | 0.69021
43602.5072 | 1.0647 | 1.2582 | 1.1801 | 0.90968 | 0.79722 | 0.71684 | 0.69624 | 0.69024
43602.5074 | 1.0695 | 1.2593 | 1.1805 | 0.91093 | 0.79724 | 0.71641 | 0.69591 | 0.68995
43602.5074 | 1.0674 | 1.2614 | 1.1824 | 0.91287 | 0.80073 | 0.71895 | 0.69887 | 0.69069
43602.5074 | 1.0657 | 1.2573 | 1.18 | 0.91025 | 0.7972 | 0.71694 | 0.69777 | 0.68978
43602.5074 | 1.0642 | 1.2605 | 1.1828 | 0.91269 | 0.80001 | 0.71843 | 0.70105 | 0.6905
43602.5074 | 1.0693 | 1.2613 | 1.1832 | 0.91352 | 0.79962 | 0.7189 | 0.69855 | 0.6903
43602.5073 | 1.081 | 1.2675 | 1.189 | 0.91723 | 0.8047 | 0.72258 | 0.70108 | 0.69217
43602.5075 | 1.0885 | 1.2727 | 1.1939 | 0.92083 | 0.80568 | 0.72376 | 0.70207 | 0.69198
43602.5075 | 1.0808 | 1.2777 | 1.1975 | 0.92322 | 0.80693 | 0.7242 | 0.7019 | 0.69224
43602.5076 | 1.08 | 1.2749 | 1.1966 | 0.92134 | 0.80895 | 0.72648 | 0.70735 | 0.6931
43602.5076 | 1.079 | 1.2776 | 1.1982 | 0.922 | 0.80664 | 0.72463 | 0.70412 | 0.69181
43602.5076 | 1.0925 | 1.2807 | 1.2002 | 0.92495 | 0.80968 | 0.72633 | 0.70432 | 0.69303
43602.5075 | 1.0939 | 1.2829 | 1.2033 | 0.92572 | 0.81063 | 0.7273 | 0.70467 | 0.69383
43602.5077 | 1.0828 | 1.2779 | 1.2002 | 0.92153 | 0.80832 | 0.72596 | 0.70415 | 0.69349
43602.5077 | 1.0835 | 1.2781 | 1.2003 | 0.92222 | 0.80779 | 0.72574 | 0.70395 | 0.69348
43602.5077 | 1.0826 | 1.2777 | 1.1998 | 0.92176 | 0.80688 | 0.72514 | 0.70304 | 0.69285
43602.5077 | 1.0763 | 1.2746 | 1.1986 | 0.92005 | 0.80805 | 0.72555 | 0.70536 | 0.69305
43602.5078 | 1.0747 | 1.273 | 1.1967 | 0.91777 | 0.80485 | 0.72363 | 0.7032 | 0.69253
43602.5077 | 1.0616 | 1.2583 | 1.1851 | 0.90639 | 0.79561 | 0.71693 | 0.69603 | 0.69033
43602.5079 | 1.0577 | 1.2569 | 1.1827 | 0.90612 | 0.79525 | 0.71614 | 0.69565 | 0.69074
43602.5079 | 1.0535 | 1.2513 | 1.1798 | 0.90245 | 0.79221 | 0.71453 | 0.69444 | 0.68978
43602.5079 | 1.0551 | 1.2536 | 1.1801 | 0.90319 | 0.79163 | 0.71399 | 0.69352 | 0.68954
43602.5079 | 1.0509 | 1.2526 | 1.1804 | 0.90278 | 0.79143 | 0.71414 | 0.69542 | 0.68934
43602.5079 | 1.0556 | 1.2531 | 1.1796 | 0.90348 | 0.79146 | 0.71392 | 0.69345 | 0.68952
43602.5079 | 1.0558 | 1.2554 | 1.1815 | 0.90503 | 0.79185 | 0.71324 | 0.6952 | 0.6893
43602.5081 | 1.0505 | 1.2531 | 1.1805 | 0.90343 | 0.79056 | 0.71277 | 0.69501 | 0.68836
43602.5081 | 1.0489 | 1.2526 | 1.1798 | 0.90381 | 0.79082 | 0.71311 | 0.69249 | 0.68864
43602.5081 | 1.0575 | 1.2577 | 1.1813 | 0.90591 | 0.79171 | 0.71336 | 0.69229 | 0.68879
43602.5081 | 1.0637 | 1.2591 | 1.1817 | 0.90761 | 0.79271 | 0.71409 | 0.69337 | 0.68846
43602.5081 | 1.0541 | 1.2538 | 1.1812 | 0.90443 | 0.79324 | 0.71454 | 0.69367 | 0.68866
43602.5081 | 1.0675 | 1.2628 | 1.1865 | 0.91168 | 0.79677 | 0.71668 | 0.69568 | 0.68881
43602.5083 | 1.0717 | 1.2662 | 1.1888 | 0.91385 | 0.799 | 0.7191 | 0.69637 | 0.68982
43602.5083 | 1.0768 | 1.2686 | 1.1899 | 0.91568 | 0.79973 | 0.71959 | 0.69726 | 0.69012
43602.5083 | 1.071 | 1.2651 | 1.1885 | 0.91241 | 0.80012 | 0.71967 | 0.70051 | 0.68992
43602.5083 | 1.0816 | 1.2701 | 1.1906 | 0.91634 | 0.79939 | 0.71922 | 0.69752 | 0.68972
43602.5083 | 1.0737 | 1.2672 | 1.1903 | 0.91521 | 0.80175 | 0.72076 | 0.69901 | 0.69052
43602.5082 | 1.0795 | 1.269 | 1.1916 | 0.9164 | 0.8005 | 0.72055 | 0.69984 | 0.69017
43602.5084 | 1.0782 | 1.2684 | 1.1922 | 0.91667 | 0.803 | 0.72275 | 0.70051 | 0.69124
43602.5085 | 1.0771 | 1.269 | 1.1919 | 0.91644 | 0.80069 | 0.72079 | 0.69901 | 0.69054
43602.5085 | 1.0755 | 1.2694 | 1.1922 | 0.91656 | 0.80136 | 0.72157 | 0.70025 | 0.69075
43602.5085 | 1.0767 | 1.2716 | 1.1932 | 0.91698 | 0.80186 | 0.72223 | 0.70143 | 0.69102
43602.5085 | 1.0785 | 1.2705 | 1.1929 | 0.91645 | 0.80202 | 0.72192 | 0.70467 | 0.69143
43602.5084 | 1.0717 | 1.2679 | 1.1928 | 0.91636 | 0.80182 | 0.72237 | 0.70096 | 0.69207
43602.5086 | 1.0683 | 1.2635 | 1.1893 | 0.91177 | 0.79938 | 0.72115 | 0.70228 | 0.6925
43602.5086 | 1.0602 | 1.2587 | 1.1872 | 0.9097 | 0.79794 | 0.72001 | 0.69947 | 0.69173
43602.5086 | 1.0577 | 1.2569 | 1.1854 | 0.90805 | 0.79544 | 0.71884 | 0.69765 | 0.69164
43602.5087 | 1.0595 | 1.2591 | 1.1868 | 0.90975 | 0.79645 | 0.71912 | 0.69888 | 0.69147
43602.5087 | 1.0575 | 1.2572 | 1.1859 | 0.90821 | 0.7962 | 0.71908 | 0.69863 | 0.69174
43602.5086 | 1.0501 | 1.2509 | 1.1813 | 0.90329 | 0.79208 | 0.71593 | 0.69555 | 0.69123
43602.5088 | 1.0466 | 1.2498 | 1.1794 | 0.90239 | 0.79082 | 0.71499 | 0.69446 | 0.69092
43602.5088 | 1.0449 | 1.2481 | 1.1789 | 0.90106 | 0.79143 | 0.71532 | 0.69488 | 0.69112
43602.5088 | 1.0459 | 1.2451 | 1.1774 | 0.89866 | 0.78963 | 0.71432 | 0.69367 | 0.69069
43602.5088 | 1.0467 | 1.2488 | 1.179 | 0.90102 | 0.78991 | 0.71428 | 0.69566 | 0.69064
43602.5089 | 1.043 | 1.2451 | 1.1777 | 0.89937 | 0.79019 | 0.71449 | 0.69387 | 0.69036
43602.5088 | 1.04 | 1.246 | 1.1771 | 0.89953 | 0.78969 | 0.71388 | 0.69317 | 0.69017
43602.509 | 1.0461 | 1.245 | 1.1763 | 0.89894 | 0.78887 | 0.71292 | 0.69252 | 0.68989
43602.509 | 1.0466 | 1.247 | 1.177 | 0.89942 | 0.78916 | 0.71323 | 0.6927 | 0.68955
43602.509 | 1.0444 | 1.2486 | 1.1781 | 0.90155 | 0.79008 | 0.71382 | 0.69575 | 0.68967
43602.509 | 1.0478 | 1.249 | 1.1795 | 0.90202 | 0.79065 | 0.7141 | 0.69426 | 0.6897
43602.509 | 1.0499 | 1.2499 | 1.1795 | 0.9023 | 0.79067 | 0.7143 | 0.69349 | 0.68998
43602.509 | 1.0621 | 1.2607 | 1.1878 | 0.90951 | 0.79676 | 0.71833 | 0.69905 | 0.69098
43602.5092 | 1.0667 | 1.2635 | 1.1897 | 0.91185 | 0.80065 | 0.72099 | 0.70041 | 0.6914
43602.5092 | 1.0714 | 1.266 | 1.1908 | 0.91461 | 0.79932 | 0.72 | 0.70103 | 0.69154
43602.5092 | 1.0752 | 1.267 | 1.1903 | 0.91442 | 0.80142 | 0.72111 | 0.69958 | 0.69137
43602.5092 | 1.0673 | 1.2636 | 1.1894 | 0.91336 | 0.80082 | 0.72093 | 0.6992 | 0.69133
43602.5092 | 1.0589 | 1.2614 | 1.1882 | 0.91195 | 0.79922 | 0.71998 | 0.70002 | 0.69072
43602.5092 | 1.0615 | 1.2585 | 1.1853 | 0.91093 | 0.79936 | 0.72003 | 0.69891 | 0.69084
43602.5094 | 1.0632 | 1.2568 | 1.1837 | 0.90978 | 0.79737 | 0.71838 | 0.70131 | 0.69073
43602.5094 | 1.0611 | 1.2571 | 1.1836 | 0.90988 | 0.79749 | 0.71859 | 0.69919 | 0.69098
43602.5094 | 1.0619 | 1.2533 | 1.1811 | 0.90701 | 0.79683 | 0.71866 | 0.69805 | 0.6908
43602.5094 | 1.0593 | 1.254 | 1.1813 | 0.90736 | 0.79551 | 0.71729 | 0.69649 | 0.69037
43602.5094 | 1.0602 | 1.2572 | 1.1818 | 0.90882 | 0.79639 | 0.71802 | 0.69754 | 0.69095
43602.5093 | 1.0559 | 1.2493 | 1.1767 | 0.9036 | 0.79202 | 0.71545 | 0.69507 | 0.69004
43602.5095 | 1.0498 | 1.2463 | 1.173 | 0.90162 | 0.79111 | 0.71454 | 0.69404 | 0.68955
43602.5096 | 1.0462 | 1.2428 | 1.1714 | 0.90036 | 0.79039 | 0.71388 | 0.69333 | 0.68915
43602.5096 | 1.048 | 1.2444 | 1.1716 | 0.90102 | 0.78956 | 0.7134 | 0.69633 | 0.68896
43602.5096 | 1.0481 | 1.2439 | 1.1709 | 0.9008 | 0.79004 | 0.71345 | 0.69431 | 0.68921
43602.5096 | 1.0438 | 1.24 | 1.1691 | 0.89933 | 0.78868 | 0.71281 | 0.69268 | 0.68887
43602.5095 | 1.0404 | 1.2376 | 1.1657 | 0.89636 | 0.78538 | 0.71023 | 0.69004 | 0.6877
43602.5097 | 1.0381 | 1.2347 | 1.164 | 0.89561 | 0.78575 | 0.71052 | 0.69092 | 0.68789
43602.5097 | 1.0416 | 1.2359 | 1.1635 | 0.8963 | 0.78515 | 0.71001 | 0.69038 | 0.68775
43602.5097 | 1.0424 | 1.2361 | 1.1636 | 0.89646 | 0.78534 | 0.71009 | 0.69302 | 0.68774
43602.5098 | 1.0385 | 1.235 | 1.1633 | 0.89546 | 0.78495 | 0.7101 | 0.69165 | 0.68787
43602.5097 | 1.0422 | 1.2356 | 1.1616 | 0.89536 | 0.78487 | 0.70943 | 0.68969 | 0.68728
43602.5099 | 1.0352 | 1.2293 | 1.1555 | 0.89248 | 0.78101 | 0.70676 | 0.68744 | 0.68583
43602.5099 | 1.0328 | 1.2269 | 1.1548 | 0.88961 | 0.78204 | 0.70711 | 0.68805 | 0.68617
43602.5099 | 1.0316 | 1.2244 | 1.1523 | 0.88934 | 0.77897 | 0.70562 | 0.68645 | 0.68536
43602.5099 | 1.0286 | 1.2249 | 1.1535 | 0.88952 | 0.77951 | 0.70589 | 0.68632 | 0.68573
43602.5099 | 1.0345 | 1.2245 | 1.1526 | 0.89023 | 0.7803 | 0.70617 | 0.68686 | 0.68597
43602.5099 | 1.0352 | 1.229 | 1.1543 | 0.89465 | 0.78237 | 0.7072 | 0.68743 | 0.68628
43602.5101 | 1.0367 | 1.2271 | 1.1526 | 0.8927 | 0.78255 | 0.70702 | 0.68774 | 0.68603
43602.5101 | 1.0374 | 1.2279 | 1.153 | 0.89337 | 0.78197 | 0.70696 | 0.68757 | 0.68603
43602.5101 | 1.0406 | 1.2282 | 1.1529 | 0.89327 | 0.78338 | 0.70749 | 0.69139 | 0.68612
43602.5101 | 1.0348 | 1.229 | 1.1544 | 0.89476 | 0.78336 | 0.70773 | 0.68985 | 0.6865
43602.5101 | 1.0412 | 1.2294 | 1.1542 | 0.89458 | 0.78364 | 0.7076 | 0.68975 | 0.68614
43602.5102 | 1.0449 | 1.233 | 1.1577 | 0.89753 | 0.78782 | 0.71073 | 0.69187 | 0.68678
43602.5102 | 1.0471 | 1.2347 | 1.1579 | 0.8982 | 0.78474 | 0.70861 | 0.68835 | 0.68576
43602.5103 | 1.0378 | 1.2304 | 1.1568 | 0.89555 | 0.78701 | 0.71012 | 0.69031 | 0.68667
43602.5103 | 1.0399 | 1.2336 | 1.1578 | 0.89766 | 0.78472 | 0.70888 | 0.68881 | 0.68638
43602.5103 | 1.0418 | 1.2321 | 1.157 | 0.89727 | 0.78605 | 0.70959 | 0.69176 | 0.68649
43602.5102 | 1.0463 | 1.2356 | 1.1588 | 0.89913 | 0.78586 | 0.70964 | 0.68961 | 0.68615
43602.5104 | 1.0427 | 1.2334 | 1.1583 | 0.89768 | 0.78693 | 0.71021 | 0.69056 | 0.68653
43602.5104 | 1.0445 | 1.2341 | 1.1579 | 0.89757 | 0.78505 | 0.70934 | 0.68991 | 0.68589
43602.5104 | 1.0479 | 1.2353 | 1.1595 | 0.89947 | 0.78708 | 0.71016 | 0.6905 | 0.68634
43602.5104 | 1.0479 | 1.2342 | 1.1591 | 0.89764 | 0.78701 | 0.71053 | 0.69071 | 0.68656
43602.5105 | 1.0453 | 1.2351 | 1.1594 | 0.89846 | 0.78604 | 0.71008 | 0.69155 | 0.68672
43602.5104 | 1.0397 | 1.2272 | 1.1545 | 0.89344 | 0.78335 | 0.70799 | 0.68833 | 0.68543
43602.5106 | 1.038 | 1.2276 | 1.1546 | 0.89373 | 0.78282 | 0.70788 | 0.68823 | 0.68606
43602.5106 | 1.0411 | 1.2293 | 1.1559 | 0.89524 | 0.78374 | 0.70816 | 0.68912 | 0.68619
43602.5106 | 1.0432 | 1.2296 | 1.1555 | 0.89496 | 0.78367 | 0.70823 | 0.69108 | 0.68586
43602.5106 | 1.0434 | 1.2297 | 1.1555 | 0.89489 | 0.78357 | 0.70798 | 0.69068 | 0.68583
43602.5106 | 1.0395 | 1.229 | 1.1567 | 0.89665 | 0.78414 | 0.70833 | 0.68942 | 0.68607
43602.5106 | 1.0453 | 1.241 | 1.1651 | 0.90344 | 0.78809 | 0.71129 | 0.69371 | 0.68696
43602.5108 | 1.0578 | 1.2436 | 1.1685 | 0.90413 | 0.79057 | 0.71342 | 0.69306 | 0.68793
43602.5108 | 1.0567 | 1.2456 | 1.1711 | 0.90582 | 0.79265 | 0.71475 | 0.69527 | 0.68826
43602.5108 | 1.0589 | 1.2464 | 1.1708 | 0.90565 | 0.79223 | 0.7148 | 0.69573 | 0.68847
43602.5108 | 1.0562 | 1.2449 | 1.171 | 0.90519 | 0.79206 | 0.71446 | 0.69375 | 0.68807
43602.5108 | 1.0552 | 1.2464 | 1.1723 | 0.90621 | 0.79236 | 0.7152 | 0.69477 | 0.68841
43602.5108 | 1.055 | 1.2459 | 1.1732 | 0.90525 | 0.79398 | 0.71671 | 0.69754 | 0.68927
43602.511 | 1.0543 | 1.2475 | 1.1739 | 0.90673 | 0.79218 | 0.7153 | 0.6975 | 0.68909
43602.511 | 1.0492 | 1.2451 | 1.1737 | 0.90501 | 0.79335 | 0.71582 | 0.69606 | 0.6895
43602.511 | 1.0528 | 1.2453 | 1.1731 | 0.90419 | 0.79235 | 0.71573 | 0.69569 | 0.68951
43602.511 | 1.0522 | 1.245 | 1.1722 | 0.90454 | 0.79154 | 0.71487 | 0.69427 | 0.68903
43602.511 | 1.0414 | 1.2436 | 1.1732 | 0.90429 | 0.79213 | 0.71564 | 0.69634 | 0.68928
43602.511 | 1.045 | 1.2397 | 1.1692 | 0.89985 | 0.78994 | 0.71446 | 0.69395 | 0.68927
43602.5112 | 1.0394 | 1.2338 | 1.1649 | 0.89573 | 0.78696 | 0.71264 | 0.69214 | 0.68903
43602.5112 | 1.0368 | 1.2344 | 1.1647 | 0.8971 | 0.78631 | 0.71227 | 0.69174 | 0.68841
43602.5112 | 1.039 | 1.2333 | 1.1637 | 0.89728 | 0.78701 | 0.71259 | 0.69176 | 0.68929
43602.5112 | 1.0342 | 1.2315 | 1.1624 | 0.89556 | 0.78521 | 0.71148 | 0.69153 | 0.68866
43602.5112 | 1.0353 | 1.233 | 1.1642 | 0.89736 | 0.7861 | 0.71166 | 0.69099 | 0.68887
43602.5111 | 1.0372 | 1.2296 | 1.1584 | 0.89475 | 0.78343 | 0.70951 | 0.68938 | 0.68778
43602.5113 | 1.0286 | 1.2291 | 1.1599 | 0.89432 | 0.78287 | 0.70906 | 0.69002 | 0.68763
43602.5114 | 1.0405 | 1.2315 | 1.1597 | 0.89614 | 0.78441 | 0.71039 | 0.69147 | 0.68843
43602.5114 | 1.0288 | 1.2292 | 1.1614 | 0.89518 | 0.78414 | 0.70976 | 0.69011 | 0.68794
43602.5114 | 1.03 | 1.23 | 1.1612 | 0.89565 | 0.78482 | 0.7102 | 0.69005 | 0.688
43602.5113 | 1.0359 | 1.2314 | 1.1616 | 0.89546 | 0.78566 | 0.71097 | 0.69331 | 0.68816
43602.5115 | 1.0459 | 1.2374 | 1.1647 | 0.90108 | 0.78864 | 0.71256 | 0.69283 | 0.68872
43602.5115 | 1.0463 | 1.2364 | 1.1651 | 0.89986 | 0.7878 | 0.71199 | 0.69244 | 0.68837
43602.5115 | 1.0458 | 1.2369 | 1.1647 | 0.89979 | 0.7877 | 0.71215 | 0.69547 | 0.68831
43602.5115 | 1.0382 | 1.2351 | 1.1649 | 0.89894 | 0.7883 | 0.71263 | 0.69424 | 0.68865
43602.5116 | 1.0401 | 1.2357 | 1.1645 | 0.8996 | 0.78747 | 0.71246 | 0.6928 | 0.68857
43602.5115 | 1.0413 | 1.239 | 1.1681 | 0.90232 | 0.79068 | 0.71469 | 0.69433 | 0.6894
43602.5117 | 1.0457 | 1.2367 | 1.1662 | 0.90102 | 0.78992 | 0.71387 | 0.69434 | 0.68898
43602.5117 | 1.045 | 1.2383 | 1.1677 | 0.90192 | 0.78943 | 0.71377 | 0.69426 | 0.68923
43602.5117 | 1.0465 | 1.2371 | 1.1656 | 0.90113 | 0.78963 | 0.7139 | 0.69444 | 0.68936
43602.5117 | 1.0463 | 1.2383 | 1.1657 | 0.90139 | 0.79041 | 0.71444 | 0.69403 | 0.68963
43602.5117 | 1.0394 | 1.235 | 1.164 | 0.90024 | 0.78869 | 0.71319 | 0.69676 | 0.68914
43602.5119 | 1.0367 | 1.23 | 1.1587 | 0.89673 | 0.78638 | 0.71158 | 0.6925 | 0.68905
43602.5119 | 1.0394 | 1.2298 | 1.158 | 0.8957 | 0.78587 | 0.71092 | 0.69159 | 0.68894
43602.5119 | 1.0369 | 1.23 | 1.1579 | 0.89654 | 0.78557 | 0.71069 | 0.69195 | 0.68849
43602.5119 | 1.0376 | 1.2311 | 1.1591 | 0.89807 | 0.78596 | 0.7106 | 0.69323 | 0.68858
43602.5119 | 1.0304 | 1.229 | 1.1591 | 0.89626 | 0.78697 | 0.71176 | 0.69212 | 0.68907
43602.5118 | 1.0381 | 1.2285 | 1.1566 | 0.89587 | 0.78535 | 0.71031 | 0.69129 | 0.6882
43602.512 | 1.0372 | 1.23 | 1.1579 | 0.89759 | 0.7875 | 0.71145 | 0.69251 | 0.68872
43602.512 | 1.0445 | 1.2285 | 1.1562 | 0.89594 | 0.78521 | 0.71017 | 0.69658 | 0.68801
43602.5121 | 1.036 | 1.2308 | 1.1594 | 0.898 | 0.78645 | 0.71074 | 0.69285 | 0.68839
43602.5121 | 1.0448 | 1.2332 | 1.1593 | 0.89936 | 0.78701 | 0.71138 | 0.69281 | 0.6885
43602.5121 | 1.0487 | 1.2334 | 1.1593 | 0.89984 | 0.7873 | 0.71196 | 0.6932 | 0.68878
43602.512 | 1.045 | 1.2331 | 1.1601 | 0.90021 | 0.78784 | 0.71166 | 0.69266 | 0.68862
43602.5122 | 1.0446 | 1.2315 | 1.1588 | 0.89925 | 0.78679 | 0.71117 | 0.69277 | 0.68823
43602.5122 | 1.0533 | 1.2364 | 1.161 | 0.90325 | 0.7896 | 0.7128 | 0.69398 | 0.68948
43602.5122 | 1.0416 | 1.2271 | 1.1562 | 0.89582 | 0.78716 | 0.71153 | 0.6919 | 0.68807
43602.5123 | 1.0445 | 1.2327 | 1.159 | 0.90111 | 0.78667 | 0.71077 | 0.69355 | 0.68861
43602.5122 | 1.0383 | 1.2297 | 1.1581 | 0.89897 | 0.78807 | 0.71165 | 0.69495 | 0.68842
43602.5124 | 1.0407 | 1.2315 | 1.1586 | 0.89946 | 0.78723 | 0.7117 | 0.69461 | 0.68842
43602.5124 | 1.0423 | 1.2335 | 1.1607 | 0.90192 | 0.78848 | 0.71251 | 0.69324 | 0.68901
43602.5124 | 1.0471 | 1.2345 | 1.1605 | 0.90233 | 0.78982 | 0.71342 | 0.69475 | 0.6893
43602.5124 | 1.0446 | 1.2319 | 1.1585 | 0.89956 | 0.78863 | 0.71256 | 0.69344 | 0.68892
43602.5124 | 1.0453 | 1.2312 | 1.158 | 0.89954 | 0.7874 | 0.71176 | 0.69359 | 0.68845
43602.5124 | 1.044 | 1.2322 | 1.1587 | 0.90114 | 0.78845 | 0.71227 | 0.69325 | 0.68901
43602.5126 | 1.0437 | 1.2311 | 1.1582 | 0.90008 | 0.7887 | 0.71204 | 0.69372 | 0.68915
43602.5126 | 1.041 | 1.2293 | 1.1568 | 0.89917 | 0.78716 | 0.71134 | 0.6927 | 0.68867
43602.5126 | 1.0435 | 1.228 | 1.1549 | 0.89748 | 0.78755 | 0.71096 | 0.69249 | 0.68861
43602.5126 | 1.0448 | 1.229 | 1.1554 | 0.89845 | 0.78634 | 0.71053 | 0.69126 | 0.68863
43602.5126 | 1.0434 | 1.2268 | 1.1538 | 0.89684 | 0.78715 | 0.71107 | 0.69574 | 0.68875
43602.5127 | 1.039 | 1.2261 | 1.1525 | 0.89691 | 0.7862 | 0.71031 | 0.69066 | 0.68844
43602.5127 | 1.0289 | 1.2224 | 1.151 | 0.89474 | 0.78491 | 0.70968 | 0.69471 | 0.68782
43602.5128 | 1.0387 | 1.2224 | 1.1496 | 0.8954 | 0.78428 | 0.7094 | 0.69166 | 0.68817
43602.5128 | 1.0299 | 1.2214 | 1.1496 | 0.89464 | 0.78395 | 0.70873 | 0.68975 | 0.6877
43602.5127 | 1.03 | 1.2187 | 1.1471 | 0.89205 | 0.78363 | 0.70851 | 0.69011 | 0.68815
43602.5129 | 1.0281 | 1.2178 | 1.1454 | 0.89209 | 0.78206 | 0.70722 | 0.68842 | 0.68777
43602.5129 | 1.0357 | 1.2193 | 1.1458 | 0.8932 | 0.78243 | 0.70768 | 0.69417 | 0.68781
43602.5129 | 1.0393 | 1.2223 | 1.1479 | 0.89586 | 0.78285 | 0.70777 | 0.68977 | 0.68759
43602.5129 | 1.0361 | 1.2198 | 1.1472 | 0.89429 | 0.78422 | 0.70818 | 0.68967 | 0.68746
43602.5129 | 1.0443 | 1.2238 | 1.1496 | 0.89766 | 0.78469 | 0.70859 | 0.69011 | 0.68751
43602.5129 | 1.0489 | 1.2353 | 1.1587 | 0.9046 | 0.79237 | 0.71441 | 0.69465 | 0.68944
43602.5131 | 1.0523 | 1.2331 | 1.1576 | 0.90322 | 0.79112 | 0.71318 | 0.6937 | 0.68896
43602.5131 | 1.055 | 1.2322 | 1.1571 | 0.90208 | 0.79066 | 0.71313 | 0.69636 | 0.68893
43602.5131 | 1.0517 | 1.2351 | 1.1608 | 0.90496 | 0.79341 | 0.71492 | 0.69576 | 0.68953
43602.5131 | 1.0518 | 1.2346 | 1.1592 | 0.90342 | 0.79027 | 0.71309 | 0.69348 | 0.68866
43602.5131 | 1.0528 | 1.2349 | 1.16 | 0.90414 | 0.79437 | 0.71613 | 0.69573 | 0.69009
43602.5132 | 1.0514 | 1.2386 | 1.1637 | 0.90524 | 0.79735 | 0.71883 | 0.70095 | 0.69143
43602.5133 | 1.0543 | 1.2389 | 1.1631 | 0.90571 | 0.79383 | 0.71657 | 0.69749 | 0.69031
43602.5133 | 1.0551 | 1.2387 | 1.1637 | 0.90659 | 0.79338 | 0.71606 | 0.69632 | 0.69004
43602.5133 | 1.0593 | 1.2445 | 1.167 | 0.9103 | 0.79517 | 0.71701 | 0.6996 | 0.69069
43602.5132 | 1.0498 | 1.2348 | 1.1597 | 0.90265 | 0.7945 | 0.71672 | 0.69716 | 0.69063
43602.5134 | 1.0385 | 1.2292 | 1.1558 | 0.90081 | 0.78938 | 0.71355 | 0.69425 | 0.69068
43602.5134 | 1.0461 | 1.2313 | 1.1555 | 0.90102 | 0.79029 | 0.71363 | 0.69528 | 0.69039
43602.5134 | 1.0359 | 1.2283 | 1.1553 | 0.89929 | 0.78996 | 0.71337 | 0.69374 | 0.69057
43602.5134 | 1.0391 | 1.2276 | 1.1528 | 0.89847 | 0.7874 | 0.71167 | 0.69291 | 0.68986
43602.5134 | 1.0363 | 1.2248 | 1.1517 | 0.89744 | 0.78717 | 0.71145 | 0.69273 | 0.69038
43602.5136 | 1.023 | 1.2142 | 1.1425 | 0.89089 | 0.78183 | 0.7076 | 0.69116 | 0.68953
43602.5136 | 1.0274 | 1.2161 | 1.1422 | 0.89345 | 0.78225 | 0.70791 | 0.6905 | 0.68942
43602.5136 | 1.0199 | 1.212 | 1.1403 | 0.88936 | 0.78256 | 0.70798 | 0.69054 | 0.68939
43602.5136 | 1.0199 | 1.2105 | 1.1389 | 0.88798 | 0.7798 | 0.7064 | 0.68833 | 0.68853
43602.5136 | 1.0229 | 1.2097 | 1.137 | 0.88781 | 0.77855 | 0.70604 | 0.69004 | 0.68906
43602.5136 | 1.0212 | 1.209 | 1.136 | 0.88768 | 0.77862 | 0.70525 | 0.6874 | 0.6883
43602.5138 | 1.0294 | 1.2125 | 1.1375 | 0.89227 | 0.78028 | 0.70682 | 0.68858 | 0.68862
43602.5138 | 1.0206 | 1.2121 | 1.1385 | 0.89191 | 0.78191 | 0.70743 | 0.69022 | 0.68869
43602.5138 | 1.028 | 1.211 | 1.1369 | 0.89091 | 0.78299 | 0.70808 | 0.68936 | 0.68918
43602.5138 | 1.0306 | 1.213 | 1.1373 | 0.89209 | 0.78019 | 0.70644 | 0.69074 | 0.68788
43602.5137 | 1.0337 | 1.2126 | 1.1378 | 0.89234 | 0.78347 | 0.70847 | 0.69012 | 0.68848
43602.5139 | 1.0408 | 1.2215 | 1.1449 | 0.89882 | 0.7873 | 0.71221 | 0.69268 | 0.68944
43602.5139 | 1.0486 | 1.2216 | 1.1446 | 0.89902 | 0.78753 | 0.71223 | 0.69741 | 0.68951
43602.5139 | 1.0471 | 1.2216 | 1.1449 | 0.8996 | 0.78802 | 0.71243 | 0.69439 | 0.68973
43602.5139 | 1.0595 | 1.2251 | 1.1469 | 0.90136 | 0.78831 | 0.71254 | 0.69412 | 0.69002
43602.5139 | 1.0439 | 1.2229 | 1.1462 | 0.89943 | 0.79148 | 0.71519 | 0.69602 | 0.69097
43602.5141 | 1.0305 | 1.217 | 1.1425 | 0.89681 | 0.78976 | 0.71477 | 0.69845 | 0.69131
43602.5141 | 1.0429 | 1.2206 | 1.1439 | 0.89968 | 0.78851 | 0.71357 | 0.6975 | 0.69157
43602.5141 | 1.0393 | 1.2157 | 1.1398 | 0.89564 | 0.78733 | 0.7122 | 0.69454 | 0.69061
43602.5141 | 1.0438 | 1.2184 | 1.1422 | 0.89885 | 0.78687 | 0.71217 | 0.69411 | 0.69108
43602.5141 | 1.0478 | 1.2208 | 1.1444 | 0.90151 | 0.79044 | 0.71455 | 0.69625 | 0.69258
43602.5141 | 1.0372 | 1.2163 | 1.1411 | 0.89713 | 0.78789 | 0.71317 | 0.69575 | 0.692
43602.5143 | 1.0319 | 1.2138 | 1.1391 | 0.89536 | 0.78652 | 0.71225 | 0.69296 | 0.69218
43602.5143 | 1.0289 | 1.2131 | 1.1383 | 0.89478 | 0.78536 | 0.71162 | 0.69368 | 0.6917
43602.5143 | 1.024 | 1.2114 | 1.1378 | 0.89316 | 0.78447 | 0.71104 | 0.69749 | 0.69186
43602.5143 | 1.0291 | 1.2116 | 1.1377 | 0.89428 | 0.78479 | 0.71094 | 0.69385 | 0.69185
43602.5143 | 1.0256 | 1.2098 | 1.1355 | 0.89236 | 0.78285 | 0.70968 | 0.69237 | 0.6915
43602.5144 | 1.0118 | 1.1987 | 1.127 | 0.88356 | 0.77631 | 0.70488 | 0.6871 | 0.69054
43602.5144 | 1.0094 | 1.1983 | 1.1269 | 0.88389 | 0.77633 | 0.70493 | 0.68906 | 0.6905
43602.5144 | 1.0025 | 1.1966 | 1.1272 | 0.88339 | 0.77675 | 0.70466 | 0.68998 | 0.69016
43602.5145 | 1.0032 | 1.1954 | 1.1253 | 0.88214 | 0.7758 | 0.70449 | 0.68767 | 0.69017
43602.5145 | 1.0022 | 1.1961 | 1.1261 | 0.88248 | 0.77524 | 0.70416 | 0.6874 | 0.69026
43602.5144 | 1.0111 | 1.2002 | 1.1285 | 0.88372 | 0.77623 | 0.70468 | 0.68783 | 0.68967
43602.5146 | 1.0158 | 1.209 | 1.1359 | 0.89003 | 0.78022 | 0.70716 | 0.69008 | 0.68978
43602.5146 | 1.0202 | 1.2108 | 1.1382 | 0.89144 | 0.78068 | 0.70748 | 0.68952 | 0.68995
43602.5146 | 1.0237 | 1.2139 | 1.1401 | 0.89287 | 0.78288 | 0.70894 | 0.69306 | 0.69042
43602.5146 | 1.022 | 1.2106 | 1.1388 | 0.88895 | 0.78096 | 0.70803 | 0.69207 | 0.68964
43602.5146 | 1.0188 | 1.2154 | 1.1424 | 0.89333 | 0.78188 | 0.70883 | 0.69166 | 0.69013
43602.5148 | 1.0316 | 1.2216 | 1.1483 | 0.89468 | 0.78393 | 0.70994 | 0.69355 | 0.69008
43602.5148 | 1.0286 | 1.2208 | 1.1491 | 0.89484 | 0.78548 | 0.71118 | 0.69335 | 0.69066
43602.5148 | 1.0263 | 1.2222 | 1.1508 | 0.89536 | 0.78524 | 0.71098 | 0.69178 | 0.69069
43602.5148 | 1.0331 | 1.2256 | 1.153 | 0.89787 | 0.78723 | 0.71294 | 0.69378 | 0.6916
43602.5148 | 1.0303 | 1.2233 | 1.1529 | 0.89602 | 0.78654 | 0.71193 | 0.6926 | 0.69069
43602.5148 | 1.0342 | 1.2293 | 1.1624 | 0.89876 | 0.79087 | 0.7152 | 0.69595 | 0.69152
43602.515 | 1.0272 | 1.225 | 1.1588 | 0.89471 | 0.7869 | 0.71359 | 0.69515 | 0.69215
43602.515 | 1.0278 | 1.2238 | 1.1586 | 0.89452 | 0.78668 | 0.71302 | 0.69449 | 0.69196
43602.515 | 1.0243 | 1.2238 | 1.159 | 0.89488 | 0.78622 | 0.713 | 0.69319 | 0.6921
43602.515 | 1.0206 | 1.2211 | 1.1574 | 0.8933 | 0.78572 | 0.71296 | 0.69801 | 0.69233
43602.515 | 1.018 | 1.214 | 1.1526 | 0.8876 | 0.78212 | 0.71059 | 0.69325 | 0.69163
43602.5151 | 0.99948 | 1.1973 | 1.1408 | 0.8782 | 0.77448 | 0.70513 | 0.68708 | 0.69092
43602.5151 | 1.0016 | 1.1972 | 1.1389 | 0.87714 | 0.77338 | 0.70392 | 0.68725 | 0.69021
43602.5151 | 0.99954 | 1.194 | 1.1374 | 0.87574 | 0.77243 | 0.70302 | 0.68967 | 0.68956
43602.5152 | 0.99361 | 1.1931 | 1.1374 | 0.87505 | 0.77125 | 0.7021 | 0.68502 | 0.68931
43602.5151 | 0.99408 | 1.1914 | 1.1364 | 0.87376 | 0.77059 | 0.70174 | 0.68516 | 0.6892
43602.5153 | 1.0018 | 1.1959 | 1.1398 | 0.87466 | 0.77009 | 0.70014 | 0.68412 | 0.6875
43602.5153 | 0.99186 | 1.1949 | 1.1405 | 0.87474 | 0.76959 | 0.69984 | 0.68536 | 0.68712
43602.5153 | 0.99621 | 1.1979 | 1.1425 | 0.87564 | 0.77006 | 0.69973 | 0.68214 | 0.68704
43602.5153 | 1.0074 | 1.2024 | 1.1449 | 0.87679 | 0.76988 | 0.69952 | 0.68161 | 0.68673
43602.5153 | 1.0059 | 1.2089 | 1.1507 | 0.88154 | 0.77295 | 0.70123 | 0.683 | 0.68652
43602.5155 | 1.0198 | 1.223 | 1.1612 | 0.88835 | 0.77888 | 0.70531 | 0.68622 | 0.68687
43602.5155 | 1.0195 | 1.2241 | 1.1619 | 0.88968 | 0.77967 | 0.70627 | 0.68656 | 0.68739
43602.5155 | 1.0272 | 1.2274 | 1.163 | 0.89071 | 0.78015 | 0.70667 | 0.68811 | 0.68746
43602.5155 | 1.0325 | 1.2312 | 1.1644 | 0.89321 | 0.78167 | 0.70735 | 0.68805 | 0.68746
43602.5154 | 1.0334 | 1.2333 | 1.1664 | 0.8949 | 0.78364 | 0.70931 | 0.68921 | 0.68783
43602.5156 | 1.0519 | 1.2475 | 1.1749 | 0.90573 | 0.79073 | 0.7141 | 0.69398 | 0.68897
43602.5156 | 1.0555 | 1.2496 | 1.1763 | 0.90832 | 0.79329 | 0.71573 | 0.6948 | 0.68962
43602.5156 | 1.0486 | 1.2486 | 1.1768 | 0.90724 | 0.79383 | 0.71619 | 0.69532 | 0.68983
43602.5156 | 1.0538 | 1.2458 | 1.1747 | 0.9053 | 0.79179 | 0.71577 | 0.69683 | 0.6894
43602.5156 | 1.054 | 1.2491 | 1.1773 | 0.90815 | 0.79387 | 0.71702 | 0.69624 | 0.69002
43602.5158 | 1.0569 | 1.2511 | 1.1781 | 0.90997 | 0.7971 | 0.71926 | 0.69822 | 0.69121
43602.5158 | 1.0583 | 1.2486 | 1.1763 | 0.9089 | 0.79588 | 0.71848 | 0.70264 | 0.69097
43602.5158 | 1.0599 | 1.2495 | 1.1761 | 0.91033 | 0.79536 | 0.71815 | 0.69887 | 0.69081
43602.5158 | 1.059 | 1.2493 | 1.1762 | 0.90974 | 0.79709 | 0.71933 | 0.69947 | 0.69153
43602.5158 | 1.0527 | 1.245 | 1.173 | 0.90787 | 0.79329 | 0.71698 | 0.69813 | 0.69053
43602.5159 | 1.0345 | 1.2313 | 1.1629 | 0.89929 | 0.78752 | 0.71356 | 0.69477 | 0.69051
43602.516 | 1.0343 | 1.229 | 1.1615 | 0.89708 | 0.78775 | 0.71318 | 0.69381 | 0.69069
43602.516 | 1.0351 | 1.2257 | 1.1588 | 0.89478 | 0.78557 | 0.71208 | 0.69413 | 0.69011
43602.516 | 1.0329 | 1.2263 | 1.1585 | 0.89595 | 0.78551 | 0.71204 | 0.69423 | 0.69059
43602.5159 | 1.0253 | 1.22 | 1.1543 | 0.89137 | 0.78304 | 0.71017 | 0.69209 | 0.69014
43602.5161 | 1.0024 | 1.2024 | 1.142 | 0.88221 | 0.77614 | 0.70514 | 0.68732 | 0.68918
43602.5161 | 1.0066 | 1.2042 | 1.1416 | 0.88225 | 0.77626 | 0.70516 | 0.68749 | 0.68945
43602.5161 | 1.0079 | 1.2039 | 1.1402 | 0.88287 | 0.77582 | 0.70426 | 0.68744 | 0.68909
43602.5161 | 1.0084 | 1.2014 | 1.1379 | 0.87889 | 0.77419 | 0.7033 | 0.69089 | 0.6881
43602.5161 | 1.0067 | 1.1998 | 1.1359 | 0.87923 | 0.77321 | 0.70224 | 0.68462 | 0.68794
43602.5163 | 1.0111 | 1.2094 | 1.1415 | 0.88679 | 0.77495 | 0.70222 | 0.68537 | 0.68672
43602.5163 | 1.0172 | 1.2108 | 1.1427 | 0.88612 | 0.77702 | 0.70395 | 0.68588 | 0.6871
43602.5163 | 1.014 | 1.2133 | 1.1444 | 0.88784 | 0.77752 | 0.70398 | 0.68603 | 0.68702
43602.5163 | 1.0169 | 1.2136 | 1.145 | 0.88799 | 0.778 | 0.70433 | 0.68634 | 0.68666
43602.5163 | 1.031 | 1.224 | 1.1525 | 0.8948 | 0.78172 | 0.70713 | 0.68827 | 0.68715
43602.5164 | 1.0522 | 1.2355 | 1.1614 | 0.90454 | 0.79106 | 0.71379 | 0.6946 | 0.6882
43602.5164 | 1.0577 | 1.2399 | 1.1642 | 0.90709 | 0.79173 | 0.71382 | 0.69463 | 0.68817
43602.5165 | 1.0545 | 1.2391 | 1.1647 | 0.90728 | 0.79451 | 0.71573 | 0.69636 | 0.68879
43602.5165 | 1.0561 | 1.2394 | 1.1645 | 0.9066 | 0.7927 | 0.71482 | 0.69706 | 0.68846
43602.5164 | 1.0564 | 1.2426 | 1.1664 | 0.90975 | 0.79443 | 0.71633 | 0.6969 | 0.68904
43602.5166 | 1.0608 | 1.2414 | 1.1642 | 0.90891 | 0.7953 | 0.71717 | 0.69794 | 0.69015
43602.5166 | 1.0714 | 1.2447 | 1.1675 | 0.91207 | 0.79662 | 0.71797 | 0.69964 | 0.69033
43602.5166 | 1.0726 | 1.2476 | 1.1694 | 0.91381 | 0.79964 | 0.71971 | 0.70021 | 0.69037
43602.5166 | 1.0575 | 1.2379 | 1.1641 | 0.90749 | 0.79705 | 0.71828 | 0.69866 | 0.68997
43602.5166 | 1.0537 | 1.2394 | 1.164 | 0.90836 | 0.7951 | 0.71743 | 0.69761 | 0.69052
43602.5168 | 1.0597 | 1.2376 | 1.1604 | 0.9077 | 0.79408 | 0.71599 | 0.69727 | 0.6898
43602.5168 | 1.0525 | 1.2315 | 1.1552 | 0.9029 | 0.79195 | 0.71469 | 0.69556 | 0.68909
43602.5168 | 1.0601 | 1.237 | 1.159 | 0.90696 | 0.79173 | 0.71466 | 0.69554 | 0.68954
43602.5168 | 1.0566 | 1.2349 | 1.1577 | 0.90613 | 0.79548 | 0.71711 | 0.69771 | 0.69037
43602.5168 | 1.061 | 1.2366 | 1.1586 | 0.90804 | 0.79195 | 0.71445 | 0.69507 | 0.68945
43602.5169 | 1.0589 | 1.2268 | 1.1496 | 0.90267 | 0.7901 | 0.71331 | 0.69442 | 0.68911
43602.5169 | 1.0598 | 1.2307 | 1.1525 | 0.90508 | 0.79213 | 0.71493 | 0.69644 | 0.68986
43602.5169 | 1.0666 | 1.2288 | 1.151 | 0.90383 | 0.79126 | 0.71435 | 0.695 | 0.68912
43602.517 | 1.0507 | 1.2238 | 1.1477 | 0.90013 | 0.79012 | 0.71315 | 0.69366 | 0.68858
43602.5169 | 1.0499 | 1.2287 | 1.1498 | 0.90327 | 0.79001 | 0.71354 | 0.69661 | 0.68912
43602.5171 | 1.0607 | 1.2211 | 1.1421 | 0.89912 | 0.78852 | 0.71178 | 0.69305 | 0.68812
43602.5171 | 1.0627 | 1.2276 | 1.1467 | 0.90451 | 0.78963 | 0.7131 | 0.69378 | 0.68895
43602.5171 | 1.044 | 1.2213 | 1.1433 | 0.90099 | 0.7907 | 0.7135 | 0.69771 | 0.68915
43602.5171 | 1.0625 | 1.2238 | 1.1428 | 0.90188 | 0.78834 | 0.71169 | 0.69359 | 0.68849
43602.5171 | 1.0623 | 1.2242 | 1.1429 | 0.90175 | 0.78983 | 0.71263 | 0.69572 | 0.68857
43602.5173 | 1.0801 | 1.2292 | 1.1467 | 0.90631 | 0.79585 | 0.71697 | 0.69784 | 0.68975
43602.5173 | 1.0761 | 1.2271 | 1.1456 | 0.90478 | 0.79094 | 0.71322 | 0.6948 | 0.68787
43602.5173 | 1.0768 | 1.2326 | 1.1499 | 0.90943 | 0.79317 | 0.71501 | 0.69848 | 0.68891
43602.5173 | 1.082 | 1.227 | 1.1455 | 0.90484 | 0.7951 | 0.71635 | 0.69736 | 0.68915
43602.5172 | 1.0879 | 1.2325 | 1.1487 | 0.90899 | 0.79322 | 0.71504 | 0.69651 | 0.68882
43602.5174 | 1.0865 | 1.237 | 1.1513 | 0.91095 | 0.79798 | 0.71911 | 0.69902 | 0.69037
43602.5174 | 1.0946 | 1.2371 | 1.1514 | 0.9106 | 0.79692 | 0.71874 | 0.69896 | 0.69053
43602.5174 | 1.0869 | 1.235 | 1.1505 | 0.91048 | 0.79938 | 0.72041 | 0.70157 | 0.6909
43602.5175 | 1.0808 | 1.2319 | 1.1481 | 0.90749 | 0.79492 | 0.71714 | 0.69749 | 0.68986
43602.5174 | 1.0854 | 1.2297 | 1.1464 | 0.90668 | 0.79427 | 0.71687 | 0.6977 | 0.69007
43602.5176 | 1.0678 | 1.2218 | 1.1406 | 0.90308 | 0.79014 | 0.71387 | 0.69512 | 0.68988
43602.5176 | 1.0571 | 1.2165 | 1.1366 | 0.899 | 0.78766 | 0.71192 | 0.69667 | 0.68939
43602.5176 | 1.0611 | 1.2157 | 1.1357 | 0.89945 | 0.78749 | 0.71205 | 0.69406 | 0.68975
43602.5176 | 1.067 | 1.2157 | 1.1341 | 0.89891 | 0.78625 | 0.71071 | 0.69274 | 0.6893
43602.5176 | 1.051 | 1.2089 | 1.1299 | 0.8956 | 0.7854 | 0.70988 | 0.69147 | 0.68896
43602.5177 | 1.029 | 1.1923 | 1.1155 | 0.88557 | 0.77466 | 0.70135 | 0.68449 | 0.68633
43602.5178 | 1.0285 | 1.1889 | 1.1132 | 0.88408 | 0.77537 | 0.70187 | 0.68699 | 0.6866
43602.5178 | 1.0213 | 1.1862 | 1.1112 | 0.88241 | 0.77337 | 0.70055 | 0.6857 | 0.68602
43602.5178 | 1.0272 | 1.1851 | 1.1091 | 0.88153 | 0.77377 | 0.70053 | 0.68423 | 0.68616
43602.5177 | 1.033 | 1.1859 | 1.1072 | 0.88107 | 0.77117 | 0.69856 | 0.6823 | 0.68538
43602.5179 | 1.0023 | 1.1747 | 1.0994 | 0.87565 | 0.76949 | 0.69673 | 0.68095 | 0.68417
43602.5179 | 1.029 | 1.1801 | 1.1022 | 0.8783 | 0.77047 | 0.69773 | 0.68116 | 0.68405
43602.5179 | 1.0352 | 1.1833 | 1.1034 | 0.87995 | 0.76927 | 0.69718 | 0.68271 | 0.68391
43602.5179 | 1.0434 | 1.1858 | 1.105 | 0.88124 | 0.77197 | 0.69861 | 0.68179 | 0.68426
43602.5179 | 1.0628 | 1.195 | 1.111 | 0.88595 | 0.77447 | 0.70074 | 0.68273 | 0.68454
43602.5181 | 1.0677 | 1.2212 | 1.1348 | 0.90369 | 0.78812 | 0.71152 | 0.69276 | 0.68702
43602.5181 | 1.1039 | 1.2352 | 1.141 | 0.90956 | 0.7933 | 0.71522 | 0.69567 | 0.68837
43602.5181 | 1.0952 | 1.2216 | 1.1319 | 0.90123 | 0.79055 | 0.71308 | 0.69388 | 0.68776
43602.5181 | 1.094 | 1.2276 | 1.1383 | 0.90626 | 0.79195 | 0.7142 | 0.69677 | 0.68822
43602.5181 | 1.086 | 1.2224 | 1.1351 | 0.9027 | 0.79218 | 0.71463 | 0.69481 | 0.68836
43602.5182 | 1.052 | 1.2093 | 1.1299 | 0.89645 | 0.78434 | 0.70906 | 0.69022 | 0.68761
43602.5183 | 1.0758 | 1.2166 | 1.1327 | 0.89975 | 0.7856 | 0.70999 | 0.69283 | 0.68873
43602.5183 | 1.0501 | 1.2063 | 1.1272 | 0.89401 | 0.78587 | 0.71003 | 0.69454 | 0.68828
43602.5183 | 1.0531 | 1.2067 | 1.1261 | 0.89338 | 0.78186 | 0.70713 | 0.68885 | 0.68734
43602.5182 | 1.0219 | 1.1897 | 1.1147 | 0.88272 | 0.7781 | 0.70415 | 0.68653 | 0.68729
43602.5184 | 1.0008 | 1.1702 | 1.0984 | 0.87156 | 0.76261 | 0.69271 | 0.67636 | 0.68437
43602.5184 | 0.99762 | 1.1697 | 1.0983 | 0.8714 | 0.76495 | 0.69448 | 0.6785 | 0.68565
43602.5184 | 0.99532 | 1.1681 | 1.0963 | 0.86969 | 0.76187 | 0.69214 | 0.67711 | 0.68464
43602.5184 | 0.98907 | 1.1625 | 1.092 | 0.86621 | 0.75967 | 0.69029 | 0.67943 | 0.68392
43602.5184 | 0.99164 | 1.1616 | 1.0904 | 0.86574 | 0.75761 | 0.68875 | 0.67503 | 0.68349
43602.5186 | 0.98623 | 1.1571 | 1.0863 | 0.86322 | 0.75499 | 0.68655 | 0.67449 | 0.68225
43602.5186 | 0.98358 | 1.1576 | 1.0868 | 0.8634 | 0.755 | 0.68636 | 0.67089 | 0.68169
43602.5186 | 0.9855 | 1.1577 | 1.0868 | 0.86243 | 0.75631 | 0.68733 | 0.67177 | 0.68235
43602.5186 | 0.98245 | 1.1582 | 1.0882 | 0.86397 | 0.75484 | 0.68642 | 0.67144 | 0.6817
43602.5186 | 0.99557 | 1.1644 | 1.0927 | 0.86823 | 0.75857 | 0.68864 | 0.67432 | 0.68233
43602.5187 | 1.0163 | 1.1767 | 1.102 | 0.87518 | 0.76324 | 0.69196 | 0.67858 | 0.68256
43602.5188 | 1.0108 | 1.181 | 1.1049 | 0.87745 | 0.76617 | 0.69423 | 0.67799 | 0.68346
43602.5188 | 1.0147 | 1.1792 | 1.1038 | 0.87555 | 0.76396 | 0.69275 | 0.67642 | 0.68256
43602.5188 | 1.0116 | 1.1827 | 1.1067 | 0.87807 | 0.76855 | 0.69517 | 0.67895 | 0.6838
43602.5187 | 0.99758 | 1.1754 | 1.1031 | 0.87385 | 0.76477 | 0.69341 | 0.67746 | 0.68356
43602.5189 | 0.97917 | 1.1625 | 1.0933 | 0.86552 | 0.75933 | 0.69006 | 0.67457 | 0.68288
43602.5189 | 0.99256 | 1.1701 | 1.0976 | 0.87269 | 0.7614 | 0.69123 | 0.67622 | 0.68428
43602.5189 | 0.98314 | 1.1597 | 1.0891 | 0.86282 | 0.75791 | 0.68927 | 0.67367 | 0.6827
43602.5189 | 0.98571 | 1.1604 | 1.0895 | 0.86517 | 0.75675 | 0.6883 | 0.6736 | 0.683
43602.5189 | 0.97633 | 1.154 | 1.0832 | 0.85892 | 0.75351 | 0.68603 | 0.67174 | 0.68267
43602.5191 | 0.95479 | 1.1369 | 1.0714 | 0.84932 | 0.74683 | 0.681 | 0.67036 | 0.68179
43602.5191 | 0.95234 | 1.1353 | 1.0704 | 0.84782 | 0.74489 | 0.67987 | 0.66605 | 0.6812
43602.5191 | 0.9559 | 1.1377 | 1.0699 | 0.84976 | 0.74324 | 0.67857 | 0.66429 | 0.68048
43602.5191 | 0.95268 | 1.1379 | 1.0711 | 0.84983 | 0.74552 | 0.68015 | 0.66667 | 0.68144
43602.5191 | 0.96678 | 1.1417 | 1.0723 | 0.85335 | 0.74566 | 0.68005 | 0.66572 | 0.68091
43602.5192 | 0.96471 | 1.1472 | 1.08 | 0.85769 | 0.75109 | 0.6831 | 0.66829 | 0.68092
43602.5193 | 0.97798 | 1.1502 | 1.0802 | 0.86017 | 0.75091 | 0.68346 | 0.67294 | 0.68124
43602.5193 | 0.97138 | 1.1507 | 1.0821 | 0.86075 | 0.75316 | 0.68473 | 0.67045 | 0.68173
43602.5193 | 0.97484 | 1.1514 | 1.082 | 0.86068 | 0.75332 | 0.68519 | 0.67039 | 0.68173
43602.5192 | 0.99459 | 1.1635 | 1.0902 | 0.86937 | 0.75691 | 0.68813 | 0.67337 | 0.68272
43602.5194 | 0.97515 | 1.1533 | 1.0836 | 0.8623 | 0.75468 | 0.68727 | 0.67379 | 0.6828
43602.5194 | 0.97962 | 1.1532 | 1.0835 | 0.86269 | 0.75523 | 0.68727 | 0.67232 | 0.68306
43602.5194 | 0.97443 | 1.1509 | 1.0813 | 0.86082 | 0.75571 | 0.6876 | 0.67272 | 0.68322
43602.5194 | 0.97252 | 1.1487 | 1.0809 | 0.85987 | 0.75231 | 0.68533 | 0.67085 | 0.68218
43602.5194 | 0.96551 | 1.1453 | 1.0771 | 0.85695 | 0.75245 | 0.68574 | 0.67377 | 0.68301
43602.5196 | 0.95364 | 1.1383 | 1.071 | 0.85322 | 0.74795 | 0.68267 | 0.6697 | 0.68276
43602.5196 | 0.95144 | 1.1349 | 1.0689 | 0.84947 | 0.74595 | 0.68136 | 0.66738 | 0.68237
43602.5196 | 0.95505 | 1.1382 | 1.0706 | 0.8537 | 0.74585 | 0.68137 | 0.66833 | 0.68263
43602.5196 | 0.95266 | 1.1359 | 1.0702 | 0.85057 | 0.7475 | 0.68225 | 0.66821 | 0.68306
43602.5196 | 0.94936 | 1.1317 | 1.0654 | 0.84824 | 0.74373 | 0.67974 | 0.66666 | 0.68258
43602.5197 | 0.95283 | 1.1342 | 1.0669 | 0.85051 | 0.74551 | 0.68065 | 0.66748 | 0.68301
43602.5198 | 0.95339 | 1.1336 | 1.067 | 0.84939 | 0.74502 | 0.68007 | 0.66675 | 0.68254
43602.5198 | 0.94787 | 1.135 | 1.0693 | 0.85193 | 0.74564 | 0.68081 | 0.6671 | 0.68265
43602.5198 | 0.95261 | 1.1362 | 1.0692 | 0.85198 | 0.74737 | 0.68184 | 0.66812 | 0.68288
43602.5197 | 0.95751 | 1.1373 | 1.0692 | 0.8528 | 0.7473 | 0.68217 | 0.66844 | 0.68249
43602.5199 | 0.95817 | 1.1418 | 1.0744 | 0.85496 | 0.74888 | 0.68351 | 0.66963 | 0.68307
43602.5199 | 0.96614 | 1.1472 | 1.0772 | 0.8591 | 0.75219 | 0.68545 | 0.67599 | 0.68415
43602.5199 | 0.95847 | 1.1433 | 1.0762 | 0.85628 | 0.75146 | 0.68493 | 0.67106 | 0.68332
43602.5199 | 0.96244 | 1.144 | 1.0752 | 0.85624 | 0.74974 | 0.68409 | 0.66994 | 0.68302
43602.5199 | 0.95978 | 1.1421 | 1.0738 | 0.85521 | 0.74956 | 0.68408 | 0.67019 | 0.6835
43602.5201 | 0.94206 | 1.1269 | 1.0642 | 0.84658 | 0.74341 | 0.68032 | 0.66812 | 0.68296
43602.5201 | 0.94741 | 1.1279 | 1.0633 | 0.84678 | 0.74427 | 0.68058 | 0.66784 | 0.68352
43602.5201 | 0.94271 | 1.1251 | 1.0608 | 0.84554 | 0.74275 | 0.67962 | 0.66718 | 0.68301
43602.5201 | 0.94049 | 1.1234 | 1.0605 | 0.845 | 0.74263 | 0.67939 | 0.66638 | 0.68315
43602.5201 | 0.93387 | 1.1193 | 1.0573 | 0.84279 | 0.74052 | 0.6781 | 0.66478 | 0.68309
43602.5202 | 0.92417 | 1.1097 | 1.0504 | 0.83752 | 0.73689 | 0.67477 | 0.66186 | 0.68222
43602.5203 | 0.92542 | 1.1116 | 1.0502 | 0.83995 | 0.73667 | 0.67453 | 0.66282 | 0.68223
43602.5203 | 0.92256 | 1.1115 | 1.0503 | 0.83922 | 0.73786 | 0.67524 | 0.66179 | 0.68241
43602.5203 | 0.92555 | 1.1079 | 1.0475 | 0.83571 | 0.73607 | 0.67402 | 0.66456 | 0.68178
43602.5202 | 0.92444 | 1.1097 | 1.0478 | 0.83779 | 0.73475 | 0.67311 | 0.66128 | 0.68115
43602.5204 | 0.93498 | 1.1072 | 1.0427 | 0.83589 | 0.73614 | 0.67306 | 0.66038 | 0.68073
43602.5204 | 0.93114 | 1.1088 | 1.0432 | 0.83717 | 0.73472 | 0.67225 | 0.66046 | 0.68046
43602.5204 | 0.93196 | 1.1104 | 1.0441 | 0.83896 | 0.73563 | 0.67277 | 0.66356 | 0.68068
43602.5204 | 0.92688 | 1.1081 | 1.0443 | 0.83856 | 0.73644 | 0.67355 | 0.66174 | 0.68093
43602.5204 | 0.94158 | 1.1117 | 1.0443 | 0.8411 | 0.7385 | 0.67504 | 0.66354 | 0.68088
43602.5206 | 0.95073 | 1.1149 | 1.047 | 0.84282 | 0.74221 | 0.67785 | 0.66529 | 0.68162
43602.5206 | 0.9623 | 1.1219 | 1.0512 | 0.84833 | 0.74367 | 0.67849 | 0.66537 | 0.68202
43602.5206 | 0.95986 | 1.1215 | 1.0501 | 0.84689 | 0.74244 | 0.67778 | 0.66842 | 0.68145
43602.5206 | 0.97324 | 1.1263 | 1.0538 | 0.85083 | 0.74603 | 0.68063 | 0.66856 | 0.68303
43602.5206 | 0.96454 | 1.1262 | 1.0544 | 0.85097 | 0.74593 | 0.68081 | 0.66911 | 0.68254
43602.5208 | 0.93761 | 1.1119 | 1.0455 | 0.84283 | 0.74041 | 0.67722 | 0.66467 | 0.6821
43602.5208 | 0.95874 | 1.1196 | 1.0497 | 0.84782 | 0.74289 | 0.67883 | 0.66936 | 0.68339
43602.5208 | 0.95526 | 1.1177 | 1.0478 | 0.84665 | 0.74466 | 0.67992 | 0.66777 | 0.68323
43602.5208 | 0.94731 | 1.1115 | 1.0429 | 0.84187 | 0.74115 | 0.67772 | 0.66575 | 0.6825
43602.5207 | 0.94625 | 1.1131 | 1.0443 | 0.84289 | 0.74221 | 0.67818 | 0.66621 | 0.6831
43602.5209 | 0.94842 | 1.1177 | 1.0478 | 0.84598 | 0.7417 | 0.67844 | 0.66961 | 0.68328
43602.5209 | 0.94504 | 1.1149 | 1.0471 | 0.84435 | 0.74364 | 0.67981 | 0.66865 | 0.68405
43602.521 | 0.955 | 1.1192 | 1.0491 | 0.8473 | 0.74218 | 0.67882 | 0.66738 | 0.68357
43602.521 | 0.9451 | 1.1153 | 1.047 | 0.84376 | 0.74176 | 0.67845 | 0.66655 | 0.68332
43602.5209 | 0.94393 | 1.1147 | 1.0465 | 0.84311 | 0.7425 | 0.67891 | 0.66692 | 0.68386
43602.5211 | 0.94898 | 1.1175 | 1.0485 | 0.8454 | 0.74168 | 0.67865 | 0.6656 | 0.68383
43602.5211 | 0.94758 | 1.1198 | 1.0515 | 0.84746 | 0.74371 | 0.67939 | 0.66546 | 0.68394
43602.5211 | 0.93805 | 1.111 | 1.0458 | 0.84059 | 0.741 | 0.67788 | 0.66491 | 0.68291
43602.5211 | 0.93576 | 1.1153 | 1.0493 | 0.84488 | 0.73923 | 0.67676 | 0.66416 | 0.68283
43602.5211 | 0.94715 | 1.1191 | 1.051 | 0.84653 | 0.74421 | 0.68014 | 0.66874 | 0.6847
43602.5213 | 0.93959 | 1.1152 | 1.0483 | 0.84308 | 0.74126 | 0.6785 | 0.66526 | 0.68442
43602.5213 | 0.94113 | 1.1139 | 1.0467 | 0.84254 | 0.74115 | 0.67868 | 0.66658 | 0.68446
43602.5213 | 0.92905 | 1.1095 | 1.0465 | 0.83963 | 0.7392 | 0.67744 | 0.66439 | 0.68409
43602.5213 | 0.94257 | 1.1156 | 1.0479 | 0.84434 | 0.74008 | 0.67816 | 0.66478 | 0.68478
43602.5213 | 0.93175 | 1.1087 | 1.045 | 0.83869 | 0.74034 | 0.67814 | 0.66823 | 0.68477
43602.5214 | 0.91893 | 1.1023 | 1.0402 | 0.83731 | 0.7356 | 0.67539 | 0.66304 | 0.68423
43602.5214 | 0.91582 | 1.0982 | 1.0394 | 0.83363 | 0.73564 | 0.67511 | 0.66327 | 0.68429
43602.5215 | 0.91461 | 1.0974 | 1.0383 | 0.8327 | 0.7335 | 0.67408 | 0.66177 | 0.68407
43602.5215 | 0.92267 | 1.0996 | 1.0375 | 0.8347 | 0.73391 | 0.67409 | 0.6648 | 0.68436
43602.5214 | 0.91876 | 1.0961 | 1.0353 | 0.83227 | 0.7335 | 0.67346 | 0.66246 | 0.68416
43602.5216 | 0.91178 | 1.0899 | 1.0317 | 0.82921 | 0.73158 | 0.67248 | 0.65971 | 0.68381
43602.5216 | 0.91434 | 1.0927 | 1.0318 | 0.83115 | 0.73112 | 0.67176 | 0.662 | 0.68375
43602.5216 | 0.90198 | 1.0906 | 1.0314 | 0.83114 | 0.73147 | 0.67175 | 0.66088 | 0.68364
43602.5216 | 0.90899 | 1.0897 | 1.0301 | 0.82993 | 0.73103 | 0.67183 | 0.65977 | 0.68367
43602.5216 | 0.90749 | 1.0879 | 1.027 | 0.82921 | 0.72968 | 0.67002 | 0.65795 | 0.68329
43602.5218 | 0.9012 | 1.0831 | 1.0235 | 0.82685 | 0.72796 | 0.66862 | 0.6582 | 0.68262
43602.5218 | 0.90953 | 1.0836 | 1.0217 | 0.82609 | 0.72704 | 0.66782 | 0.65789 | 0.68227
43602.5218 | 0.90254 | 1.0839 | 1.0233 | 0.82703 | 0.72776 | 0.66811 | 0.65738 | 0.68233
43602.5218 | 0.89806 | 1.0807 | 1.0226 | 0.82577 | 0.72665 | 0.66793 | 0.65658 | 0.6822
43602.5218 | 0.9048 | 1.0838 | 1.0228 | 0.82686 | 0.72756 | 0.66848 | 0.6576 | 0.68237
43602.5219 | 0.92308 | 1.0956 | 1.029 | 0.83368 | 0.73234 | 0.67195 | 0.66362 | 0.6832
43602.522 | 0.92839 | 1.0985 | 1.03 | 0.83564 | 0.73427 | 0.673 | 0.66215 | 0.68375
43602.522 | 0.91607 | 1.0933 | 1.0293 | 0.83253 | 0.73341 | 0.67246 | 0.66151 | 0.68301
43602.522 | 0.92301 | 1.0936 | 1.0287 | 0.8323 | 0.73204 | 0.67217 | 0.66119 | 0.68325
43602.5219 | 0.92356 | 1.0965 | 1.0296 | 0.83448 | 0.7332 | 0.67253 | 0.66115 | 0.68317
43602.5221 | 0.92404 | 1.0952 | 1.0283 | 0.83399 | 0.73306 | 0.67288 | 0.66219 | 0.68339
43602.5221 | 0.92315 | 1.094 | 1.0279 | 0.83295 | 0.73335 | 0.67317 | 0.66194 | 0.68322
43602.5221 | 0.92688 | 1.095 | 1.0271 | 0.83364 | 0.73307 | 0.67324 | 0.6615 | 0.68341
43602.5221 | 0.9226 | 1.091 | 1.0255 | 0.83093 | 0.73211 | 0.67227 | 0.6627 | 0.68299
43602.5221 | 0.9267 | 1.0926 | 1.0257 | 0.83274 | 0.73237 | 0.67267 | 0.66155 | 0.68337
43602.5223 | 0.92077 | 1.0886 | 1.0226 | 0.8311 | 0.73215 | 0.67237 | 0.665 | 0.68339
43602.5223 | 0.91182 | 1.0872 | 1.0234 | 0.82998 | 0.73077 | 0.67123 | 0.66074 | 0.68306
43602.5223 | 0.92004 | 1.0894 | 1.0237 | 0.83125 | 0.7326 | 0.67278 | 0.66115 | 0.68381
43602.5223 | 0.91934 | 1.0869 | 1.0219 | 0.82899 | 0.73157 | 0.67153 | 0.66064 | 0.68321
43602.5223 | 0.92375 | 1.0893 | 1.0213 | 0.83106 | 0.73138 | 0.67138 | 0.66073 | 0.68343
43602.5224 | 0.91004 | 1.0811 | 1.0171 | 0.82731 | 0.72833 | 0.66883 | 0.66069 | 0.68232
43602.5225 | 0.92027 | 1.0852 | 1.0187 | 0.82941 | 0.73054 | 0.67074 | 0.65981 | 0.68322
43602.5225 | 0.91816 | 1.0822 | 1.0161 | 0.82668 | 0.72983 | 0.67002 | 0.65862 | 0.68273
43602.5225 | 0.90851 | 1.0793 | 1.0152 | 0.82587 | 0.72882 | 0.66943 | 0.65907 | 0.68227
43602.5224 | 0.91338 | 1.0773 | 1.0122 | 0.82447 | 0.72738 | 0.66815 | 0.65676 | 0.68213
43602.5226 | 0.91455 | 1.0749 | 1.0075 | 0.8223 | 0.72421 | 0.66615 | 0.65617 | 0.68156
43602.5226 | 0.90715 | 1.0723 | 1.0071 | 0.82203 | 0.72505 | 0.66628 | 0.65574 | 0.68162
43602.5226 | 0.90895 | 1.073 | 1.0067 | 0.82229 | 0.72378 | 0.66546 | 0.65506 | 0.68134
43602.5226 | 0.9033 | 1.0694 | 1.0053 | 0.82055 | 0.72434 | 0.66584 | 0.65547 | 0.68151
43602.5226 | 0.90183 | 1.065 | 1.0004 | 0.81892 | 0.72069 | 0.66322 | 0.65444 | 0.68078
43602.5228 | 0.92198 | 1.0703 | 1.0018 | 0.82113 | 0.72303 | 0.66471 | 0.65703 | 0.68175
43602.5228 | 0.9201 | 1.0692 | 1.0022 | 0.82119 | 0.72455 | 0.66567 | 0.65502 | 0.68166
43602.5228 | 0.90654 | 1.0639 | 0.99874 | 0.81751 | 0.72179 | 0.66383 | 0.65397 | 0.68047
43602.5228 | 0.92258 | 1.0716 | 1.0033 | 0.8222 | 0.72314 | 0.66479 | 0.6556 | 0.68126
43602.5228 | 0.91621 | 1.0678 | 0.99987 | 0.81901 | 0.72309 | 0.66437 | 0.65504 | 0.68014
43602.523 | 0.9243 | 1.0745 | 1.0059 | 0.82363 | 0.72989 | 0.66932 | 0.65813 | 0.68177
43602.523 | 0.93533 | 1.0825 | 1.0101 | 0.82714 | 0.73066 | 0.67043 | 0.66033 | 0.68211
43602.523 | 0.94244 | 1.0776 | 1.0071 | 0.82517 | 0.72493 | 0.6662 | 0.66104 | 0.68035
43602.523 | 0.94789 | 1.0882 | 1.0154 | 0.83188 | 0.73334 | 0.67273 | 0.66273 | 0.68278
43602.5229 | 0.92367 | 1.076 | 1.0073 | 0.82447 | 0.72855 | 0.66961 | 0.65897 | 0.68161
43602.5231 | 0.93792 | 1.0856 | 1.0144 | 0.83078 | 0.72855 | 0.67001 | 0.65959 | 0.68204
43602.5231 | 0.94523 | 1.085 | 1.0135 | 0.82963 | 0.73286 | 0.67288 | 0.66151 | 0.6828
43602.5231 | 0.94183 | 1.0842 | 1.0129 | 0.8288 | 0.7296 | 0.67042 | 0.65918 | 0.6821
43602.5232 | 0.93437 | 1.0841 | 1.0135 | 0.82912 | 0.73123 | 0.6717 | 0.66168 | 0.68247
43602.5231 | 0.94371 | 1.0874 | 1.0152 | 0.83061 | 0.73262 | 0.67237 | 0.66104 | 0.68318
43602.5233 | 0.92628 | 1.0816 | 1.0132 | 0.82898 | 0.73111 | 0.67146 | 0.66488 | 0.68365
43602.5233 | 0.93102 | 1.0792 | 1.0099 | 0.82708 | 0.73044 | 0.67116 | 0.66174 | 0.68322
43602.5233 | 0.9251 | 1.0765 | 1.0074 | 0.82508 | 0.72861 | 0.6695 | 0.65968 | 0.68311
43602.5233 | 0.91707 | 1.0756 | 1.0083 | 0.82566 | 0.72814 | 0.66904 | 0.65926 | 0.68301
43602.5233 | 0.91653 | 1.07 | 1.0017 | 0.82144 | 0.72549 | 0.66702 | 0.65748 | 0.68328
43602.5235 | 0.90805 | 1.064 | 0.99784 | 0.81923 | 0.72321 | 0.6657 | 0.65869 | 0.68305
43602.5235 | 0.91175 | 1.067 | 0.99839 | 0.81997 | 0.72402 | 0.66613 | 0.65887 | 0.68326
43602.5235 | 0.89733 | 1.0578 | 0.99326 | 0.81554 | 0.72185 | 0.66474 | 0.65548 | 0.68219
43602.5235 | 0.89527 | 1.0562 | 0.99278 | 0.81457 | 0.7187 | 0.66275 | 0.65391 | 0.68175
43602.5235 | 0.89887 | 1.0577 | 0.9924 | 0.81514 | 0.71974 | 0.663 | 0.65451 | 0.68214
43602.5236 | 0.90247 | 1.057 | 0.99035 | 0.81473 | 0.7174 | 0.6612 | 0.65463 | 0.68119
43602.5236 | 0.89546 | 1.0545 | 0.9893 | 0.81397 | 0.71893 | 0.66241 | 0.65507 | 0.68164
43602.5237 | 0.90658 | 1.0567 | 0.98953 | 0.81393 | 0.71657 | 0.66055 | 0.65244 | 0.68066
43602.5237 | 0.89924 | 1.0546 | 0.9888 | 0.81317 | 0.71875 | 0.66213 | 0.65353 | 0.68143
43602.5236 | 0.90149 | 1.0539 | 0.98815 | 0.81205 | 0.71781 | 0.66118 | 0.65189 | 0.68039
43602.5238 | 0.91222 | 1.0581 | 0.99085 | 0.81579 | 0.71956 | 0.66237 | 0.65409 | 0.68126
43602.5238 | 0.9194 | 1.0616 | 0.99132 | 0.81605 | 0.71872 | 0.66157 | 0.65278 | 0.68042
43602.5238 | 0.90542 | 1.0542 | 0.98701 | 0.81201 | 0.72057 | 0.66295 | 0.65338 | 0.68084
43602.5238 | 0.89966 | 1.0528 | 0.98578 | 0.81142 | 0.71601 | 0.66005 | 0.6537 | 0.67973
43602.5238 | 0.89365 | 1.0445 | 0.979 | 0.80782 | 0.71528 | 0.6595 | 0.65207 | 0.68007
43602.524 | 0.88989 | 1.042 | 0.97665 | 0.80638 | 0.71399 | 0.65871 | 0.64978 | 0.68007
43602.524 | 0.89729 | 1.0399 | 0.97378 | 0.80419 | 0.71054 | 0.65621 | 0.65073 | 0.67926
43602.524 | 0.88992 | 1.0388 | 0.97303 | 0.80453 | 0.7105 | 0.65621 | 0.64899 | 0.67968
43602.524 | 0.90177 | 1.0413 | 0.97416 | 0.80594 | 0.71149 | 0.65663 | 0.64929 | 0.67987
43602.524 | 0.89368 | 1.0397 | 0.97357 | 0.80574 | 0.71104 | 0.6565 | 0.64805 | 0.67966
43602.5241 | 0.89154 | 1.0286 | 0.96251 | 0.79816 | 0.70618 | 0.65284 | 0.64998 | 0.67862
43602.5242 | 0.89243 | 1.0322 | 0.96558 | 0.80084 | 0.70792 | 0.65424 | 0.64698 | 0.6793
43602.5242 | 0.89054 | 1.0272 | 0.96157 | 0.7979 | 0.70642 | 0.65302 | 0.6459 | 0.67867
43602.5242 | 0.89288 | 1.0276 | 0.96212 | 0.79885 | 0.70591 | 0.65289 | 0.64576 | 0.67875
43602.5241 | 0.87484 | 1.0246 | 0.96122 | 0.79814 | 0.7052 | 0.652 | 0.64429 | 0.6781
43602.5243 | 0.89643 | 1.0271 | 0.95981 | 0.79751 | 0.70542 | 0.65245 | 0.64505 | 0.67813
43602.5243 | 0.91299 | 1.0323 | 0.96211 | 0.79973 | 0.70779 | 0.65397 | 0.64724 | 0.67848
43602.5243 | 0.91025 | 1.0295 | 0.96078 | 0.79793 | 0.70644 | 0.65306 | 0.64473 | 0.67812
43602.5243 | 0.92828 | 1.0359 | 0.96493 | 0.80151 | 0.70835 | 0.65449 | 0.64611 | 0.6788
43602.5243 | 0.90685 | 1.0288 | 0.96031 | 0.79912 | 0.70827 | 0.65499 | 0.64698 | 0.67898
43602.5245 | 0.91837 | 1.0262 | 0.95637 | 0.79683 | 0.70825 | 0.65492 | 0.64562 | 0.67956
43602.5245 | 0.89701 | 1.0182 | 0.95131 | 0.79314 | 0.70362 | 0.6518 | 0.6435 | 0.67833
43602.5245 | 0.90828 | 1.0208 | 0.95262 | 0.79445 | 0.70321 | 0.65157 | 0.64643 | 0.67833
43602.5245 | 0.91589 | 1.0264 | 0.95583 | 0.79688 | 0.70712 | 0.65429 | 0.64743 | 0.67897
43602.5245 | 0.91031 | 1.012 | 0.94474 | 0.78983 | 0.69981 | 0.64865 | 0.64151 | 0.67789
43602.5247 | 0.91989 | 1.0109 | 0.94413 | 0.7891 | 0.69883 | 0.64814 | 0.64072 | 0.67819
43602.5247 | 0.88683 | 1.003 | 0.93856 | 0.78567 | 0.70044 | 0.6493 | 0.6417 | 0.67832
43602.5247 | 0.91647 | 1.0101 | 0.94301 | 0.78854 | 0.69777 | 0.64724 | 0.64119 | 0.67775
43602.5247 | 0.9058 | 1.0071 | 0.94014 | 0.78609 | 0.69913 | 0.64817 | 0.64009 | 0.67792
43602.5246 | 0.92501 | 1.0142 | 0.94453 | 0.79088 | 0.69963 | 0.64839 | 0.64138 | 0.6778
43602.5248 | 0.89517 | 0.99822 | 0.93341 | 0.78251 | 0.69401 | 0.64441 | 0.63766 | 0.67655
43602.5248 | 0.91076 | 1.0056 | 0.93695 | 0.78549 | 0.6991 | 0.64807 | 0.64075 | 0.67782
43602.5248 | 0.90439 | 1.0002 | 0.93349 | 0.78238 | 0.69679 | 0.64598 | 0.63932 | 0.6769
43602.5249 | 0.9246 | 1.01 | 0.94054 | 0.78849 | 0.69878 | 0.64812 | 0.64009 | 0.67756
43602.5248 | 0.90101 | 0.99382 | 0.92856 | 0.77976 | 0.69417 | 0.64509 | 0.63899 | 0.67742
43602.525 | 0.89457 | 0.98508 | 0.92229 | 0.7754 | 0.69562 | 0.64638 | 0.63981 | 0.67741
43602.525 | 0.90346 | 0.98585 | 0.92192 | 0.77536 | 0.68766 | 0.6407 | 0.63769 | 0.67631
43602.525 | 0.9109 | 0.99222 | 0.92521 | 0.77816 | 0.69283 | 0.64421 | 0.6384 | 0.67758
43602.525 | 0.88788 | 0.9804 | 0.91867 | 0.77317 | 0.69068 | 0.6428 | 0.63722 | 0.67677
43602.525 | 0.89014 | 0.97682 | 0.91496 | 0.77075 | 0.68731 | 0.64041 | 0.63475 | 0.67661
43602.5252 | 0.86837 | 0.97174 | 0.91179 | 0.76858 | 0.68983 | 0.64172 | 0.63715 | 0.67689
43602.5252 | 0.87494 | 0.972 | 0.91123 | 0.76858 | 0.6864 | 0.63952 | 0.63426 | 0.6766
43602.5252 | 0.90722 | 0.98035 | 0.91664 | 0.7732 | 0.68594 | 0.63942 | 0.63323 | 0.67686
43602.5252 | 0.89078 | 0.97555 | 0.9135 | 0.77101 | 0.69186 | 0.64355 | 0.63908 | 0.67796
43602.5252 | 0.90925 | 0.9779 | 0.91326 | 0.77164 | 0.68583 | 0.63974 | 0.63661 | 0.67649
43602.5253 | 0.87795 | 0.96656 | 0.9049 | 0.76522 | 0.68498 | 0.63935 | 0.63431 | 0.67682
43602.5253 | 0.8964 | 0.97116 | 0.90843 | 0.7683 | 0.68146 | 0.63684 | 0.63206 | 0.67621
43602.5254 | 0.93384 | 0.98522 | 0.91828 | 0.77626 | 0.69273 | 0.6451 | 0.63856 | 0.67831
43602.5254 | 0.91768 | 0.97765 | 0.91352 | 0.77191 | 0.69142 | 0.64382 | 0.63668 | 0.67777
43602.5253 | 0.89028 | 0.9614 | 0.90031 | 0.76216 | 0.68508 | 0.63923 | 0.63401 | 0.67724
43602.5255 | 0.91297 | 0.97203 | 0.90703 | 0.76897 | 0.68778 | 0.64232 | 0.63792 | 0.67871
43602.5255 | 0.89142 | 0.96038 | 0.89946 | 0.76261 | 0.68437 | 0.63935 | 0.63352 | 0.67783
43602.5255 | 0.9114 | 0.96671 | 0.90479 | 0.76718 | 0.68792 | 0.64194 | 0.63579 | 0.67875
43602.5255 | 0.90538 | 0.9586 | 0.89848 | 0.76189 | 0.68291 | 0.63819 | 0.63285 | 0.67776
43602.5255 | 0.89864 | 0.96238 | 0.89952 | 0.76412 | 0.68558 | 0.64038 | 0.63433 | 0.67842
43602.5257 | 0.90543 | 0.95357 | 0.89344 | 0.75872 | 0.68224 | 0.63823 | 0.63315 | 0.67847
43602.5257 | 0.9174 | 0.96517 | 0.90164 | 0.76643 | 0.6857 | 0.64124 | 0.63597 | 0.67956
43602.5257 | 0.89461 | 0.95845 | 0.89652 | 0.76221 | 0.68498 | 0.64066 | 0.63372 | 0.67929
43602.5257 | 0.89487 | 0.95672 | 0.89545 | 0.76117 | 0.68313 | 0.63924 | 0.63339 | 0.67897
43602.5257 | 0.90865 | 0.96202 | 0.89931 | 0.76483 | 0.68765 | 0.64276 | 0.63611 | 0.68002
43602.5259 | 0.89737 | 0.95291 | 0.89252 | 0.75872 | 0.68364 | 0.64015 | 0.63473 | 0.6795
43602.5259 | 0.93115 | 0.96712 | 0.90355 | 0.76915 | 0.68715 | 0.64244 | 0.63737 | 0.68046
43602.5259 | 0.91074 | 0.96338 | 0.90067 | 0.76654 | 0.68716 | 0.64259 | 0.63665 | 0.68048
43602.5259 | 0.89139 | 0.95414 | 0.8941 | 0.7606 | 0.68686 | 0.64242 | 0.63729 | 0.68045
43602.5258 | 0.91 | 0.95617 | 0.89578 | 0.76316 | 0.6825 | 0.63955 | 0.6376 | 0.68066
43602.526 | 0.86832 | 0.94419 | 0.88713 | 0.75659 | 0.68045 | 0.63767 | 0.63427 | 0.6808
43602.526 | 0.87838 | 0.94351 | 0.88605 | 0.7557 | 0.67782 | 0.63621 | 0.63271 | 0.68028
43602.5261 | 0.8961 | 0.94979 | 0.89048 | 0.75987 | 0.68215 | 0.63953 | 0.6347 | 0.6813
43602.5261 | 0.87114 | 0.93483 | 0.88043 | 0.75102 | 0.67781 | 0.63545 | 0.63458 | 0.68029
43602.526 | 0.87364 | 0.93307 | 0.87777 | 0.75121 | 0.67422 | 0.6337 | 0.6305 | 0.68139
43602.5262 | 0.87371 | 0.93136 | 0.87659 | 0.75124 | 0.67452 | 0.63379 | 0.63357 | 0.68131
43602.5262 | 0.8673 | 0.92846 | 0.87402 | 0.74886 | 0.67444 | 0.63365 | 0.63087 | 0.68158
43602.5262 | 0.86798 | 0.92963 | 0.8749 | 0.74937 | 0.67408 | 0.63348 | 0.63109 | 0.68157
43602.5262 | 0.84795 | 0.92134 | 0.86868 | 0.7447 | 0.67084 | 0.63142 | 0.62855 | 0.6809
43602.5262 | 0.87848 | 0.92973 | 0.87452 | 0.74973 | 0.67459 | 0.63342 | 0.63117 | 0.68166
43602.5264 | 0.87204 | 0.93355 | 0.87751 | 0.75217 | 0.67383 | 0.63328 | 0.63119 | 0.6811
43602.5264 | 0.87265 | 0.93311 | 0.87752 | 0.75216 | 0.67565 | 0.63478 | 0.63185 | 0.68145
43602.5264 | 0.87931 | 0.93244 | 0.87676 | 0.75107 | 0.67597 | 0.6348 | 0.63124 | 0.68155
43602.5264 | 0.88073 | 0.93239 | 0.87636 | 0.75091 | 0.67525 | 0.63437 | 0.63143 | 0.68142
43602.5264 | 0.89769 | 0.94781 | 0.88988 | 0.76193 | 0.68286 | 0.6409 | 0.63908 | 0.68361
43602.5266 | 0.87577 | 0.9408 | 0.88367 | 0.7567 | 0.68031 | 0.6388 | 0.63578 | 0.68372
43602.5266 | 0.89031 | 0.94345 | 0.88629 | 0.75887 | 0.68205 | 0.64023 | 0.63768 | 0.68441
43602.5266 | 0.87426 | 0.93655 | 0.88187 | 0.75508 | 0.68124 | 0.63959 | 0.63656 | 0.68429
43602.5266 | 0.87093 | 0.93552 | 0.8812 | 0.75503 | 0.67829 | 0.63783 | 0.63475 | 0.68419
43602.5265 | 0.85476 | 0.92651 | 0.87632 | 0.75135 | 0.6786 | 0.63803 | 0.63978 | 0.68597
43602.5267 | 0.83242 | 0.92431 | 0.87421 | 0.75141 | 0.67732 | 0.63724 | 0.63451 | 0.68674
43602.5267 | 0.82215 | 0.92704 | 0.87627 | 0.75362 | 0.67809 | 0.63838 | 0.63666 | 0.68705
43602.5268 | 0.83862 | 0.92692 | 0.87571 | 0.75322 | 0.67904 | 0.63866 | 0.63649 | 0.68728
43602.5268 | 0.82056 | 0.92315 | 0.8734 | 0.75082 | 0.67735 | 0.6374 | 0.63451 | 0.68679
43602.5267 | 0.80748 | 0.91656 | 0.86881 | 0.74811 | 0.67404 | 0.63529 | 0.63564 | 0.68659
43602.5269 | 0.79775 | 0.9132 | 0.86588 | 0.74558 | 0.67246 | 0.634 | 0.63166 | 0.68603
43602.5269 | 0.80088 | 0.91356 | 0.86639 | 0.74613 | 0.67148 | 0.63319 | 0.63043 | 0.68566
43602.5269 | 0.80079 | 0.91568 | 0.86753 | 0.74808 | 0.67222 | 0.63343 | 0.63121 | 0.68559
43602.5269 | 0.79673 | 0.91521 | 0.86688 | 0.74762 | 0.67241 | 0.63331 | 0.63508 | 0.6852
43602.5269 | 0.80412 | 0.91493 | 0.86625 | 0.74695 | 0.67086 | 0.63199 | 0.63257 | 0.68461
43602.5271 | 0.79433 | 0.91047 | 0.86473 | 0.74489 | 0.66987 | 0.632 | 0.62911 | 0.68451
43602.5271 | 0.79679 | 0.91302 | 0.86638 | 0.74693 | 0.67043 | 0.63202 | 0.63048 | 0.68471
43602.5271 | 0.80373 | 0.91578 | 0.86791 | 0.74855 | 0.6713 | 0.63222 | 0.62977 | 0.6845
43602.5271 | 0.79994 | 0.91476 | 0.86791 | 0.74786 | 0.67139 | 0.63229 | 0.63311 | 0.6844
43602.5271 | 0.82969 | 0.92239 | 0.87194 | 0.75087 | 0.67349 | 0.6335 | 0.63376 | 0.68457
43602.5273 | 0.83819 | 0.92874 | 0.87607 | 0.75435 | 0.67644 | 0.63569 | 0.63305 | 0.68517
43602.5273 | 0.81553 | 0.92571 | 0.87671 | 0.7532 | 0.67738 | 0.63612 | 0.63272 | 0.68483
43602.5273 | 0.83419 | 0.92677 | 0.87586 | 0.75321 | 0.67589 | 0.63596 | 0.63399 | 0.68509
43602.5273 | 0.81364 | 0.92396 | 0.87499 | 0.75211 | 0.67646 | 0.63641 | 0.63377 | 0.68524
43602.5272 | 0.83429 | 0.92623 | 0.87683 | 0.75271 | 0.67693 | 0.63763 | 0.63501 | 0.68605
43602.5274 | 0.83858 | 0.93126 | 0.88074 | 0.75663 | 0.68144 | 0.64012 | 0.63772 | 0.68688
43602.5274 | 0.82902 | 0.92729 | 0.87855 | 0.75465 | 0.6782 | 0.63845 | 0.63691 | 0.6868
43602.5275 | 0.85507 | 0.93539 | 0.88306 | 0.75886 | 0.68103 | 0.64029 | 0.6375 | 0.68779
43602.5275 | 0.83279 | 0.92885 | 0.87932 | 0.75547 | 0.68078 | 0.63995 | 0.63717 | 0.68725
43602.5274 | 0.81518 | 0.92253 | 0.87524 | 0.75373 | 0.678 | 0.63907 | 0.63752 | 0.68822
43602.5276 | 0.81879 | 0.9218 | 0.87364 | 0.75254 | 0.67774 | 0.63943 | 0.6382 | 0.68835
43602.5276 | 0.81066 | 0.92087 | 0.87312 | 0.75233 | 0.67737 | 0.6386 | 0.63747 | 0.68832
43602.5276 | 0.80801 | 0.91973 | 0.87252 | 0.75155 | 0.67709 | 0.63885 | 0.63624 | 0.68838
43602.5276 | 0.80231 | 0.918 | 0.87118 | 0.75069 | 0.67599 | 0.63807 | 0.63535 | 0.68807
43602.5276 | 0.80028 | 0.91683 | 0.86974 | 0.751 | 0.67582 | 0.63715 | 0.63489 | 0.68773
43602.5278 | 0.79518 | 0.91497 | 0.86835 | 0.74986 | 0.6749 | 0.63626 | 0.63486 | 0.68761
43602.5278 | 0.80518 | 0.91459 | 0.86784 | 0.74912 | 0.67433 | 0.63594 | 0.63405 | 0.68749
43602.5278 | 0.79664 | 0.91314 | 0.86769 | 0.74899 | 0.67397 | 0.63572 | 0.63683 | 0.6873
43602.5278 | 0.79787 | 0.91415 | 0.86789 | 0.74934 | 0.67458 | 0.63633 | 0.6353 | 0.68739
43602.5278 | 0.79447 | 0.91476 | 0.86885 | 0.74903 | 0.67328 | 0.63555 | 0.63387 | 0.68715
43602.528 | 0.80607 | 0.92036 | 0.87329 | 0.75245 | 0.67542 | 0.63638 | 0.63653 | 0.68687
43602.528 | 0.80614 | 0.92051 | 0.87464 | 0.75289 | 0.67571 | 0.63687 | 0.63768 | 0.68696
43602.528 | 0.80374 | 0.92214 | 0.87597 | 0.75383 | 0.67655 | 0.63716 | 0.63529 | 0.68701
43602.528 | 0.804 | 0.92464 | 0.87755 | 0.7549 | 0.67699 | 0.63735 | 0.63525 | 0.68707
43602.5279 | 0.81364 | 0.92968 | 0.88256 | 0.75846 | 0.68016 | 0.63941 | 0.63692 | 0.68748
43602.5281 | 0.80592 | 0.92934 | 0.88403 | 0.75914 | 0.68082 | 0.64028 | 0.63845 | 0.68801
43602.5281 | 0.82125 | 0.93283 | 0.88494 | 0.76013 | 0.68127 | 0.64085 | 0.63867 | 0.68832
43602.5282 | 0.80745 | 0.92993 | 0.88471 | 0.75993 | 0.68131 | 0.64089 | 0.63882 | 0.68833
43602.5282 | 0.80988 | 0.93086 | 0.88498 | 0.75986 | 0.68171 | 0.6415 | 0.63833 | 0.68848
43602.5281 | 0.81414 | 0.9331 | 0.88668 | 0.7608 | 0.68246 | 0.64231 | 0.63992 | 0.68944
43602.5283 | 0.82062 | 0.93791 | 0.88949 | 0.76292 | 0.68469 | 0.64393 | 0.64194 | 0.68991
43602.5283 | 0.82136 | 0.93892 | 0.89055 | 0.76299 | 0.6848 | 0.64452 | 0.64178 | 0.69034
43602.5283 | 0.81662 | 0.93677 | 0.88924 | 0.76215 | 0.68487 | 0.64414 | 0.64192 | 0.6903
43602.5283 | 0.81358 | 0.9367 | 0.88948 | 0.76189 | 0.68452 | 0.64427 | 0.64157 | 0.69032
43602.5283 | 0.80458 | 0.93723 | 0.8918 | 0.76406 | 0.68628 | 0.64579 | 0.64345 | 0.69115
43602.5285 | 0.80841 | 0.9367 | 0.89151 | 0.76346 | 0.68603 | 0.64589 | 0.64267 | 0.69126
43602.5285 | 0.80402 | 0.93606 | 0.8911 | 0.76378 | 0.68554 | 0.64519 | 0.64287 | 0.69104
43602.5285 | 0.80448 | 0.93534 | 0.89074 | 0.76327 | 0.68562 | 0.64554 | 0.64289 | 0.69132
43602.5285 | 0.80812 | 0.93469 | 0.88988 | 0.76202 | 0.68532 | 0.64562 | 0.64335 | 0.69128
43602.5285 | 0.80747 | 0.93401 | 0.88882 | 0.76146 | 0.68456 | 0.6453 | 0.64308 | 0.69154
43602.5287 | 0.80611 | 0.93101 | 0.88745 | 0.76091 | 0.68378 | 0.6444 | 0.64165 | 0.69128
43602.5287 | 0.805 | 0.9317 | 0.88732 | 0.76092 | 0.68383 | 0.64466 | 0.64179 | 0.69149
43602.5287 | 0.80258 | 0.93195 | 0.8882 | 0.76151 | 0.68355 | 0.64421 | 0.642 | 0.69125
43602.5287 | 0.79966 | 0.93123 | 0.88787 | 0.76119 | 0.68361 | 0.64429 | 0.64117 | 0.6912
43602.5286 | 0.79766 | 0.92821 | 0.88489 | 0.75917 | 0.68277 | 0.644 | 0.64124 | 0.69128
43602.5288 | 0.79645 | 0.9265 | 0.88394 | 0.75839 | 0.68158 | 0.64254 | 0.64035 | 0.69059
43602.5288 | 0.78953 | 0.92426 | 0.88306 | 0.75787 | 0.68119 | 0.64207 | 0.64021 | 0.69034
43602.5289 | 0.79193 | 0.92525 | 0.88357 | 0.7578 | 0.68106 | 0.64194 | 0.63892 | 0.69046
43602.5289 | 0.78958 | 0.92515 | 0.88387 | 0.7584 | 0.68128 | 0.64212 | 0.64009 | 0.69017
43602.5288 | 0.79438 | 0.93158 | 0.88938 | 0.76031 | 0.68145 | 0.64171 | 0.64193 | 0.68915
43602.529 | 0.79983 | 0.94233 | 0.90155 | 0.76826 | 0.68559 | 0.64361 | 0.64094 | 0.68867
43602.529 | 0.80993 | 0.94631 | 0.90403 | 0.76938 | 0.68677 | 0.64435 | 0.64083 | 0.68881
43602.529 | 0.80301 | 0.94625 | 0.90576 | 0.77043 | 0.68759 | 0.64493 | 0.6422 | 0.68878
43602.529 | 0.81295 | 0.95025 | 0.90873 | 0.77216 | 0.68854 | 0.64558 | 0.64128 | 0.68897
43602.529 | 0.81769 | 0.96708 | 0.92586 | 0.78272 | 0.69711 | 0.65112 | 0.64585 | 0.68983
43602.5292 | 0.82503 | 0.97539 | 0.93252 | 0.78796 | 0.70083 | 0.65465 | 0.652 | 0.69142
43602.5292 | 0.81937 | 0.97523 | 0.93339 | 0.78812 | 0.70189 | 0.65545 | 0.65148 | 0.69167
43602.5292 | 0.82866 | 0.97782 | 0.93318 | 0.78785 | 0.70256 | 0.65628 | 0.6511 | 0.69222
43602.5292 | 0.83 | 0.98015 | 0.93578 | 0.79033 | 0.70295 | 0.65672 | 0.65173 | 0.69251
43602.5292 | 0.83042 | 0.98369 | 0.93975 | 0.79316 | 0.7062 | 0.65945 | 0.65372 | 0.69352
43602.5294 | 0.82148 | 0.97963 | 0.9378 | 0.79218 | 0.70637 | 0.6602 | 0.65825 | 0.69422
43602.5294 | 0.82336 | 0.98025 | 0.93872 | 0.79251 | 0.70643 | 0.66001 | 0.65441 | 0.69444
43602.5294 | 0.82059 | 0.97933 | 0.93849 | 0.79214 | 0.70735 | 0.66086 | 0.65563 | 0.6948
43602.5294 | 0.8199 | 0.98006 | 0.93824 | 0.79191 | 0.70697 | 0.66085 | 0.65595 | 0.69496
43602.5294 | 0.83642 | 0.98517 | 0.94075 | 0.79346 | 0.70828 | 0.66172 | 0.65638 | 0.69532
43602.5295 | 0.82474 | 0.98549 | 0.9449 | 0.79581 | 0.7095 | 0.6623 | 0.65739 | 0.6955
43602.5295 | 0.82851 | 0.98857 | 0.94605 | 0.7969 | 0.71052 | 0.66331 | 0.65673 | 0.69595
43602.5296 | 0.83918 | 0.99159 | 0.94717 | 0.79751 | 0.71086 | 0.66341 | 0.65755 | 0.69575
43602.5296 | 0.83331 | 0.99137 | 0.94778 | 0.79859 | 0.71143 | 0.66356 | 0.65788 | 0.69579
43602.5295 | 0.8336 | 0.99689 | 0.9532 | 0.80126 | 0.71362 | 0.6652 | 0.66281 | 0.69586
43602.5297 | 0.84277 | 1.0048 | 0.96022 | 0.8061 | 0.71734 | 0.66757 | 0.66423 | 0.69676
43602.5297 | 0.84946 | 1.0083 | 0.96106 | 0.80657 | 0.71796 | 0.66793 | 0.66223 | 0.69671
43602.5297 | 0.84069 | 1.0069 | 0.96191 | 0.80711 | 0.71845 | 0.66857 | 0.6619 | 0.69651
43602.5298 | 0.84348 | 1.008 | 0.96292 | 0.8084 | 0.71896 | 0.66898 | 0.66226 | 0.69665
43602.5297 | 0.85926 | 1.0185 | 0.96956 | 0.81197 | 0.72278 | 0.67168 | 0.66478 | 0.69761
43602.5299 | 0.84525 | 1.0147 | 0.96978 | 0.81158 | 0.7232 | 0.6718 | 0.66827 | 0.69766
43602.5299 | 0.85325 | 1.0185 | 0.9701 | 0.81218 | 0.7232 | 0.67236 | 0.66534 | 0.69774
43602.5299 | 0.85718 | 1.0192 | 0.97018 | 0.81288 | 0.72343 | 0.67229 | 0.66493 | 0.69749
43602.5299 | 0.86042 | 1.0214 | 0.97173 | 0.81363 | 0.72437 | 0.67265 | 0.66611 | 0.69789
43602.5299 | 0.86248 | 1.0254 | 0.97448 | 0.81485 | 0.72443 | 0.67282 | 0.66645 | 0.69731
43602.5301 | 0.85611 | 1.0291 | 0.98017 | 0.81816 | 0.72692 | 0.67481 | 0.66734 | 0.69768
43602.5301 | 0.87025 | 1.0341 | 0.98145 | 0.81959 | 0.72772 | 0.67526 | 0.66852 | 0.69794
43602.5301 | 0.87366 | 1.0388 | 0.98497 | 0.82158 | 0.72973 | 0.67621 | 0.66893 | 0.69794
43602.5301 | 0.88402 | 1.0418 | 0.98631 | 0.82285 | 0.73098 | 0.67702 | 0.66989 | 0.69826
43602.5301 | 0.87124 | 1.0447 | 0.99141 | 0.82537 | 0.73335 | 0.67941 | 0.67195 | 0.69876
43602.5302 | 0.87596 | 1.0495 | 0.996 | 0.82787 | 0.73717 | 0.68214 | 0.67378 | 0.69986
43602.5303 | 0.88352 | 1.0509 | 0.99575 | 0.8279 | 0.73633 | 0.68196 | 0.67404 | 0.69985
43602.5303 | 0.87933 | 1.0499 | 0.99569 | 0.82738 | 0.73635 | 0.68198 | 0.67362 | 0.69978
43602.5303 | 0.87881 | 1.0504 | 0.99658 | 0.82909 | 0.7373 | 0.68259 | 0.67453 | 0.7002
43602.5302 | 0.87034 | 1.0439 | 0.99184 | 0.8247 | 0.7344 | 0.6811 | 0.67264 | 0.6998
43602.5304 | 0.86858 | 1.0398 | 0.98828 | 0.82269 | 0.73258 | 0.6802 | 0.67174 | 0.69988
43602.5304 | 0.864 | 1.0381 | 0.98825 | 0.82251 | 0.73231 | 0.6799 | 0.67171 | 0.69976
43602.5304 | 0.85998 | 1.0361 | 0.98779 | 0.82251 | 0.73189 | 0.67949 | 0.67212 | 0.6997
43602.5304 | 0.86904 | 1.039 | 0.98785 | 0.82229 | 0.73224 | 0.67944 | 0.67121 | 0.69991
43602.5306 | 0.85972 | 1.0361 | 0.98878 | 0.82201 | 0.73029 | 0.67789 | 0.66934 | 0.69899
43602.5306 | 0.86708 | 1.039 | 0.98945 | 0.82229 | 0.73091 | 0.67797 | 0.67466 | 0.69911
43602.5306 | 0.85574 | 1.0371 | 0.99094 | 0.82285 | 0.73082 | 0.67779 | 0.67048 | 0.69856
43602.5306 | 0.87291 | 1.0418 | 0.99086 | 0.82304 | 0.73108 | 0.67809 | 0.66993 | 0.69846
43602.5306 | 0.86795 | 1.0479 | 0.99921 | 0.82722 | 0.73369 | 0.67957 | 0.67075 | 0.69797
43602.5307 | 0.87992 | 1.0582 | 1.0068 | 0.83117 | 0.7364 | 0.6808 | 0.67208 | 0.6978
43602.5308 | 0.88647 | 1.0609 | 1.0077 | 0.83193 | 0.73703 | 0.681 | 0.67095 | 0.69755
43602.5308 | 0.87501 | 1.0584 | 1.0097 | 0.83193 | 0.73787 | 0.6812 | 0.6713 | 0.69745
43602.5308 | 0.87419 | 1.0573 | 1.0085 | 0.8308 | 0.73658 | 0.68084 | 0.67423 | 0.69719
43602.5307 | 0.89295 | 1.0708 | 1.0174 | 0.83525 | 0.74007 | 0.68339 | 0.67501 | 0.69723
43602.5309 | 0.90343 | 1.0808 | 1.0261 | 0.83957 | 0.74377 | 0.68624 | 0.67474 | 0.69781
43602.5309 | 0.89226 | 1.0814 | 1.0278 | 0.8415 | 0.74422 | 0.68619 | 0.68037 | 0.69746
43602.5309 | 0.9037 | 1.0844 | 1.0279 | 0.84245 | 0.74548 | 0.68696 | 0.67803 | 0.69773
43602.531 | 0.90517 | 1.0842 | 1.0292 | 0.84169 | 0.7454 | 0.68685 | 0.67655 | 0.69742
43602.5309 | 0.90973 | 1.0883 | 1.0323 | 0.8435 | 0.74704 | 0.68829 | 0.67833 | 0.698
43602.5311 | 0.90772 | 1.0896 | 1.0335 | 0.84493 | 0.74867 | 0.68962 | 0.67826 | 0.69864
43602.5311 | 0.90345 | 1.0877 | 1.0333 | 0.84422 | 0.74792 | 0.68921 | 0.68197 | 0.6985
43602.5311 | 0.9086 | 1.0888 | 1.0335 | 0.84444 | 0.74774 | 0.68934 | 0.67904 | 0.69867
43602.5311 | 0.90874 | 1.0902 | 1.0339 | 0.84508 | 0.74829 | 0.68941 | 0.67817 | 0.69862
43602.5311 | 0.91062 | 1.092 | 1.0355 | 0.84647 | 0.75 | 0.69073 | 0.67939 | 0.69926
43602.5313 | 0.90326 | 1.0884 | 1.0343 | 0.84473 | 0.7485 | 0.68991 | 0.67899 | 0.69906
43602.5313 | 0.91096 | 1.0912 | 1.0348 | 0.84582 | 0.74907 | 0.69017 | 0.68227 | 0.69907
43602.5313 | 0.90634 | 1.0929 | 1.036 | 0.84774 | 0.75022 | 0.69067 | 0.68033 | 0.69956
43602.5313 | 0.91087 | 1.0933 | 1.0353 | 0.84663 | 0.75065 | 0.69104 | 0.68009 | 0.69961
43602.5314 | 0.91353 | 1.0939 | 1.0362 | 0.84557 | 0.7481 | 0.68845 | 0.67818 | 0.69766
43602.5314 | 0.91216 | 1.0944 | 1.037 | 0.84613 | 0.74913 | 0.68896 | 0.68118 | 0.69757
43602.5314 | 0.90309 | 1.0925 | 1.0391 | 0.84644 | 0.74907 | 0.68892 | 0.67774 | 0.69775
43602.5315 | 0.9135 | 1.0981 | 1.0402 | 0.84773 | 0.74959 | 0.68974 | 0.67861 | 0.69796
43602.5314 | 0.91024 | 1.0968 | 1.0397 | 0.84684 | 0.74913 | 0.6889 | 0.67793 | 0.69652
43602.5316 | 0.91997 | 1.0999 | 1.041 | 0.84699 | 0.74907 | 0.68873 | 0.68044 | 0.69613
43602.5316 | 0.91331 | 1.0985 | 1.0414 | 0.84682 | 0.74875 | 0.68835 | 0.67888 | 0.6958
43602.5316 | 0.91321 | 1.0986 | 1.0413 | 0.84633 | 0.74854 | 0.68846 | 0.67772 | 0.69591
43602.5316 | 0.91849 | 1.0993 | 1.041 | 0.84627 | 0.74862 | 0.68817 | 0.67726 | 0.69596
43602.5316 | 0.91789 | 1.1009 | 1.042 | 0.84692 | 0.74842 | 0.68791 | 0.67711 | 0.6952
43602.5318 | 0.91357 | 1.1021 | 1.045 | 0.84801 | 0.74828 | 0.68776 | 0.67722 | 0.69517
43602.5318 | 0.9171 | 1.1049 | 1.0454 | 0.84945 | 0.74903 | 0.68854 | 0.67766 | 0.69514
43602.5318 | 0.91417 | 1.1039 | 1.0465 | 0.8498 | 0.75045 | 0.68892 | 0.67756 | 0.6954
43602.5318 | 0.91868 | 1.1027 | 1.0448 | 0.84686 | 0.74892 | 0.68836 | 0.67633 | 0.69487
43602.5318 | 0.92391 | 1.105 | 1.0442 | 0.84735 | 0.74853 | 0.68799 | 0.67897 | 0.69455
43602.532 | 0.92487 | 1.1063 | 1.0457 | 0.84862 | 0.74913 | 0.68817 | 0.67946 | 0.69458
43602.532 | 0.92701 | 1.1069 | 1.0467 | 0.84988 | 0.75042 | 0.68846 | 0.67765 | 0.69441
43602.532 | 0.92578 | 1.1093 | 1.048 | 0.85078 | 0.75163 | 0.6892 | 0.68096 | 0.69487
43602.532 | 0.92795 | 1.1075 | 1.0471 | 0.84889 | 0.75193 | 0.68927 | 0.67819 | 0.69494
43602.5319 | 0.91985 | 1.1046 | 1.0462 | 0.84712 | 0.74912 | 0.68786 | 0.67817 | 0.69395
43602.5321 | 0.92205 | 1.1095 | 1.0507 | 0.85001 | 0.75165 | 0.68924 | 0.6782 | 0.69433
43602.5321 | 0.9288 | 1.1141 | 1.0509 | 0.85271 | 0.75211 | 0.69011 | 0.68153 | 0.69462
43602.5322 | 0.93298 | 1.1144 | 1.0508 | 0.85163 | 0.75296 | 0.69022 | 0.67903 | 0.69456
43602.5321 | 0.92992 | 1.1107 | 1.0481 | 0.85011 | 0.7512 | 0.6891 | 0.67779 | 0.69407
43602.5323 | 0.92363 | 1.1079 | 1.0477 | 0.84909 | 0.75067 | 0.6891 | 0.67609 | 0.69459
43602.5323 | 0.92853 | 1.1102 | 1.0484 | 0.85036 | 0.75146 | 0.68939 | 0.67676 | 0.69489
43602.5323 | 0.92719 | 1.1091 | 1.0476 | 0.84923 | 0.75098 | 0.68914 | 0.68217 | 0.69455
43602.5323 | 0.92839 | 1.1108 | 1.0483 | 0.85009 | 0.75053 | 0.68899 | 0.67898 | 0.69455
43602.5323 | 0.92966 | 1.1129 | 1.0506 | 0.85233 | 0.75364 | 0.69086 | 0.68321 | 0.69538
43602.5325 | 0.93559 | 1.1147 | 1.051 | 0.8522 | 0.75381 | 0.69123 | 0.67958 | 0.69479
43602.5325 | 0.92964 | 1.1135 | 1.0512 | 0.85089 | 0.75353 | 0.69064 | 0.6779 | 0.69523
43602.5325 | 0.92812 | 1.1116 | 1.0517 | 0.85161 | 0.75284 | 0.69085 | 0.67823 | 0.695
43602.5325 | 0.93664 | 1.1153 | 1.0517 | 0.85377 | 0.75447 | 0.6919 | 0.68288 | 0.69565
43602.5324 | 0.9416 | 1.1202 | 1.0546 | 0.856 | 0.75571 | 0.69277 | 0.68318 | 0.69584
43602.5326 | 0.93878 | 1.1203 | 1.0558 | 0.8562 | 0.75509 | 0.69274 | 0.68009 | 0.69566
43602.5326 | 0.94329 | 1.1251 | 1.0589 | 0.85899 | 0.75867 | 0.6948 | 0.68467 | 0.6973
43602.5327 | 0.94245 | 1.123 | 1.0573 | 0.85791 | 0.75785 | 0.69463 | 0.68157 | 0.69666
43602.5327 | 0.94062 | 1.121 | 1.056 | 0.85566 | 0.75759 | 0.69448 | 0.68253 | 0.69645
43602.5326 | 0.9333 | 1.1164 | 1.0527 | 0.85406 | 0.75376 | 0.69236 | 0.68107 | 0.69615
43602.5328 | 0.92204 | 1.1061 | 1.0466 | 0.84841 | 0.75187 | 0.69122 | 0.68019 | 0.69595
43602.5328 | 0.92181 | 1.1066 | 1.0459 | 0.84952 | 0.75077 | 0.6902 | 0.67904 | 0.69552
43602.5328 | 0.92442 | 1.1092 | 1.0482 | 0.85051 | 0.75233 | 0.69165 | 0.67907 | 0.69655
43602.5328 | 0.92288 | 1.1092 | 1.0477 | 0.85149 | 0.75304 | 0.69152 | 0.67888 | 0.69668
43602.5328 | 0.92458 | 1.1085 | 1.0467 | 0.84991 | 0.75171 | 0.69095 | 0.67945 | 0.6961
43602.533 | 0.92607 | 1.1139 | 1.0518 | 0.85366 | 0.75397 | 0.6924 | 0.68073 | 0.69638
43602.533 | 0.93343 | 1.1153 | 1.0527 | 0.85396 | 0.7547 | 0.69305 | 0.68117 | 0.69643
43602.533 | 0.93634 | 1.1177 | 1.0534 | 0.85434 | 0.75507 | 0.69285 | 0.68228 | 0.69598
43602.533 | 0.93659 | 1.1183 | 1.0534 | 0.85489 | 0.75592 | 0.69342 | 0.68002 | 0.69625
43602.5331 | 0.94476 | 1.1242 | 1.0569 | 0.85744 | 0.75589 | 0.69347 | 0.681 | 0.6961
43602.5332 | 0.94337 | 1.1236 | 1.0571 | 0.85745 | 0.75926 | 0.6952 | 0.68567 | 0.69717
43602.5332 | 0.9389 | 1.1221 | 1.0573 | 0.85662 | 0.75754 | 0.69464 | 0.68465 | 0.69683
43602.5332 | 0.94584 | 1.1265 | 1.0588 | 0.85995 | 0.7587 | 0.69538 | 0.68348 | 0.697
43602.5331 | 0.94162 | 1.1272 | 1.0615 | 0.86139 | 0.76116 | 0.69751 | 0.68469 | 0.69822
43602.5333 | 0.9412 | 1.1261 | 1.0602 | 0.86027 | 0.76045 | 0.69687 | 0.68454 | 0.69777
43602.5333 | 0.94115 | 1.1244 | 1.0592 | 0.85828 | 0.76053 | 0.69669 | 0.68418 | 0.69781
43602.5333 | 0.95103 | 1.1274 | 1.0596 | 0.85955 | 0.75899 | 0.69568 | 0.68288 | 0.69712
43602.5334 | 0.94563 | 1.1273 | 1.0615 | 0.85996 | 0.7623 | 0.69764 | 0.68446 | 0.69822
43602.5333 | 0.94664 | 1.1278 | 1.061 | 0.86098 | 0.7615 | 0.69725 | 0.68377 | 0.69801
43602.5335 | 0.93656 | 1.1245 | 1.0597 | 0.85826 | 0.76006 | 0.69664 | 0.68379 | 0.69779
43602.5335 | 0.94242 | 1.1248 | 1.0584 | 0.85895 | 0.75982 | 0.69653 | 0.68366 | 0.69778
43602.5335 | 0.9425 | 1.1247 | 1.0585 | 0.8586 | 0.75965 | 0.69677 | 0.68868 | 0.69801
43602.5335 | 0.94229 | 1.124 | 1.0578 | 0.85829 | 0.76021 | 0.69696 | 0.6867 | 0.69827
43602.5335 | 0.93712 | 1.118 | 1.0535 | 0.85532 | 0.75717 | 0.69468 | 0.68305 | 0.69755
43602.5337 | 0.94 | 1.1186 | 1.0522 | 0.85593 | 0.75835 | 0.6953 | 0.68343 | 0.69822
43602.5337 | 0.93539 | 1.1134 | 1.0489 | 0.85251 | 0.7561 | 0.69347 | 0.68219 | 0.69713
43602.5337 | 0.93632 | 1.1135 | 1.0487 | 0.85265 | 0.75473 | 0.69278 | 0.68098 | 0.69705
43602.5337 | 0.93269 | 1.116 | 1.05 | 0.85419 | 0.75543 | 0.69298 | 0.68363 | 0.69705
43602.5337 | 0.93009 | 1.1098 | 1.046 | 0.85145 | 0.75415 | 0.69208 | 0.68115 | 0.69671
43602.5339 | 0.93179 | 1.1081 | 1.043 | 0.84988 | 0.75242 | 0.69107 | 0.6816 | 0.69617
43602.5339 | 0.92835 | 1.1083 | 1.0449 | 0.85012 | 0.75174 | 0.69049 | 0.67973 | 0.69596
43602.5339 | 0.93901 | 1.1125 | 1.045 | 0.8518 | 0.75293 | 0.69159 | 0.68062 | 0.69678
43602.5338 | 0.92959 | 1.1091 | 1.0452 | 0.85078 | 0.75325 | 0.69091 | 0.68047 | 0.69596
43602.534 | 0.93744 | 1.113 | 1.0463 | 0.85224 | 0.75319 | 0.69023 | 0.67936 | 0.69479
43602.534 | 0.94285 | 1.1132 | 1.0464 | 0.85237 | 0.75405 | 0.69105 | 0.67961 | 0.69522
43602.534 | 0.94035 | 1.1147 | 1.0473 | 0.85223 | 0.75268 | 0.69016 | 0.67829 | 0.69449
43602.534 | 0.95522 | 1.121 | 1.0503 | 0.85557 | 0.75526 | 0.69198 | 0.67915 | 0.69526
43602.534 | 0.956 | 1.1225 | 1.0533 | 0.85701 | 0.75627 | 0.69232 | 0.68123 | 0.69426
43602.5342 | 0.9557 | 1.1253 | 1.0564 | 0.85825 | 0.75885 | 0.69446 | 0.68192 | 0.69434
43602.5342 | 0.96276 | 1.1269 | 1.0569 | 0.85848 | 0.75739 | 0.69352 | 0.68065 | 0.69406
43602.5342 | 0.96346 | 1.1298 | 1.0593 | 0.86084 | 0.75922 | 0.69468 | 0.68584 | 0.69436
43602.5342 | 0.95734 | 1.1285 | 1.0586 | 0.86004 | 0.76023 | 0.6955 | 0.6841 | 0.69479
43602.5342 | 0.96528 | 1.1333 | 1.0625 | 0.86254 | 0.76199 | 0.69659 | 0.68461 | 0.69494
43602.5344 | 0.95634 | 1.1335 | 1.0655 | 0.8623 | 0.76487 | 0.69883 | 0.68936 | 0.69556
43602.5344 | 0.96378 | 1.1343 | 1.0647 | 0.86303 | 0.76113 | 0.69605 | 0.68368 | 0.69409
43602.5344 | 0.97632 | 1.1394 | 1.0675 | 0.86591 | 0.76214 | 0.69687 | 0.68372 | 0.69481
43602.5344 | 0.97106 | 1.1379 | 1.0677 | 0.86521 | 0.76442 | 0.69852 | 0.6851 | 0.6955
43602.5345 | 0.95669 | 1.1359 | 1.0678 | 0.86366 | 0.76145 | 0.69713 | 0.68498 | 0.69536
43602.5345 | 0.96072 | 1.1369 | 1.0679 | 0.86481 | 0.7634 | 0.69834 | 0.68491 | 0.69635
43602.5345 | 0.95717 | 1.1358 | 1.0673 | 0.86316 | 0.76153 | 0.69695 | 0.68362 | 0.69541
43602.5345 | 0.95836 | 1.1362 | 1.0667 | 0.86381 | 0.76308 | 0.69778 | 0.68438 | 0.69629
43602.5347 | 0.93892 | 1.1212 | 1.0564 | 0.85393 | 0.75548 | 0.69267 | 0.68099 | 0.69511
43602.5347 | 0.93822 | 1.1212 | 1.0567 | 0.85455 | 0.75379 | 0.69167 | 0.68064 | 0.69466
43602.5347 | 0.93057 | 1.1208 | 1.0576 | 0.85546 | 0.75565 | 0.69266 | 0.68074 | 0.69526
43602.5347 | 0.93229 | 1.1162 | 1.0547 | 0.85126 | 0.75332 | 0.69151 | 0.67998 | 0.69452
43602.5347 | 0.93496 | 1.1161 | 1.0523 | 0.85111 | 0.75164 | 0.68981 | 0.67758 | 0.69404
43602.5349 | 0.93003 | 1.1134 | 1.0513 | 0.85048 | 0.74967 | 0.68844 | 0.67711 | 0.69339
43602.5349 | 0.93112 | 1.1132 | 1.0502 | 0.84986 | 0.75113 | 0.68919 | 0.67731 | 0.69371
43602.5349 | 0.93044 | 1.1115 | 1.0503 | 0.84819 | 0.74983 | 0.68846 | 0.6758 | 0.69316
43602.5349 | 0.92837 | 1.1116 | 1.0495 | 0.84859 | 0.7491 | 0.68798 | 0.67636 | 0.69314
43602.5348 | 0.9299 | 1.1132 | 1.0507 | 0.84948 | 0.74968 | 0.68775 | 0.6747 | 0.69259
43602.535 | 0.93851 | 1.1221 | 1.0557 | 0.85457 | 0.7542 | 0.69028 | 0.67791 | 0.69283
43602.535 | 0.94017 | 1.1204 | 1.054 | 0.85255 | 0.75364 | 0.69017 | 0.67867 | 0.69265
43602.5351 | 0.93836 | 1.1179 | 1.0526 | 0.85039 | 0.75127 | 0.68829 | 0.67547 | 0.69195
43602.5351 | 0.94574 | 1.1205 | 1.0529 | 0.85283 | 0.75189 | 0.68903 | 0.67669 | 0.69235
43602.535 | 0.94855 | 1.1223 | 1.0536 | 0.85421 | 0.75324 | 0.68957 | 0.67703 | 0.69234
43602.5352 | 0.94274 | 1.118 | 1.0504 | 0.85269 | 0.75253 | 0.68887 | 0.67733 | 0.69221
43602.5352 | 0.93693 | 1.1136 | 1.0485 | 0.84957 | 0.75205 | 0.68875 | 0.67614 | 0.69218
43602.5352 | 0.94217 | 1.1125 | 1.046 | 0.8493 | 0.7487 | 0.68678 | 0.67563 | 0.69125
43602.5352 | 0.94579 | 1.1161 | 1.0481 | 0.85162 | 0.75179 | 0.6885 | 0.67541 | 0.69233
43602.5354 | 0.93673 | 1.1048 | 1.0388 | 0.84572 | 0.74552 | 0.68449 | 0.67607 | 0.69106
43602.5354 | 0.9402 | 1.1067 | 1.0395 | 0.84679 | 0.74769 | 0.68557 | 0.67481 | 0.69159
43602.5354 | 0.93005 | 1.1023 | 1.0365 | 0.84327 | 0.74685 | 0.68486 | 0.67266 | 0.69119
43602.5354 | 0.92667 | 1.1012 | 1.0353 | 0.84325 | 0.7452 | 0.68387 | 0.67154 | 0.69074
43602.5354 | 0.92409 | 1.0936 | 1.0289 | 0.83869 | 0.74258 | 0.68169 | 0.67102 | 0.69002
43602.5355 | 0.92998 | 1.0955 | 1.0291 | 0.84058 | 0.74315 | 0.68223 | 0.6708 | 0.69046
43602.5356 | 0.91902 | 1.0883 | 1.0239 | 0.83559 | 0.74045 | 0.68042 | 0.66883 | 0.68933
43602.5356 | 0.92049 | 1.0905 | 1.0243 | 0.83664 | 0.73806 | 0.67863 | 0.66843 | 0.68885
43602.5356 | 0.92549 | 1.091 | 1.0243 | 0.83736 | 0.74013 | 0.67999 | 0.66904 | 0.68993
43602.5355 | 0.91934 | 1.0814 | 1.0158 | 0.83181 | 0.73584 | 0.6767 | 0.66616 | 0.68834
43602.5357 | 0.92407 | 1.0826 | 1.0149 | 0.83314 | 0.7352 | 0.67617 | 0.66523 | 0.68801
43602.5357 | 0.92009 | 1.0804 | 1.0139 | 0.83208 | 0.73494 | 0.67604 | 0.66588 | 0.68788
43602.5357 | 0.92751 | 1.082 | 1.0141 | 0.83233 | 0.73652 | 0.6771 | 0.66591 | 0.68847
43602.5358 | 0.9209 | 1.0769 | 1.0108 | 0.82978 | 0.73371 | 0.67489 | 0.66825 | 0.68725
43602.5357 | 0.92125 | 1.0783 | 1.0094 | 0.82951 | 0.73359 | 0.67484 | 0.66511 | 0.68714
43602.5359 | 0.93193 | 1.0767 | 1.0074 | 0.82901 | 0.73316 | 0.67481 | 0.66603 | 0.68697
43602.5359 | 0.92468 | 1.0783 | 1.009 | 0.83063 | 0.73368 | 0.67531 | 0.66524 | 0.68699
43602.5359 | 0.91846 | 1.0716 | 1.0036 | 0.82629 | 0.73103 | 0.67319 | 0.6635 | 0.68596
43602.5359 | 0.94542 | 1.0803 | 1.0096 | 0.83128 | 0.73278 | 0.67442 | 0.66463 | 0.68677
43602.5359 | 0.92119 | 1.0741 | 1.005 | 0.82838 | 0.73352 | 0.67494 | 0.66435 | 0.68695
43602.5361 | 0.93421 | 1.0745 | 1.0041 | 0.82825 | 0.73304 | 0.6744 | 0.66646 | 0.68648
43602.5361 | 0.93088 | 1.0686 | 0.99938 | 0.82475 | 0.72945 | 0.67207 | 0.66185 | 0.68583
43602.5361 | 0.94328 | 1.0791 | 1.0071 | 0.83095 | 0.73276 | 0.67446 | 0.66504 | 0.68676
43602.5361 | 0.9448 | 1.0765 | 1.0044 | 0.82873 | 0.73444 | 0.67546 | 0.66848 | 0.68663
43602.5362 | 0.94057 | 1.0767 | 1.0053 | 0.82937 | 0.73708 | 0.67733 | 0.66816 | 0.6876
43602.5362 | 0.93947 | 1.0865 | 1.0146 | 0.83614 | 0.73863 | 0.67925 | 0.66936 | 0.68829
43602.5363 | 0.92931 | 1.0756 | 1.0067 | 0.82969 | 0.73511 | 0.67656 | 0.6672 | 0.68732
43602.5363 | 0.94155 | 1.0777 | 1.0068 | 0.83064 | 0.73628 | 0.67779 | 0.66784 | 0.68793
43602.5362 | 0.94673 | 1.0797 | 1.0077 | 0.83217 | 0.73565 | 0.67738 | 0.67122 | 0.68911
43602.5364 | 0.93105 | 1.0715 | 1.0018 | 0.82837 | 0.73144 | 0.67426 | 0.66737 | 0.68864
43602.5364 | 0.94213 | 1.0784 | 1.006 | 0.83159 | 0.73476 | 0.67678 | 0.66739 | 0.68955
43602.5364 | 0.92754 | 1.0715 | 1.0022 | 0.828 | 0.73411 | 0.67613 | 0.66667 | 0.68919
43602.5365 | 0.91934 | 1.0681 | 1.0006 | 0.82661 | 0.73099 | 0.67426 | 0.66474 | 0.68897
43602.5364 | 0.92272 | 1.072 | 1.0042 | 0.82957 | 0.73438 | 0.67661 | 0.66766 | 0.69038
43602.5366 | 0.90983 | 1.0665 | 1.001 | 0.82681 | 0.73309 | 0.67589 | 0.66714 | 0.69036
43602.5366 | 0.91382 | 1.0654 | 1.0002 | 0.82615 | 0.73057 | 0.6739 | 0.66752 | 0.68942
43602.5366 | 0.90211 | 1.0659 | 1.001 | 0.82724 | 0.73274 | 0.67509 | 0.6659 | 0.69023
43602.5366 | 0.91102 | 1.0648 | 0.99985 | 0.82647 | 0.73126 | 0.67418 | 0.66533 | 0.68989
43602.5366 | 0.89297 | 1.0554 | 0.99459 | 0.82222 | 0.72693 | 0.6718 | 0.66258 | 0.69007
43602.5368 | 0.88909 | 1.0531 | 0.99377 | 0.82054 | 0.72757 | 0.67196 | 0.66351 | 0.69006
43602.5368 | 0.88431 | 1.0499 | 0.99215 | 0.81942 | 0.72545 | 0.67075 | 0.66234 | 0.68973
43602.5368 | 0.89381 | 1.0553 | 0.99459 | 0.82239 | 0.72695 | 0.67166 | 0.66376 | 0.69026
43602.5368 | 0.89782 | 1.0562 | 0.99538 | 0.82293 | 0.72917 | 0.67295 | 0.66631 | 0.69101
43602.5369 | 0.89606 | 1.0582 | 0.99667 | 0.82315 | 0.72789 | 0.67245 | 0.66586 | 0.6908
43602.5369 | 0.88562 | 1.0554 | 0.99748 | 0.82283 | 0.72814 | 0.67216 | 0.6636 | 0.69001
43602.537 | 0.89998 | 1.06 | 0.9984 | 0.82409 | 0.72967 | 0.67333 | 0.66488 | 0.69091
43602.5369 | 0.87679 | 1.0531 | 0.99726 | 0.82111 | 0.72764 | 0.67222 | 0.66235 | 0.69
43602.5371 | 0.88807 | 1.0593 | 0.99974 | 0.82429 | 0.72949 | 0.67291 | 0.66479 | 0.69051
43602.5371 | 0.88441 | 1.0583 | 0.99978 | 0.82379 | 0.7285 | 0.67232 | 0.66369 | 0.6899
43602.5371 | 0.88449 | 1.0564 | 0.99939 | 0.82299 | 0.72874 | 0.67289 | 0.66375 | 0.69038
43602.5371 | 0.89303 | 1.0589 | 0.99928 | 0.82373 | 0.72788 | 0.67214 | 0.66619 | 0.68994
43602.5371 | 0.88305 | 1.0535 | 0.99664 | 0.82107 | 0.72573 | 0.67029 | 0.66185 | 0.68965
43602.5373 | 0.87572 | 1.0498 | 0.99527 | 0.81863 | 0.72458 | 0.66995 | 0.66174 | 0.68966
43602.5373 | 0.87716 | 1.0504 | 0.99493 | 0.81965 | 0.72469 | 0.6697 | 0.66195 | 0.69
43602.5373 | 0.87562 | 1.0509 | 0.9949 | 0.81945 | 0.72414 | 0.66954 | 0.66054 | 0.68961
43602.5373 | 0.88323 | 1.0551 | 0.99691 | 0.82112 | 0.72508 | 0.67012 | 0.66164 | 0.68993
43602.5373 | 0.8769 | 1.0506 | 0.99503 | 0.81879 | 0.72427 | 0.66921 | 0.6616 | 0.68897
43602.5375 | 0.87274 | 1.0495 | 0.99576 | 0.81857 | 0.72388 | 0.66906 | 0.66305 | 0.68845
43602.5375 | 0.87662 | 1.0505 | 0.99565 | 0.81836 | 0.72365 | 0.66885 | 0.66095 | 0.68878
43602.5375 | 0.88081 | 1.0539 | 0.99768 | 0.82037 | 0.72468 | 0.66935 | 0.66056 | 0.6885
43602.5375 | 0.88795 | 1.0564 | 0.99847 | 0.82209 | 0.72573 | 0.66995 | 0.66085 | 0.68878
43602.5374 | 0.89811 | 1.07 | 1.0098 | 0.82845 | 0.72986 | 0.67259 | 0.66832 | 0.6887
43602.5376 | 0.90864 | 1.0836 | 1.0218 | 0.83631 | 0.73543 | 0.67654 | 0.66545 | 0.68967
43602.5376 | 0.91145 | 1.0858 | 1.0237 | 0.83693 | 0.73866 | 0.67873 | 0.67036 | 0.69078
43602.5377 | 0.91126 | 1.0853 | 1.0242 | 0.83613 | 0.73705 | 0.67821 | 0.6699 | 0.68989
43602.5377 | 0.92856 | 1.0939 | 1.0279 | 0.84078 | 0.73981 | 0.67975 | 0.66899 | 0.69099
43602.5376 | 0.90942 | 1.0885 | 1.0285 | 0.83854 | 0.7402 | 0.68142 | 0.67013 | 0.69133
43602.5378 | 0.90065 | 1.0786 | 1.0223 | 0.83412 | 0.73677 | 0.67992 | 0.66979 | 0.69192
43602.5378 | 0.89099 | 1.0742 | 1.0208 | 0.83119 | 0.73595 | 0.67905 | 0.67086 | 0.69208
43602.5378 | 0.8891 | 1.0693 | 1.0173 | 0.82886 | 0.7342 | 0.67814 | 0.66773 | 0.69171
43602.5378 | 0.88663 | 1.0675 | 1.0165 | 0.8287 | 0.73329 | 0.67747 | 0.66685 | 0.69193
43602.538 | 0.85955 | 1.0428 | 0.99817 | 0.81888 | 0.72559 | 0.67218 | 0.66375 | 0.69205
43602.538 | 0.86 | 1.0417 | 0.9965 | 0.81769 | 0.72505 | 0.67138 | 0.66319 | 0.69202
43602.538 | 0.85365 | 1.0389 | 0.99456 | 0.81668 | 0.72389 | 0.67058 | 0.66435 | 0.69181
43602.538 | 0.85999 | 1.0392 | 0.99361 | 0.81682 | 0.72362 | 0.67056 | 0.66598 | 0.69198
43602.538 | 0.85547 | 1.028 | 0.9823 | 0.81069 | 0.71896 | 0.66722 | 0.65957 | 0.69122
43602.5382 | 0.83835 | 1.0147 | 0.97419 | 0.80472 | 0.71431 | 0.66351 | 0.66029 | 0.68999
43602.5382 | 0.83565 | 1.0134 | 0.97372 | 0.8052 | 0.71332 | 0.66291 | 0.65612 | 0.68948
43602.5382 | 0.83482 | 1.0136 | 0.97333 | 0.8038 | 0.71301 | 0.66238 | 0.65532 | 0.68934
43602.5381 | 0.82528 | 1.0101 | 0.97289 | 0.80311 | 0.71159 | 0.66163 | 0.6538 | 0.68873
43602.5383 | 0.84555 | 1.02 | 0.97825 | 0.80476 | 0.70996 | 0.65882 | 0.64996 | 0.6856
43602.5383 | 0.84406 | 1.0212 | 0.98072 | 0.806 | 0.71103 | 0.65905 | 0.64987 | 0.68545
43602.5383 | 0.84354 | 1.0223 | 0.98181 | 0.80644 | 0.71048 | 0.65871 | 0.65007 | 0.68474
43602.5383 | 0.85335 | 1.0289 | 0.98551 | 0.80841 | 0.71224 | 0.65982 | 0.65423 | 0.68461
43602.5385 | 0.88663 | 1.0635 | 1.013 | 0.82224 | 0.7224 | 0.66528 | 0.65551 | 0.68332
43602.5385 | 0.88625 | 1.0647 | 1.0145 | 0.82424 | 0.72388 | 0.66638 | 0.65566 | 0.68325
43602.5385 | 0.88066 | 1.0656 | 1.0171 | 0.82373 | 0.72439 | 0.66695 | 0.65578 | 0.68351
43602.5384 | 0.88837 | 1.0708 | 1.0205 | 0.82585 | 0.72613 | 0.66897 | 0.65806 | 0.68396
43602.5386 | 0.93305 | 1.1083 | 1.0447 | 0.84591 | 0.74159 | 0.67916 | 0.66737 | 0.68567
43602.5386 | 0.93017 | 1.1067 | 1.044 | 0.84501 | 0.74344 | 0.68048 | 0.66837 | 0.68616
43602.5386 | 0.92883 | 1.1061 | 1.0443 | 0.84446 | 0.74199 | 0.67999 | 0.66718 | 0.68575
43602.5386 | 0.96838 | 1.1221 | 1.0526 | 0.85418 | 0.74754 | 0.6836 | 0.67169 | 0.68762
43602.5386 | 0.9493 | 1.1153 | 1.0482 | 0.85134 | 0.74697 | 0.68504 | 0.6722 | 0.68817
43602.5388 | 0.92927 | 1.1056 | 1.0428 | 0.84564 | 0.74549 | 0.68443 | 0.67269 | 0.68932
43602.5388 | 0.92477 | 1.1049 | 1.0429 | 0.84613 | 0.7451 | 0.68456 | 0.67268 | 0.68931
43602.5388 | 0.93042 | 1.1059 | 1.0433 | 0.84731 | 0.74655 | 0.68543 | 0.673 | 0.69008
43602.5388 | 0.92824 | 1.1039 | 1.0425 | 0.84541 | 0.74618 | 0.68556 | 0.67211 | 0.69043
43602.5389 | 0.90758 | 1.0858 | 1.0304 | 0.83584 | 0.73994 | 0.6832 | 0.67166 | 0.69192
43602.539 | 0.90688 | 1.0875 | 1.0308 | 0.83959 | 0.74113 | 0.68333 | 0.6761 | 0.69233
43602.5389 | 0.89273 | 1.0765 | 1.0249 | 0.8327 | 0.73847 | 0.68175 | 0.6714 | 0.69238
43602.5392 | 0.88323 | 1.0635 | 1.0159 | 0.82767 | 0.73183 | 0.67646 | 0.66519 | 0.69068
43602.5392 | 0.88013 | 1.0628 | 1.0156 | 0.82657 | 0.73145 | 0.67599 | 0.66632 | 0.69019
43602.5392 | 0.88576 | 1.0687 | 1.0218 | 0.83022 | 0.73301 | 0.6771 | 0.66667 | 0.69014
43602.5393 | 0.90324 | 1.0913 | 1.0406 | 0.83941 | 0.74091 | 0.68201 | 0.66952 | 0.69011
43602.5393 | 0.90688 | 1.0923 | 1.0408 | 0.83961 | 0.74118 | 0.68244 | 0.67009 | 0.69013
43602.5394 | 0.9165 | 1.0993 | 1.0443 | 0.8425 | 0.7424 | 0.68278 | 0.66962 | 0.69009
43602.5394 | 0.91281 | 1.0997 | 1.0461 | 0.84378 | 0.74372 | 0.68355 | 0.67566 | 0.69012
43602.5393 | 0.93052 | 1.1157 | 1.0591 | 0.84954 | 0.74999 | 0.68778 | 0.67974 | 0.69064
43602.5395 | 0.93939 | 1.1265 | 1.0658 | 0.8589 | 0.75421 | 0.69112 | 0.678 | 0.69182
43602.5395 | 0.93686 | 1.1239 | 1.0654 | 0.85573 | 0.75518 | 0.69174 | 0.67871 | 0.69194
43602.5395 | 0.93387 | 1.1208 | 1.064 | 0.85389 | 0.75313 | 0.69102 | 0.67831 | 0.69152
43602.5395 | 0.93833 | 1.1243 | 1.065 | 0.85622 | 0.75395 | 0.69144 | 0.67886 | 0.69191
43602.5397 | 0.9403 | 1.1253 | 1.0659 | 0.85753 | 0.75688 | 0.69385 | 0.68355 | 0.69303
43602.5397 | 0.94115 | 1.1231 | 1.0647 | 0.85527 | 0.75639 | 0.69341 | 0.68393 | 0.69298
43602.5397 | 0.93745 | 1.123 | 1.0657 | 0.85627 | 0.75556 | 0.69322 | 0.68116 | 0.69294
43602.5397 | 0.94376 | 1.1277 | 1.0672 | 0.85988 | 0.75745 | 0.69449 | 0.6821 | 0.69352
43602.5398 | 0.93772 | 1.1217 | 1.0634 | 0.85613 | 0.75706 | 0.69405 | 0.6816 | 0.69403
43602.5398 | 0.93823 | 1.1221 | 1.0648 | 0.85566 | 0.75638 | 0.69395 | 0.68101 | 0.69401
43602.5398 | 0.93566 | 1.1227 | 1.0651 | 0.85596 | 0.75601 | 0.69375 | 0.68095 | 0.69385
43602.5398 | 0.94062 | 1.124 | 1.0643 | 0.8567 | 0.75697 | 0.69434 | 0.6862 | 0.69455
43602.54 | 0.93764 | 1.1265 | 1.0696 | 0.85908 | 0.75878 | 0.6962 | 0.68387 | 0.69494
43602.54 | 0.94233 | 1.1293 | 1.071 | 0.86086 | 0.76041 | 0.69709 | 0.68358 | 0.69581
43602.54 | 0.94336 | 1.1281 | 1.07 | 0.8591 | 0.75961 | 0.69696 | 0.68342 | 0.69529
43602.54 | 0.94183 | 1.1275 | 1.0703 | 0.8597 | 0.75989 | 0.697 | 0.68691 | 0.69554
43602.5401 | 0.94536 | 1.1303 | 1.0705 | 0.86218 | 0.76009 | 0.69654 | 0.68372 | 0.69571
43602.5401 | 0.94075 | 1.1257 | 1.0694 | 0.85888 | 0.76051 | 0.69694 | 0.6843 | 0.69559
43602.5401 | 0.93451 | 1.1257 | 1.0713 | 0.85798 | 0.75947 | 0.69652 | 0.68489 | 0.69532
43602.5401 | 0.937 | 1.1262 | 1.0695 | 0.85889 | 0.75878 | 0.6964 | 0.68854 | 0.69527
43602.5403 | 0.93676 | 1.1267 | 1.0709 | 0.85905 | 0.75905 | 0.69607 | 0.68317 | 0.69524
43602.5403 | 0.93733 | 1.1271 | 1.0724 | 0.85931 | 0.75968 | 0.69645 | 0.68371 | 0.69539
43602.5403 | 0.93738 | 1.1306 | 1.0741 | 0.8618 | 0.76005 | 0.69673 | 0.68453 | 0.69541
43602.5403 | 0.94759 | 1.1331 | 1.0755 | 0.8618 | 0.76237 | 0.69801 | 0.68397 | 0.69569
43602.5404 | 0.95259 | 1.138 | 1.0797 | 0.86411 | 0.76335 | 0.69849 | 0.68455 | 0.69584
43602.5404 | 0.95331 | 1.1393 | 1.0798 | 0.86326 | 0.76347 | 0.69875 | 0.68535 | 0.6956
43602.5405 | 0.95154 | 1.1401 | 1.0809 | 0.8651 | 0.76404 | 0.69916 | 0.687 | 0.69579
43602.5404 | 0.95534 | 1.1431 | 1.0837 | 0.86641 | 0.76543 | 0.69972 | 0.68854 | 0.69621
43602.5406 | 0.96259 | 1.15 | 1.0887 | 0.87101 | 0.76927 | 0.7033 | 0.68989 | 0.69702
43602.5406 | 0.96342 | 1.1502 | 1.0898 | 0.87121 | 0.76916 | 0.7031 | 0.68979 | 0.69684
43602.5406 | 0.9697 | 1.1533 | 1.0905 | 0.87309 | 0.77033 | 0.70383 | 0.68987 | 0.69722
43602.5406 | 0.96525 | 1.1535 | 1.0923 | 0.87339 | 0.77076 | 0.70444 | 0.68918 | 0.69755
43602.5407 | 0.9705 | 1.1601 | 1.0952 | 0.87792 | 0.77373 | 0.70653 | 0.69242 | 0.69863
43602.5407 | 0.96059 | 1.1539 | 1.0941 | 0.87342 | 0.77362 | 0.70647 | 0.69262 | 0.69868
43602.5408 | 0.9656 | 1.1545 | 1.0928 | 0.87352 | 0.77145 | 0.70577 | 0.69167 | 0.69886
43602.5407 | 0.96829 | 1.1569 | 1.0942 | 0.87532 | 0.77297 | 0.70638 | 0.69281 | 0.69937
43602.5409 | 0.96567 | 1.155 | 1.0951 | 0.87477 | 0.77344 | 0.70732 | 0.69368 | 0.69985
43602.5409 | 0.96624 | 1.1549 | 1.0949 | 0.87451 | 0.77316 | 0.7071 | 0.69333 | 0.69982
43602.5409 | 0.96868 | 1.1567 | 1.0958 | 0.87469 | 0.77369 | 0.70765 | 0.69318 | 0.70013
43602.5409 | 0.96864 | 1.1561 | 1.0941 | 0.87551 | 0.77371 | 0.70769 | 0.69351 | 0.70004
43602.541 | 0.96797 | 1.161 | 1.1008 | 0.87699 | 0.77522 | 0.70893 | 0.695 | 0.70055
43602.5411 | 0.97086 | 1.1631 | 1.1018 | 0.87957 | 0.77621 | 0.70969 | 0.69535 | 0.70065
43602.5411 | 0.96646 | 1.1643 | 1.1042 | 0.88097 | 0.77772 | 0.71002 | 0.69596 | 0.70083
43602.541 | 0.96659 | 1.1607 | 1.1018 | 0.8774 | 0.77682 | 0.70998 | 0.69507 | 0.70061
43602.5412 | 0.9783 | 1.1698 | 1.1093 | 0.8819 | 0.77945 | 0.7119 | 0.69751 | 0.70147
43602.5412 | 0.97629 | 1.1701 | 1.1094 | 0.88243 | 0.77967 | 0.71196 | 0.69712 | 0.70167
43602.5412 | 0.97096 | 1.1654 | 1.1084 | 0.87998 | 0.77939 | 0.712 | 0.69788 | 0.7015
43602.5412 | 0.97255 | 1.1668 | 1.1087 | 0.88041 | 0.77867 | 0.71175 | 0.69729 | 0.70169
43602.5413 | 0.97958 | 1.1738 | 1.1138 | 0.88433 | 0.78191 | 0.71438 | 0.70008 | 0.70246
43602.5414 | 0.98527 | 1.1757 | 1.115 | 0.88431 | 0.78286 | 0.71494 | 0.69954 | 0.70266
43602.5414 | 0.98364 | 1.1753 | 1.1151 | 0.88521 | 0.78226 | 0.71436 | 0.69941 | 0.70247
43602.5413 | 0.98401 | 1.1763 | 1.1164 | 0.88519 | 0.78348 | 0.71539 | 0.70003 | 0.70277
43602.5415 | 0.98917 | 1.1848 | 1.1233 | 0.89073 | 0.78726 | 0.71831 | 0.70313 | 0.70399
43602.5415 | 0.99068 | 1.185 | 1.124 | 0.89058 | 0.78748 | 0.71881 | 0.70322 | 0.70418
43602.5415 | 0.9905 | 1.1864 | 1.1248 | 0.89115 | 0.7882 | 0.71959 | 0.70353 | 0.70462
43602.5415 | 0.9888 | 1.1866 | 1.1255 | 0.89143 | 0.78887 | 0.7194 | 0.7042 | 0.70472
43602.5417 | 1.0015 | 1.1976 | 1.1343 | 0.89594 | 0.7928 | 0.72312 | 0.70546 | 0.70533
43602.5417 | 1.0043 | 1.2003 | 1.1356 | 0.89937 | 0.79479 | 0.72403 | 0.70933 | 0.70643
43602.5417 | 0.99923 | 1.1979 | 1.1362 | 0.89665 | 0.79489 | 0.72431 | 0.71288 | 0.70607
43602.5416 | 1.006 | 1.1994 | 1.1358 | 0.89757 | 0.79446 | 0.72428 | 0.7084 | 0.70589
43602.5418 | 0.99657 | 1.2023 | 1.1421 | 0.90197 | 0.79805 | 0.72693 | 0.71326 | 0.70738
43602.5418 | 1.0067 | 1.2047 | 1.1419 | 0.90233 | 0.79839 | 0.7275 | 0.71134 | 0.70735
43602.5418 | 1.0024 | 1.2035 | 1.1429 | 0.90134 | 0.79822 | 0.72725 | 0.71043 | 0.70691
43602.5418 | 1.0035 | 1.2042 | 1.1418 | 0.90305 | 0.79853 | 0.72742 | 0.71084 | 0.70737
43602.542 | 1.0138 | 1.2106 | 1.147 | 0.90313 | 0.80065 | 0.72868 | 0.71196 | 0.70776
43602.542 | 1.0098 | 1.2099 | 1.1477 | 0.90424 | 0.80083 | 0.72932 | 0.71221 | 0.70786
43602.542 | 1.0145 | 1.2106 | 1.148 | 0.90421 | 0.80076 | 0.72911 | 0.71466 | 0.70784
43602.542 | 1.0076 | 1.2099 | 1.1497 | 0.90521 | 0.80171 | 0.72974 | 0.7126 | 0.70831
43602.5421 | 1.0213 | 1.2184 | 1.1544 | 0.90646 | 0.80377 | 0.73161 | 0.71427 | 0.70861
43602.5421 | 1.0195 | 1.219 | 1.1543 | 0.9077 | 0.80339 | 0.73165 | 0.71306 | 0.70856
43602.5421 | 1.0143 | 1.2167 | 1.155 | 0.90663 | 0.80393 | 0.73166 | 0.71345 | 0.70849
43602.5421 | 1.0176 | 1.2175 | 1.155 | 0.90645 | 0.80309 | 0.73128 | 0.71371 | 0.70818
43602.5423 | 1.0258 | 1.2251 | 1.1627 | 0.90954 | 0.80512 | 0.73221 | 0.71396 | 0.70874
43602.5423 | 1.0283 | 1.226 | 1.1625 | 0.91035 | 0.80568 | 0.73294 | 0.71502 | 0.70832
43602.5423 | 1.0238 | 1.2285 | 1.1651 | 0.91241 | 0.80678 | 0.7332 | 0.71462 | 0.70879
43602.5423 | 1.023 | 1.2255 | 1.1646 | 0.91088 | 0.80674 | 0.73358 | 0.71596 | 0.70866
43602.5424 | 1.0318 | 1.2329 | 1.1705 | 0.91362 | 0.8088 | 0.7346 | 0.71603 | 0.70862
43602.5424 | 1.0256 | 1.2309 | 1.1712 | 0.91358 | 0.80911 | 0.73568 | 0.71641 | 0.70893
43602.5424 | 1.0271 | 1.2317 | 1.1707 | 0.9145 | 0.80894 | 0.73548 | 0.72108 | 0.70921
43602.5424 | 1.0294 | 1.231 | 1.1706 | 0.91292 | 0.80957 | 0.73602 | 0.71878 | 0.70961
43602.5426 | 1.03 | 1.2327 | 1.1716 | 0.91382 | 0.80932 | 0.73582 | 0.71778 | 0.70896
43602.5426 | 1.0291 | 1.2323 | 1.1717 | 0.91338 | 0.8094 | 0.73592 | 0.72061 | 0.70942
43602.5426 | 1.0246 | 1.2319 | 1.1723 | 0.91342 | 0.80897 | 0.73582 | 0.71793 | 0.70937
43602.5426 | 1.0326 | 1.2353 | 1.173 | 0.91524 | 0.80965 | 0.73626 | 0.71737 | 0.70954
43602.5427 | 1.0475 | 1.254 | 1.1897 | 0.92403 | 0.81748 | 0.74131 | 0.72169 | 0.70974
43602.5427 | 1.0516 | 1.2568 | 1.1921 | 0.92639 | 0.81878 | 0.74219 | 0.72431 | 0.71005
43602.5428 | 1.05 | 1.2603 | 1.1948 | 0.92813 | 0.81978 | 0.74297 | 0.72359 | 0.71005
43602.5427 | 1.0624 | 1.2644 | 1.1973 | 0.92942 | 0.82139 | 0.74375 | 0.7233 | 0.71042
43602.5429 | 1.0745 | 1.2798 | 1.2102 | 0.93865 | 0.82798 | 0.74935 | 0.72926 | 0.71175
43602.5429 | 1.0759 | 1.28 | 1.2118 | 0.94033 | 0.82985 | 0.75046 | 0.73131 | 0.71214
43602.5429 | 1.0699 | 1.2788 | 1.2118 | 0.93845 | 0.82933 | 0.75016 | 0.72956 | 0.71138
43602.5429 | 1.0688 | 1.2787 | 1.212 | 0.93897 | 0.82947 | 0.75096 | 0.72954 | 0.71227
43602.543 | 1.074 | 1.2782 | 1.2099 | 0.93662 | 0.82905 | 0.751 | 0.73111 | 0.71289
43602.5431 | 1.0676 | 1.2786 | 1.2118 | 0.93817 | 0.82927 | 0.75087 | 0.73047 | 0.71298
43602.5431 | 1.0668 | 1.2758 | 1.2101 | 0.93637 | 0.82936 | 0.75099 | 0.7303 | 0.7131
43602.543 | 1.064 | 1.2749 | 1.2103 | 0.93666 | 0.82858 | 0.75053 | 0.72976 | 0.71277
43602.5432 | 1.0659 | 1.2763 | 1.2101 | 0.93646 | 0.82983 | 0.7511 | 0.73066 | 0.7136
43602.5432 | 1.0685 | 1.2749 | 1.2107 | 0.9345 | 0.82973 | 0.75124 | 0.72983 | 0.71369
43602.5432 | 1.0609 | 1.2744 | 1.2118 | 0.93564 | 0.82939 | 0.75124 | 0.73008 | 0.71375
43602.5432 | 1.0697 | 1.2786 | 1.2113 | 0.93764 | 0.82968 | 0.75084 | 0.72969 | 0.71327
43602.5434 | 1.0654 | 1.2784 | 1.2147 | 0.93713 | 0.82973 | 0.75073 | 0.72952 | 0.71326
43602.5434 | 1.0693 | 1.2797 | 1.2149 | 0.93739 | 0.82973 | 0.75065 | 0.7292 | 0.71309
43602.5434 | 1.0736 | 1.2823 | 1.2153 | 0.93902 | 0.83085 | 0.75156 | 0.73336 | 0.71333
43602.5433 | 1.0743 | 1.2822 | 1.2164 | 0.93796 | 0.8301 | 0.75078 | 0.72967 | 0.71232
43602.5435 | 1.0867 | 1.2955 | 1.2273 | 0.94534 | 0.83527 | 0.75425 | 0.73245 | 0.71259
43602.5435 | 1.088 | 1.2961 | 1.227 | 0.94413 | 0.83467 | 0.75377 | 0.73155 | 0.71232
43602.5435 | 1.0884 | 1.2981 | 1.228 | 0.94684 | 0.83571 | 0.75476 | 0.73302 | 0.71307
43602.5435 | 1.0863 | 1.2992 | 1.2293 | 0.94825 | 0.8372 | 0.7558 | 0.73313 | 0.71298
43602.5437 | 1.1012 | 1.3064 | 1.2331 | 0.95045 | 0.83855 | 0.75632 | 0.73692 | 0.71262
43602.5437 | 1.0942 | 1.3035 | 1.2337 | 0.94906 | 0.83839 | 0.75623 | 0.73394 | 0.71202
43602.5437 | 1.0933 | 1.3054 | 1.2348 | 0.95006 | 0.83846 | 0.75642 | 0.73365 | 0.71232
43602.5437 | 1.1005 | 1.3078 | 1.2363 | 0.95272 | 0.8401 | 0.7576 | 0.73515 | 0.71283
43602.5438 | 1.1107 | 1.321 | 1.2486 | 0.96088 | 0.84767 | 0.76329 | 0.73968 | 0.71423
43602.5438 | 1.1183 | 1.3231 | 1.2484 | 0.96146 | 0.84777 | 0.76309 | 0.74188 | 0.71431
43602.5438 | 1.115 | 1.3237 | 1.2508 | 0.96271 | 0.84859 | 0.76347 | 0.74058 | 0.71394
43602.5438 | 1.1155 | 1.3253 | 1.2521 | 0.96467 | 0.85061 | 0.76528 | 0.74155 | 0.71529
43602.544 | 1.1163 | 1.3244 | 1.2534 | 0.96237 | 0.85065 | 0.76631 | 0.74495 | 0.71605
43602.544 | 1.1168 | 1.3256 | 1.2536 | 0.96362 | 0.85072 | 0.7662 | 0.74357 | 0.71613
43602.544 | 1.1136 | 1.3258 | 1.2552 | 0.96363 | 0.85096 | 0.76627 | 0.74279 | 0.71587
43602.544 | 1.1218 | 1.327 | 1.2546 | 0.96412 | 0.85066 | 0.76591 | 0.74246 | 0.7158
43602.5441 | 1.1169 | 1.3308 | 1.2628 | 0.9656 | 0.85413 | 0.76912 | 0.74534 | 0.7174
43602.5442 | 1.1196 | 1.332 | 1.2622 | 0.96595 | 0.85469 | 0.76968 | 0.74615 | 0.71856
43602.5442 | 1.1218 | 1.3323 | 1.2624 | 0.96626 | 0.85456 | 0.76923 | 0.74477 | 0.71746
43602.5441 | 1.1259 | 1.3317 | 1.2617 | 0.96547 | 0.8537 | 0.769 | 0.74524 | 0.71749
43602.5443 | 1.1114 | 1.3206 | 1.2544 | 0.95714 | 0.84826 | 0.76549 | 0.74184 | 0.71679
43602.5443 | 1.1107 | 1.3193 | 1.2534 | 0.95605 | 0.84718 | 0.76409 | 0.74056 | 0.71654
43602.5443 | 1.108 | 1.3182 | 1.253 | 0.95551 | 0.8464 | 0.76364 | 0.74006 | 0.71607
43602.5443 | 1.1084 | 1.3189 | 1.2526 | 0.95553 | 0.84621 | 0.76317 | 0.73884 | 0.71566
43602.5445 | 1.1223 | 1.3344 | 1.2652 | 0.96234 | 0.85116 | 0.76657 | 0.74457 | 0.7171
43602.5445 | 1.119 | 1.3355 | 1.2675 | 0.96341 | 0.85238 | 0.76746 | 0.74327 | 0.71707
43602.5445 | 1.1236 | 1.3396 | 1.2696 | 0.96574 | 0.85342 | 0.76818 | 0.74358 | 0.71728
43602.5444 | 1.1212 | 1.3403 | 1.2724 | 0.96758 | 0.8552 | 0.76933 | 0.7452 | 0.71771
43602.5446 | 1.1503 | 1.3653 | 1.2924 | 0.9809 | 0.86562 | 0.77733 | 0.75092 | 0.72033
43602.5446 | 1.1499 | 1.3659 | 1.2942 | 0.98234 | 0.8675 | 0.77867 | 0.75415 | 0.72089
43602.5446 | 1.1511 | 1.3675 | 1.2958 | 0.98265 | 0.8682 | 0.77889 | 0.75256 | 0.72104
43602.5446 | 1.1493 | 1.3682 | 1.2975 | 0.98369 | 0.86889 | 0.77978 | 0.7539 | 0.72102
43602.5448 | 1.1566 | 1.3784 | 1.3057 | 0.99031 | 0.87453 | 0.78441 | 0.75776 | 0.72264
43602.5448 | 1.1594 | 1.3809 | 1.3074 | 0.99199 | 0.87525 | 0.78488 | 0.76191 | 0.723
43602.5448 | 1.1649 | 1.3821 | 1.3073 | 0.99351 | 0.87619 | 0.78572 | 0.75933 | 0.72287
43602.5447 | 1.1625 | 1.3814 | 1.3076 | 0.99273 | 0.87631 | 0.78587 | 0.75876 | 0.72304
43602.5449 | 1.1676 | 1.3806 | 1.3073 | 0.99155 | 0.87592 | 0.78559 | 0.75923 | 0.7231
43602.5449 | 1.1677 | 1.3816 | 1.3079 | 0.99321 | 0.8768 | 0.78588 | 0.75997 | 0.72367
43602.5449 | 1.166 | 1.3808 | 1.3071 | 0.99189 | 0.8767 | 0.78604 | 0.7594 | 0.72311
43602.5449 | 1.1554 | 1.377 | 1.3068 | 0.99107 | 0.87655 | 0.78595 | 0.75949 | 0.72387
43602.5451 | 1.1586 | 1.3757 | 1.3053 | 0.98959 | 0.87511 | 0.78517 | 0.7587 | 0.72348
43602.5451 | 1.1583 | 1.3759 | 1.3049 | 0.98997 | 0.87499 | 0.78529 | 0.7587 | 0.72352
43602.5451 | 1.1563 | 1.3752 | 1.3053 | 0.99041 | 0.87531 | 0.78536 | 0.75963 | 0.72333
43602.5451 | 1.16 | 1.3768 | 1.3049 | 0.99109 | 0.87482 | 0.78496 | 0.76214 | 0.7232
43602.5452 | 1.1669 | 1.3819 | 1.3084 | 0.99299 | 0.87647 | 0.78603 | 0.75951 | 0.72369
43602.5452 | 1.1678 | 1.3817 | 1.3091 | 0.99306 | 0.87729 | 0.78616 | 0.7597 | 0.72387
43602.5453 | 1.1692 | 1.3836 | 1.3092 | 0.99556 | 0.87764 | 0.7865 | 0.75908 | 0.72325
43602.5452 | 1.1637 | 1.3822 | 1.3092 | 0.99403 | 0.87837 | 0.78729 | 0.7604 | 0.72366
43602.5454 | 1.175 | 1.3899 | 1.3135 | 0.99989 | 0.88191 | 0.78995 | 0.7629 | 0.72487
43602.5454 | 1.1754 | 1.3893 | 1.3141 | 0.99925 | 0.882 | 0.79 | 0.76247 | 0.72464
43602.5454 | 1.1827 | 1.3946 | 1.3164 | 1.0031 | 0.88323 | 0.79094 | 0.76409 | 0.72497
43602.5454 | 1.1832 | 1.3931 | 1.3176 | 1.0024 | 0.88477 | 0.79167 | 0.7679 | 0.725
43602.5455 | 1.1958 | 1.4087 | 1.3299 | 1.0132 | 0.8929 | 0.79851 | 0.77044 | 0.72697
43602.5456 | 1.1979 | 1.4095 | 1.3313 | 1.0141 | 0.89404 | 0.79902 | 0.77022 | 0.72707
43602.5456 | 1.1975 | 1.4094 | 1.3303 | 1.0139 | 0.89404 | 0.79939 | 0.7706 | 0.72752
43602.5455 | 1.1961 | 1.4077 | 1.3301 | 1.0127 | 0.89432 | 0.79947 | 0.77354 | 0.72743
43602.5457 | 1.1832 | 1.4014 | 1.3246 | 1.0091 | 0.89019 | 0.79697 | 0.76855 | 0.72687
43602.5457 | 1.1894 | 1.4003 | 1.3232 | 1.008 | 0.89039 | 0.79692 | 0.76941 | 0.72719
43602.5457 | 1.1789 | 1.3956 | 1.3212 | 1.004 | 0.88846 | 0.79556 | 0.76992 | 0.72643
43602.5457 | 1.1812 | 1.3957 | 1.3195 | 1.0044 | 0.88709 | 0.79441 | 0.76683 | 0.72653
43602.5459 | 1.1704 | 1.3858 | 1.3099 | 0.99681 | 0.88141 | 0.7901 | 0.76464 | 0.72484
43602.5459 | 1.1725 | 1.3861 | 1.3104 | 0.99692 | 0.88118 | 0.78906 | 0.76293 | 0.72445
43602.5459 | 1.1679 | 1.3842 | 1.3095 | 0.99628 | 0.88087 | 0.78961 | 0.76242 | 0.72479
43602.5458 | 1.1711 | 1.3834 | 1.308 | 0.99544 | 0.87987 | 0.78857 | 0.76148 | 0.72433
43602.546 | 1.1601 | 1.3772 | 1.302 | 0.99083 | 0.87558 | 0.78508 | 0.76113 | 0.72334
43602.546 | 1.1638 | 1.3785 | 1.3025 | 0.99218 | 0.87614 | 0.78566 | 0.7589 | 0.72327
43602.546 | 1.1676 | 1.378 | 1.302 | 0.99116 | 0.87592 | 0.78539 | 0.75853 | 0.72316
43602.546 | 1.1705 | 1.3805 | 1.3036 | 0.99328 | 0.87677 | 0.78555 | 0.75921 | 0.72285
43602.5462 | 1.186 | 1.3962 | 1.3156 | 1.0042 | 0.88401 | 0.7914 | 0.76385 | 0.72344
43602.5462 | 1.1847 | 1.3974 | 1.3173 | 1.0043 | 0.8854 | 0.79224 | 0.76364 | 0.72416
43602.5462 | 1.1898 | 1.3996 | 1.3184 | 1.0062 | 0.88572 | 0.79229 | 0.76439 | 0.72354
43602.5462 | 1.1924 | 1.4006 | 1.3199 | 1.0077 | 0.88792 | 0.79425 | 0.76657 | 0.72468
43602.5463 | 1.1972 | 1.4086 | 1.3265 | 1.0147 | 0.89421 | 0.79884 | 0.76989 | 0.72604
43602.5463 | 1.1959 | 1.4076 | 1.3264 | 1.0147 | 0.8936 | 0.79889 | 0.77064 | 0.7257
43602.5463 | 1.1947 | 1.4088 | 1.3266 | 1.015 | 0.8944 | 0.79933 | 0.77203 | 0.72603
43602.5463 | 1.1941 | 1.4052 | 1.3251 | 1.0126 | 0.893 | 0.79846 | 0.76901 | 0.72574
43602.5465 | 1.1839 | 1.3939 | 1.3154 | 1.0059 | 0.88705 | 0.79459 | 0.77002 | 0.72516
43602.5465 | 1.1886 | 1.3966 | 1.3154 | 1.0076 | 0.88782 | 0.79455 | 0.76767 | 0.72504
43602.5465 | 1.1837 | 1.3912 | 1.3117 | 1.0041 | 0.88602 | 0.79351 | 0.76671 | 0.72441
43602.5465 | 1.1764 | 1.3865 | 1.3095 | 1.0005 | 0.88361 | 0.79185 | 0.7647 | 0.72442
43602.5466 | 1.1607 | 1.3782 | 1.3016 | 0.99538 | 0.87684 | 0.78596 | 0.76213 | 0.72272
43602.5466 | 1.1699 | 1.3771 | 1.301 | 0.99387 | 0.87735 | 0.78655 | 0.76006 | 0.72237
43602.5467 | 1.1689 | 1.3778 | 1.3006 | 0.99413 | 0.87702 | 0.78622 | 0.75957 | 0.72259
43602.5466 | 1.1678 | 1.3772 | 1.3003 | 0.99376 | 0.87626 | 0.7858 | 0.75967 | 0.72238
43602.5468 | 1.1709 | 1.382 | 1.3041 | 0.99612 | 0.87792 | 0.7865 | 0.75921 | 0.72188
43602.5468 | 1.1728 | 1.3848 | 1.3057 | 0.99938 | 0.87872 | 0.78714 | 0.76381 | 0.72197
43602.5468 | 1.1738 | 1.3833 | 1.3046 | 0.99683 | 0.87949 | 0.78795 | 0.76147 | 0.72222
43602.5468 | 1.1778 | 1.387 | 1.3074 | 1 | 0.88092 | 0.78874 | 0.76216 | 0.7226
43602.547 | 1.1789 | 1.3908 | 1.3107 | 1.0031 | 0.88328 | 0.79016 | 0.76505 | 0.72299
43602.547 | 1.1765 | 1.3892 | 1.3108 | 1.0026 | 0.88345 | 0.7908 | 0.76375 | 0.72304
43602.547 | 1.1858 | 1.3915 | 1.3108 | 1.0035 | 0.88259 | 0.79028 | 0.76316 | 0.72309
43602.5469 | 1.1785 | 1.39 | 1.3106 | 1.003 | 0.88374 | 0.79096 | 0.76316 | 0.72285
43602.5471 | 1.1938 | 1.3983 | 1.3182 | 1.0101 | 0.88947 | 0.79537 | 0.76672 | 0.72473
43602.5471 | 1.1861 | 1.3972 | 1.317 | 1.0083 | 0.88871 | 0.79481 | 0.76842 | 0.72448
43602.5471 | 1.1895 | 1.3978 | 1.3168 | 1.0078 | 0.88774 | 0.79413 | 0.76939 | 0.72418
43602.5471 | 1.1927 | 1.3995 | 1.3175 | 1.0094 | 0.88839 | 0.79453 | 0.76694 | 0.72423
43602.5473 | 1.181 | 1.3883 | 1.3078 | 1.0013 | 0.88251 | 0.78975 | 0.76248 | 0.72281
43602.5473 | 1.181 | 1.3866 | 1.3067 | 1.0005 | 0.88174 | 0.78884 | 0.76189 | 0.72217
43602.5473 | 1.1789 | 1.3867 | 1.3064 | 1.0006 | 0.88094 | 0.78838 | 0.76264 | 0.72227
43602.5473 | 1.1757 | 1.3855 | 1.305 | 0.99968 | 0.88164 | 0.78861 | 0.76508 | 0.72249
43602.5474 | 1.1609 | 1.3701 | 1.291 | 0.99073 | 0.8732 | 0.78226 | 0.75591 | 0.7199
43602.5474 | 1.164 | 1.3692 | 1.2899 | 0.98966 | 0.87332 | 0.78218 | 0.75589 | 0.71966
43602.5475 | 1.1607 | 1.3666 | 1.2886 | 0.98899 | 0.872 | 0.78096 | 0.75452 | 0.71903
43602.5474 | 1.1596 | 1.366 | 1.2877 | 0.98805 | 0.87104 | 0.78064 | 0.7552 | 0.71895
43602.5476 | 1.1569 | 1.3597 | 1.2798 | 0.98493 | 0.86944 | 0.77889 | 0.75296 | 0.7177
43602.5476 | 1.1542 | 1.3601 | 1.2807 | 0.98681 | 0.86804 | 0.77796 | 0.75241 | 0.71737
43602.5476 | 1.1573 | 1.3593 | 1.2787 | 0.98551 | 0.86897 | 0.77894 | 0.7531 | 0.71759
43602.5476 | 1.1595 | 1.3581 | 1.2777 | 0.98566 | 0.86832 | 0.77789 | 0.75178 | 0.71699
43602.5477 | 1.1377 | 1.3488 | 1.2681 | 0.97997 | 0.86294 | 0.77428 | 0.75176 | 0.7152
43602.5478 | 1.1507 | 1.3493 | 1.2677 | 0.98161 | 0.86408 | 0.77465 | 0.75177 | 0.71575
43602.5478 | 1.1459 | 1.3486 | 1.2667 | 0.9804 | 0.86372 | 0.77427 | 0.74899 | 0.71507
43602.5477 | 1.1519 | 1.3481 | 1.2648 | 0.98106 | 0.86349 | 0.77374 | 0.74886 | 0.71493
43602.5479 | 1.1663 | 1.3488 | 1.2644 | 0.98287 | 0.86362 | 0.77457 | 0.7483 | 0.71404
43602.5479 | 1.1553 | 1.348 | 1.2649 | 0.98223 | 0.86474 | 0.77521 | 0.74962 | 0.71468
43602.5479 | 1.1594 | 1.3485 | 1.2646 | 0.98261 | 0.86488 | 0.77529 | 0.75345 | 0.71503
43602.5479 | 1.1598 | 1.3503 | 1.2663 | 0.98447 | 0.86553 | 0.77597 | 0.75124 | 0.71488
43602.5481 | 1.1752 | 1.3557 | 1.2698 | 0.98968 | 0.86959 | 0.77814 | 0.75212 | 0.71522
43602.5481 | 1.1724 | 1.3563 | 1.27 | 0.9892 | 0.86965 | 0.77859 | 0.75197 | 0.71517
43602.5481 | 1.1694 | 1.3566 | 1.2708 | 0.98962 | 0.87007 | 0.77861 | 0.75433 | 0.71532
43602.548 | 1.1841 | 1.3611 | 1.2733 | 0.99227 | 0.87232 | 0.78038 | 0.75663 | 0.71564
43602.5482 | 1.1902 | 1.3661 | 1.277 | 0.99574 | 0.87496 | 0.78213 | 0.75555 | 0.71602
43602.5482 | 1.1794 | 1.3655 | 1.2771 | 0.99478 | 0.87574 | 0.7829 | 0.75623 | 0.71639
43602.5482 | 1.1935 | 1.3718 | 1.2815 | 0.99866 | 0.87618 | 0.78376 | 0.75801 | 0.71704
43602.5482 | 1.1929 | 1.3704 | 1.2796 | 0.99723 | 0.87643 | 0.78369 | 0.75693 | 0.71696
43602.5484 | 1.1804 | 1.3684 | 1.2795 | 0.99621 | 0.87831 | 0.78489 | 0.75916 | 0.71808
43602.5484 | 1.1928 | 1.3705 | 1.2812 | 0.99779 | 0.8747 | 0.78218 | 0.7556 | 0.71701
43602.5484 | 1.1608 | 1.3648 | 1.2779 | 0.9932 | 0.8763 | 0.78378 | 0.75775 | 0.71759
43602.5484 | 1.1657 | 1.3646 | 1.2767 | 0.99284 | 0.87406 | 0.78252 | 0.75582 | 0.71756
43602.5485 | 1.1499 | 1.3501 | 1.2652 | 0.983 | 0.86471 | 0.77492 | 0.75044 | 0.71548
43602.5485 | 1.1597 | 1.3506 | 1.2657 | 0.98389 | 0.86554 | 0.7752 | 0.75006 | 0.7159
43602.5486 | 1.1505 | 1.3466 | 1.2621 | 0.98004 | 0.86309 | 0.77322 | 0.74854 | 0.71459
43602.5485 | 1.1584 | 1.3493 | 1.2649 | 0.98294 | 0.86296 | 0.77337 | 0.7501 | 0.71508
43602.5487 | 1.1364 | 1.342 | 1.2605 | 0.97699 | 0.86089 | 0.77119 | 0.74718 | 0.71455
43602.5487 | 1.1497 | 1.3455 | 1.2615 | 0.97872 | 0.86049 | 0.77183 | 0.74668 | 0.71512
43602.5487 | 1.1486 | 1.3436 | 1.2604 | 0.97746 | 0.86055 | 0.7708 | 0.74968 | 0.71414
43602.5487 | 1.1503 | 1.3446 | 1.2611 | 0.97848 | 0.86075 | 0.77095 | 0.74735 | 0.71448
43602.5488 | 1.1455 | 1.3438 | 1.2617 | 0.9776 | 0.86055 | 0.7711 | 0.74631 | 0.71411
43602.5489 | 1.1419 | 1.3436 | 1.2617 | 0.97708 | 0.85996 | 0.77073 | 0.74618 | 0.71467
43602.5489 | 1.1364 | 1.3423 | 1.2615 | 0.97666 | 0.86058 | 0.77102 | 0.74639 | 0.71456
43602.5488 | 1.1396 | 1.3414 | 1.2606 | 0.9763 | 0.8593 | 0.77081 | 0.74647 | 0.71475
43602.549 | 1.1361 | 1.3368 | 1.2566 | 0.9728 | 0.85494 | 0.76707 | 0.74233 | 0.71354
43602.549 | 1.1305 | 1.3377 | 1.2575 | 0.97332 | 0.85706 | 0.76861 | 0.74409 | 0.71444
43602.549 | 1.1301 | 1.3335 | 1.2542 | 0.9705 | 0.85397 | 0.7665 | 0.7419 | 0.71374
43602.549 | 1.1311 | 1.3354 | 1.2558 | 0.97121 | 0.85488 | 0.76689 | 0.74206 | 0.71397
43602.5492 | 1.1449 | 1.3427 | 1.2618 | 0.97488 | 0.85721 | 0.76915 | 0.74326 | 0.7143
43602.5492 | 1.1399 | 1.3416 | 1.2618 | 0.97461 | 0.85756 | 0.76882 | 0.74579 | 0.71411
43602.5492 | 1.1374 | 1.3438 | 1.2643 | 0.97642 | 0.85789 | 0.76959 | 0.74814 | 0.71443
43602.5491 | 1.1339 | 1.3415 | 1.2629 | 0.97457 | 0.85783 | 0.76958 | 0.74572 | 0.71444
43602.5493 | 1.1314 | 1.337 | 1.2599 | 0.97075 | 0.85514 | 0.76787 | 0.74507 | 0.71462
43602.5493 | 1.126 | 1.3362 | 1.2593 | 0.96792 | 0.85225 | 0.7661 | 0.74165 | 0.71362
43602.5493 | 1.13 | 1.3362 | 1.2592 | 0.96848 | 0.85207 | 0.76554 | 0.74135 | 0.7139
43602.5493 | 1.1277 | 1.3358 | 1.2587 | 0.96863 | 0.85174 | 0.76554 | 0.74185 | 0.7137
43602.5495 | 1.1196 | 1.326 | 1.2507 | 0.9609 | 0.84595 | 0.76107 | 0.73705 | 0.71288
43602.5495 | 1.1214 | 1.3278 | 1.2507 | 0.96071 | 0.84636 | 0.76162 | 0.73701 | 0.71297
43602.5495 | 1.1167 | 1.3248 | 1.2511 | 0.9597 | 0.84517 | 0.76038 | 0.73677 | 0.71242
43602.5495 | 1.1116 | 1.3235 | 1.2498 | 0.95849 | 0.84432 | 0.76006 | 0.73662 | 0.71269
43602.5496 | 1.112 | 1.3202 | 1.2466 | 0.95546 | 0.84261 | 0.75809 | 0.73408 | 0.7114
43602.5496 | 1.1109 | 1.3196 | 1.2464 | 0.95509 | 0.84118 | 0.75741 | 0.73377 | 0.71128
43602.5497 | 1.115 | 1.3224 | 1.2466 | 0.95723 | 0.84207 | 0.75805 | 0.73453 | 0.71157
43602.5496 | 1.1131 | 1.3207 | 1.2455 | 0.95523 | 0.8415 | 0.75754 | 0.73384 | 0.71118
43602.5498 | 1.1099 | 1.3191 | 1.244 | 0.9548 | 0.84054 | 0.75631 | 0.73241 | 0.71045
43602.5498 | 1.1131 | 1.3208 | 1.2437 | 0.95708 | 0.84112 | 0.75652 | 0.73285 | 0.7105
43602.5498 | 1.1105 | 1.3174 | 1.2423 | 0.95471 | 0.84096 | 0.75645 | 0.73233 | 0.70995
43602.5498 | 1.1102 | 1.3187 | 1.2428 | 0.95556 | 0.84074 | 0.75619 | 0.73341 | 0.71028
43602.55 | 1.1071 | 1.3129 | 1.2362 | 0.95356 | 0.83938 | 0.75488 | 0.73247 | 0.70921
43602.55 | 1.1091 | 1.3115 | 1.2353 | 0.9524 | 0.8382 | 0.75401 | 0.73065 | 0.70898
43602.55 | 1.104 | 1.3099 | 1.234 | 0.95101 | 0.837 | 0.75346 | 0.72971 | 0.7085
43602.5499 | 1.1066 | 1.3093 | 1.2322 | 0.95131 | 0.83657 | 0.75314 | 0.73128 | 0.70845
43602.5501 | 1.1048 | 1.3102 | 1.2325 | 0.95274 | 0.83704 | 0.75267 | 0.73029 | 0.7079
43602.5501 | 1.1072 | 1.3119 | 1.2336 | 0.95428 | 0.83905 | 0.75396 | 0.73014 | 0.70855
43602.5501 | 1.1052 | 1.3116 | 1.2341 | 0.95496 | 0.83894 | 0.75413 | 0.73236 | 0.70868
43602.5501 | 1.126 | 1.3186 | 1.238 | 0.95915 | 0.84232 | 0.75667 | 0.73345 | 0.70884
43602.5503 | 1.1146 | 1.3157 | 1.2369 | 0.95733 | 0.84354 | 0.75788 | 0.73429 | 0.70949
43602.5503 | 1.1172 | 1.3142 | 1.235 | 0.95668 | 0.84155 | 0.75646 | 0.73554 | 0.70895
43602.5503 | 1.1122 | 1.314 | 1.2347 | 0.95687 | 0.84111 | 0.75635 | 0.73347 | 0.7091
43602.5503 | 1.1168 | 1.3106 | 1.2322 | 0.95414 | 0.84049 | 0.75571 | 0.73226 | 0.70869
43602.5504 | 1.1048 | 1.3022 | 1.2248 | 0.9494 | 0.83603 | 0.75259 | 0.73145 | 0.70897
43602.5504 | 1.1048 | 1.3027 | 1.2255 | 0.9488 | 0.83499 | 0.75181 | 0.73295 | 0.70814
43602.5505 | 1.1014 | 1.3021 | 1.2258 | 0.94949 | 0.8361 | 0.7522 | 0.73054 | 0.70854
43602.5504 | 1.0969 | 1.3021 | 1.2255 | 0.94839 | 0.83522 | 0.75179 | 0.72945 | 0.7088
43602.5506 | 1.1024 | 1.2992 | 1.2228 | 0.94689 | 0.83445 | 0.75109 | 0.728 | 0.70832
43602.5506 | 1.0941 | 1.2968 | 1.2215 | 0.94547 | 0.83322 | 0.75024 | 0.72845 | 0.70793
43602.5506 | 1.1009 | 1.2985 | 1.2221 | 0.94633 | 0.83264 | 0.75026 | 0.73188 | 0.7082
43602.5506 | 1.0886 | 1.2896 | 1.2137 | 0.94003 | 0.82949 | 0.74755 | 0.7294 | 0.70715
43602.5508 | 1.0834 | 1.2836 | 1.2083 | 0.9355 | 0.82418 | 0.74341 | 0.72169 | 0.70582
43602.5508 | 1.0829 | 1.2835 | 1.2086 | 0.93612 | 0.82468 | 0.74408 | 0.72221 | 0.70615
43602.5508 | 1.0839 | 1.2845 | 1.2082 | 0.93707 | 0.8237 | 0.74307 | 0.72182 | 0.70556
43602.5508 | 1.0761 | 1.2812 | 1.208 | 0.93513 | 0.82456 | 0.74353 | 0.72523 | 0.70587
43602.5509 | 1.09 | 1.2913 | 1.2137 | 0.94185 | 0.8281 | 0.7459 | 0.72456 | 0.70627
43602.5509 | 1.0918 | 1.2914 | 1.2149 | 0.94132 | 0.8288 | 0.74665 | 0.72465 | 0.70654
43602.551 | 1.0958 | 1.294 | 1.2152 | 0.94201 | 0.8296 | 0.74676 | 0.72762 | 0.70632
43602.5509 | 1.0972 | 1.2952 | 1.2178 | 0.94455 | 0.83058 | 0.74756 | 0.72602 | 0.70632
43602.5511 | 1.1034 | 1.3071 | 1.2288 | 0.95127 | 0.83742 | 0.75295 | 0.73173 | 0.70776
43602.5511 | 1.1096 | 1.3068 | 1.2291 | 0.95137 | 0.8383 | 0.75348 | 0.7297 | 0.70794
43602.5511 | 1.1039 | 1.3079 | 1.2303 | 0.95236 | 0.83761 | 0.75289 | 0.72977 | 0.70775
43602.5511 | 1.1076 | 1.3088 | 1.2323 | 0.9518 | 0.83667 | 0.75264 | 0.73006 | 0.70772
43602.5512 | 1.107 | 1.3099 | 1.2341 | 0.95248 | 0.83654 | 0.75263 | 0.73023 | 0.70824
43602.5513 | 1.1056 | 1.3093 | 1.2341 | 0.95107 | 0.83914 | 0.75415 | 0.73051 | 0.70836
43602.5513 | 1.1072 | 1.3066 | 1.232 | 0.94882 | 0.83539 | 0.75182 | 0.72933 | 0.70741
43602.5512 | 1.1038 | 1.3079 | 1.2331 | 0.95071 | 0.83623 | 0.75238 | 0.72933 | 0.70794
43602.5514 | 1.0909 | 1.2999 | 1.2269 | 0.94324 | 0.83135 | 0.74944 | 0.72689 | 0.70751
43602.5514 | 1.0876 | 1.2971 | 1.2269 | 0.94192 | 0.83037 | 0.7486 | 0.72593 | 0.70725
43602.5514 | 1.0871 | 1.2969 | 1.2258 | 0.94257 | 0.83055 | 0.74865 | 0.73016 | 0.70738
43602.5514 | 1.0915 | 1.2971 | 1.2263 | 0.94106 | 0.82903 | 0.7477 | 0.72686 | 0.7067
43602.5516 | 1.0855 | 1.2971 | 1.2266 | 0.94154 | 0.82852 | 0.74681 | 0.72446 | 0.70673
43602.5516 | 1.0889 | 1.2983 | 1.2277 | 0.94146 | 0.82959 | 0.74766 | 0.72699 | 0.70715
43602.5516 | 1.0896 | 1.2995 | 1.2283 | 0.94222 | 0.82935 | 0.74736 | 0.72482 | 0.70693
43602.5516 | 1.0854 | 1.296 | 1.2264 | 0.9404 | 0.82939 | 0.74751 | 0.72574 | 0.70742
43602.5517 | 1.0839 | 1.2914 | 1.2234 | 0.93686 | 0.82673 | 0.74548 | 0.72402 | 0.70657
43602.5517 | 1.0859 | 1.2915 | 1.2216 | 0.93669 | 0.82529 | 0.74434 | 0.72667 | 0.70592
43602.5517 | 1.086 | 1.2906 | 1.2224 | 0.93566 | 0.82505 | 0.74393 | 0.72264 | 0.7057
43602.5517 | 1.0799 | 1.2899 | 1.2209 | 0.93625 | 0.82489 | 0.74414 | 0.72347 | 0.70625
43602.5519 | 1.0809 | 1.2899 | 1.2218 | 0.93566 | 0.82518 | 0.74435 | 0.723 | 0.70569
43602.5519 | 1.0865 | 1.2931 | 1.2219 | 0.93649 | 0.82435 | 0.74346 | 0.72215 | 0.70578
43602.5519 | 1.0819 | 1.2919 | 1.221 | 0.93705 | 0.82542 | 0.7439 | 0.72139 | 0.70577
43602.5519 | 1.0804 | 1.2883 | 1.2194 | 0.93375 | 0.82374 | 0.74344 | 0.72194 | 0.70543
43602.552 | 1.0787 | 1.2884 | 1.2184 | 0.93449 | 0.82255 | 0.74226 | 0.72126 | 0.70518
43602.5521 | 1.0767 | 1.2881 | 1.217 | 0.9348 | 0.82269 | 0.74262 | 0.72069 | 0.70523
43602.5521 | 1.0846 | 1.287 | 1.2167 | 0.9333 | 0.8223 | 0.74189 | 0.72101 | 0.70492
43602.552 | 1.082 | 1.2867 | 1.2159 | 0.93311 | 0.8218 | 0.74171 | 0.72268 | 0.70463
43602.5522 | 1.081 | 1.2831 | 1.2125 | 0.93132 | 0.82171 | 0.74188 | 0.7211 | 0.70514
43602.5522 | 1.078 | 1.2828 | 1.212 | 0.93166 | 0.82063 | 0.7407 | 0.71857 | 0.7045
43602.5522 | 1.0749 | 1.2831 | 1.213 | 0.93167 | 0.82086 | 0.74075 | 0.72201 | 0.70447
43602.5522 | 1.0733 | 1.283 | 1.213 | 0.93256 | 0.82126 | 0.74111 | 0.72341 | 0.70519
43602.5524 | 1.0803 | 1.2875 | 1.2144 | 0.93511 | 0.82224 | 0.74133 | 0.71971 | 0.70484
43602.5524 | 1.0844 | 1.2859 | 1.2145 | 0.93331 | 0.82228 | 0.74174 | 0.72426 | 0.70487
43602.5524 | 1.0869 | 1.289 | 1.2146 | 0.93586 | 0.82249 | 0.74185 | 0.72254 | 0.70495
43602.5524 | 1.0901 | 1.2935 | 1.2193 | 0.93872 | 0.82648 | 0.74517 | 0.7231 | 0.70561
43602.5525 | 1.0892 | 1.2957 | 1.2217 | 0.94004 | 0.82782 | 0.74581 | 0.72427 | 0.70617
43602.5525 | 1.0906 | 1.2946 | 1.2202 | 0.9387 | 0.82705 | 0.74528 | 0.72311 | 0.70592
43602.5526 | 1.0863 | 1.293 | 1.2203 | 0.93915 | 0.82676 | 0.74524 | 0.72397 | 0.7056
43602.5525 | 1.0838 | 1.2913 | 1.2193 | 0.9379 | 0.82656 | 0.74528 | 0.72311 | 0.70561
43602.5527 | 1.086 | 1.2919 | 1.2202 | 0.93969 | 0.82633 | 0.745 | 0.72322 | 0.7056
43602.5527 | 1.0791 | 1.289 | 1.2192 | 0.93735 | 0.8256 | 0.74464 | 0.72258 | 0.7055
43602.5527 | 1.0874 | 1.2918 | 1.2193 | 0.9378 | 0.82597 | 0.74463 | 0.72306 | 0.70551
43602.5527 | 1.0901 | 1.2916 | 1.2195 | 0.93811 | 0.82535 | 0.74462 | 0.72245 | 0.70534
43602.5529 | 1.0975 | 1.3034 | 1.2297 | 0.94561 | 0.83218 | 0.74901 | 0.72735 | 0.70666
43602.5529 | 1.095 | 1.3006 | 1.2283 | 0.94416 | 0.83078 | 0.74837 | 0.72624 | 0.70654
43602.5529 | 1.095 | 1.3007 | 1.228 | 0.94395 | 0.82964 | 0.74783 | 0.72606 | 0.70666
43602.5528 | 1.0981 | 1.3004 | 1.2283 | 0.9432 | 0.8304 | 0.7479 | 0.72556 | 0.70669
43602.553 | 1.0944 | 1.3029 | 1.2308 | 0.94457 | 0.83142 | 0.74883 | 0.72693 | 0.70671
43602.553 | 1.0952 | 1.3006 | 1.2301 | 0.94243 | 0.83115 | 0.74863 | 0.73127 | 0.70702
43602.553 | 1.0989 | 1.3029 | 1.2306 | 0.94382 | 0.83002 | 0.74783 | 0.72732 | 0.70647
43602.553 | 1.0945 | 1.3016 | 1.2298 | 0.94318 | 0.83089 | 0.74795 | 0.72653 | 0.70719
43602.5532 | 1.0887 | 1.2941 | 1.2234 | 0.93685 | 0.82489 | 0.74426 | 0.72353 | 0.7068
43602.5532 | 1.0842 | 1.2928 | 1.2232 | 0.93705 | 0.82549 | 0.74464 | 0.72306 | 0.70655
43602.5532 | 1.0854 | 1.2919 | 1.2215 | 0.93633 | 0.82517 | 0.74419 | 0.72634 | 0.70659
43602.5532 | 1.0736 | 1.2829 | 1.2149 | 0.93102 | 0.82099 | 0.74161 | 0.72395 | 0.70578
43602.5533 | 1.0711 | 1.2771 | 1.2097 | 0.92641 | 0.81763 | 0.73863 | 0.71738 | 0.70506
43602.5534 | 1.0711 | 1.2799 | 1.2105 | 0.92857 | 0.81743 | 0.73864 | 0.72047 | 0.70493
43602.5534 | 1.0703 | 1.2788 | 1.2101 | 0.92728 | 0.81865 | 0.73957 | 0.71922 | 0.70537
43602.5533 | 1.0699 | 1.2798 | 1.2121 | 0.92856 | 0.81923 | 0.73999 | 0.71866 | 0.7051
43602.5535 | 1.0873 | 1.2927 | 1.2199 | 0.93538 | 0.82258 | 0.74226 | 0.71995 | 0.70532
43602.5535 | 1.081 | 1.2918 | 1.2206 | 0.93481 | 0.82426 | 0.74362 | 0.72208 | 0.70609
43602.5535 | 1.0862 | 1.2934 | 1.2224 | 0.9361 | 0.82447 | 0.74377 | 0.7261 | 0.7064
43602.5535 | 1.0916 | 1.301 | 1.2287 | 0.94178 | 0.82852 | 0.74676 | 0.72505 | 0.70703
43602.5537 | 1.1007 | 1.3073 | 1.2352 | 0.94623 | 0.83296 | 0.75076 | 0.72997 | 0.70818
43602.5537 | 1.1077 | 1.3119 | 1.2373 | 0.94824 | 0.8336 | 0.75059 | 0.72866 | 0.70802
43602.5537 | 1.1014 | 1.3093 | 1.2375 | 0.9463 | 0.83398 | 0.75133 | 0.72823 | 0.70817
43602.5537 | 1.1031 | 1.3081 | 1.2372 | 0.94704 | 0.83334 | 0.7511 | 0.72843 | 0.70844
43602.5538 | 1.1021 | 1.3064 | 1.2353 | 0.94496 | 0.83253 | 0.75045 | 0.72766 | 0.70877
43602.5538 | 1.0932 | 1.3038 | 1.2352 | 0.94412 | 0.83193 | 0.7503 | 0.72704 | 0.70839
43602.5539 | 1.092 | 1.3013 | 1.2333 | 0.94248 | 0.83113 | 0.74992 | 0.72985 | 0.70857
43602.5538 | 1.0831 | 1.2947 | 1.2285 | 0.93789 | 0.82789 | 0.74708 | 0.72459 | 0.70756
43602.554 | 1.0794 | 1.287 | 1.2216 | 0.9335 | 0.82418 | 0.74402 | 0.72276 | 0.70722
43602.554 | 1.081 | 1.2873 | 1.2205 | 0.93359 | 0.82346 | 0.74355 | 0.72285 | 0.70678
43602.554 | 1.0815 | 1.2865 | 1.2194 | 0.93315 | 0.82356 | 0.74347 | 0.72207 | 0.70691
43602.554 | 1.0747 | 1.2828 | 1.2159 | 0.93076 | 0.82076 | 0.74144 | 0.71988 | 0.70604
43602.5542 | 1.0752 | 1.2763 | 1.21 | 0.92676 | 0.81832 | 0.73929 | 0.71785 | 0.70558
43602.5542 | 1.0696 | 1.2746 | 1.209 | 0.92548 | 0.81684 | 0.73873 | 0.72031 | 0.70543
43602.5542 | 1.07 | 1.2756 | 1.2092 | 0.92608 | 0.81675 | 0.73832 | 0.71748 | 0.7053
43602.5541 | 1.0681 | 1.2737 | 1.2076 | 0.92471 | 0.81551 | 0.73724 | 0.71685 | 0.70442
43602.5543 | 1.0664 | 1.2731 | 1.2055 | 0.92475 | 0.81494 | 0.73615 | 0.71588 | 0.70313
43602.5543 | 1.0655 | 1.2731 | 1.2052 | 0.9247 | 0.81456 | 0.73587 | 0.71546 | 0.70309
43602.5543 | 1.0709 | 1.2761 | 1.2063 | 0.92563 | 0.81523 | 0.73621 | 0.71513 | 0.70334
43602.5543 | 1.0767 | 1.278 | 1.2071 | 0.92725 | 0.81614 | 0.73672 | 0.72053 | 0.70265
43602.5545 | 1.0853 | 1.2856 | 1.2105 | 0.93378 | 0.82112 | 0.73969 | 0.72029 | 0.70313
43602.5545 | 1.0835 | 1.286 | 1.2102 | 0.93388 | 0.82037 | 0.73968 | 0.71857 | 0.70283
43602.5545 | 1.0854 | 1.2857 | 1.2103 | 0.93384 | 0.82017 | 0.73995 | 0.71779 | 0.70258
43602.5545 | 1.0842 | 1.2836 | 1.2076 | 0.93392 | 0.82153 | 0.74032 | 0.71838 | 0.70324
43602.5547 | 1.0889 | 1.2832 | 1.2042 | 0.93564 | 0.82171 | 0.74079 | 0.71941 | 0.70286
43602.5547 | 1.0868 | 1.2808 | 1.2025 | 0.93472 | 0.82179 | 0.74069 | 0.7196 | 0.70282
43602.5547 | 1.0834 | 1.2801 | 1.2029 | 0.93465 | 0.82074 | 0.73977 | 0.71777 | 0.70245
43602.5546 | 1.0924 | 1.2817 | 1.2027 | 0.93626 | 0.82226 | 0.74099 | 0.72136 | 0.70241
43602.5548 | 1.0947 | 1.2845 | 1.2038 | 0.9384 | 0.82412 | 0.74251 | 0.72159 | 0.70337
43602.5548 | 1.0989 | 1.2843 | 1.2043 | 0.93891 | 0.82498 | 0.74292 | 0.72149 | 0.70345
43602.5548 | 1.0963 | 1.2821 | 1.2036 | 0.93725 | 0.82571 | 0.74319 | 0.7218 | 0.7036
43602.5548 | 1.0916 | 1.2805 | 1.2021 | 0.93681 | 0.82329 | 0.7423 | 0.72072 | 0.70335
43602.555 | 1.0848 | 1.2738 | 1.197 | 0.93403 | 0.82015 | 0.7402 | 0.71907 | 0.7034
43602.555 | 1.0854 | 1.2713 | 1.1949 | 0.93135 | 0.81998 | 0.73985 | 0.72051 | 0.70341
43602.555 | 1.0812 | 1.2691 | 1.1931 | 0.93062 | 0.8195 | 0.73977 | 0.72012 | 0.70365
43602.555 | 1.0684 | 1.2632 | 1.1894 | 0.92641 | 0.81516 | 0.73671 | 0.71625 | 0.70296
43602.5551 | 1.0702 | 1.2619 | 1.1875 | 0.92468 | 0.81372 | 0.73536 | 0.71879 | 0.70267
43602.5551 | 1.0729 | 1.2626 | 1.1873 | 0.92571 | 0.81357 | 0.73514 | 0.71625 | 0.70258
43602.5552 | 1.0715 | 1.2635 | 1.1884 | 0.92622 | 0.8137 | 0.73557 | 0.71536 | 0.70261
43602.5551 | 1.0741 | 1.2651 | 1.1893 | 0.92698 | 0.81378 | 0.73593 | 0.71643 | 0.70286
43602.5553 | 1.0668 | 1.261 | 1.1867 | 0.92363 | 0.8109 | 0.73406 | 0.71709 | 0.70189
43602.5553 | 1.0652 | 1.2607 | 1.1868 | 0.9238 | 0.81261 | 0.73484 | 0.71485 | 0.70235
43602.5553 | 1.0635 | 1.259 | 1.1845 | 0.92178 | 0.81171 | 0.73429 | 0.71464 | 0.70194
43602.5553 | 1.0581 | 1.2566 | 1.1816 | 0.91949 | 0.80818 | 0.73148 | 0.7112 | 0.70101
43602.5555 | 1.0532 | 1.2506 | 1.1762 | 0.91566 | 0.80426 | 0.72888 | 0.70939 | 0.70004
43602.5555 | 1.0537 | 1.2495 | 1.1749 | 0.91534 | 0.80523 | 0.72886 | 0.70901 | 0.7
43602.5555 | 1.054 | 1.2478 | 1.1743 | 0.91414 | 0.80595 | 0.72917 | 0.71088 | 0.7003
43602.5555 | 1.0519 | 1.2498 | 1.1763 | 0.91639 | 0.80621 | 0.72939 | 0.709 | 0.70029
43602.5556 | 1.0596 | 1.2514 | 1.1759 | 0.91691 | 0.80615 | 0.72882 | 0.70877 | 0.69976
43602.5556 | 1.0588 | 1.2512 | 1.1765 | 0.91528 | 0.80605 | 0.72878 | 0.70856 | 0.69937
43602.5556 | 1.0553 | 1.2531 | 1.1775 | 0.91882 | 0.80706 | 0.72975 | 0.70921 | 0.69991
43602.5556 | 1.0688 | 1.256 | 1.179 | 0.91974 | 0.80804 | 0.73015 | 0.71237 | 0.69917
43602.5558 | 1.0786 | 1.2654 | 1.1884 | 0.92675 | 0.81341 | 0.73405 | 0.71381 | 0.70034
43602.5558 | 1.0758 | 1.2648 | 1.1889 | 0.92549 | 0.81391 | 0.7342 | 0.71627 | 0.7006
43602.5558 | 1.0792 | 1.2687 | 1.1915 | 0.92888 | 0.81449 | 0.73492 | 0.71465 | 0.70079
43602.5558 | 1.0814 | 1.2691 | 1.1929 | 0.92827 | 0.81637 | 0.73627 | 0.71634 | 0.70127
43602.556 | 1.0837 | 1.2742 | 1.1978 | 0.93204 | 0.81861 | 0.73777 | 0.71785 | 0.70229
43602.556 | 1.0829 | 1.2743 | 1.1985 | 0.93254 | 0.81983 | 0.73873 | 0.71829 | 0.70256
43602.556 | 1.0788 | 1.2741 | 1.1989 | 0.93289 | 0.81968 | 0.73866 | 0.71795 | 0.70222
43602.5559 | 1.0815 | 1.2738 | 1.1987 | 0.93129 | 0.81796 | 0.73784 | 0.71863 | 0.70211
43602.5561 | 1.0816 | 1.2735 | 1.1981 | 0.93001 | 0.81736 | 0.73758 | 0.71648 | 0.70254
43602.5561 | 1.075 | 1.2723 | 1.1985 | 0.92924 | 0.81675 | 0.73719 | 0.7164 | 0.70225
43602.5561 | 1.0696 | 1.271 | 1.1978 | 0.92883 | 0.8167 | 0.73744 | 0.71544 | 0.70265
43602.5561 | 1.07 | 1.2711 | 1.1976 | 0.92784 | 0.8153 | 0.73623 | 0.7167 | 0.70237
43602.5563 | 1.0702 | 1.2685 | 1.1955 | 0.92519 | 0.81336 | 0.73511 | 0.71729 | 0.70176
43602.5563 | 1.0662 | 1.2675 | 1.1955 | 0.92473 | 0.81233 | 0.73471 | 0.71463 | 0.70161
43602.5563 | 1.0696 | 1.2682 | 1.1952 | 0.9251 | 0.813 | 0.73497 | 0.71472 | 0.70168
43602.5563 | 1.0668 | 1.2703 | 1.198 | 0.92615 | 0.81346 | 0.735 | 0.71486 | 0.70152
43602.5564 | 1.0729 | 1.2798 | 1.2076 | 0.9318 | 0.81803 | 0.7388 | 0.71727 | 0.70302
43602.5565 | 1.0837 | 1.283 | 1.2084 | 0.93342 | 0.81926 | 0.73931 | 0.71795 | 0.70304
43602.5565 | 1.082 | 1.2831 | 1.2099 | 0.93361 | 0.82 | 0.73979 | 0.72324 | 0.70273
43602.5564 | 1.088 | 1.2903 | 1.2166 | 0.93754 | 0.82349 | 0.74256 | 0.7203 | 0.7041
43602.5566 | 1.0932 | 1.2981 | 1.2251 | 0.94245 | 0.82777 | 0.74647 | 0.72434 | 0.70564
43602.5566 | 1.0934 | 1.2981 | 1.2254 | 0.94183 | 0.82811 | 0.74651 | 0.72498 | 0.70564
43602.5566 | 1.0922 | 1.2993 | 1.2264 | 0.9422 | 0.82805 | 0.7471 | 0.72498 | 0.70583
43602.5566 | 1.0932 | 1.3018 | 1.2302 | 0.9436 | 0.82993 | 0.74856 | 0.7261 | 0.70698
43602.5568 | 1.0895 | 1.3003 | 1.2314 | 0.94207 | 0.82979 | 0.7492 | 0.72756 | 0.70815
43602.5568 | 1.0912 | 1.3017 | 1.2319 | 0.94297 | 0.82981 | 0.74875 | 0.72715 | 0.70801
43602.5568 | 1.0923 | 1.3022 | 1.2323 | 0.94276 | 0.83043 | 0.74919 | 0.72778 | 0.70838
43602.5568 | 1.0803 | 1.295 | 1.2291 | 0.939 | 0.82808 | 0.7476 | 0.72515 | 0.7086
43602.5569 | 1.0794 | 1.2909 | 1.2241 | 0.93498 | 0.82436 | 0.74461 | 0.72261 | 0.70775
43602.557 | 1.0776 | 1.2887 | 1.2239 | 0.93426 | 0.82519 | 0.74515 | 0.72471 | 0.70825
43602.557 | 1.0762 | 1.2869 | 1.2221 | 0.9329 | 0.82398 | 0.7446 | 0.72695 | 0.70835
43602.5569 | 1.074 | 1.2838 | 1.2199 | 0.93078 | 0.82226 | 0.74332 | 0.72092 | 0.70786
43602.5571 | 1.0675 | 1.2739 | 1.2124 | 0.92515 | 0.81919 | 0.74162 | 0.72149 | 0.70773
43602.5571 | 1.0598 | 1.2742 | 1.2133 | 0.92595 | 0.81851 | 0.74116 | 0.72042 | 0.70741
43602.5571 | 1.0677 | 1.2759 | 1.2127 | 0.92663 | 0.81812 | 0.74061 | 0.7187 | 0.70751
43602.5571 | 1.0632 | 1.2707 | 1.2095 | 0.92291 | 0.817 | 0.73952 | 0.71816 | 0.70711
43602.5573 | 1.0637 | 1.2696 | 1.2071 | 0.92207 | 0.81556 | 0.73828 | 0.72144 | 0.70607
43602.5573 | 1.0605 | 1.269 | 1.207 | 0.92335 | 0.81562 | 0.73867 | 0.71917 | 0.70652
43602.5573 | 1.0602 | 1.2699 | 1.2082 | 0.92363 | 0.81555 | 0.73827 | 0.71776 | 0.70625
43602.5573 | 1.0696 | 1.2776 | 1.2114 | 0.92651 | 0.8171 | 0.73899 | 0.71775 | 0.70627
43602.5574 | 1.08 | 1.2913 | 1.2218 | 0.93484 | 0.82265 | 0.74247 | 0.72385 | 0.70588
43602.5574 | 1.0791 | 1.2931 | 1.2243 | 0.93676 | 0.82407 | 0.74335 | 0.72208 | 0.70633
43602.5575 | 1.0898 | 1.2972 | 1.2246 | 0.93732 | 0.82416 | 0.7439 | 0.72253 | 0.7066
43602.5574 | 1.1039 | 1.3117 | 1.2371 | 0.94929 | 0.83317 | 0.74993 | 0.72729 | 0.70782
43602.5576 | 1.1244 | 1.3255 | 1.2478 | 0.95983 | 0.84245 | 0.75724 | 0.73343 | 0.70993
43602.5576 | 1.124 | 1.3263 | 1.2485 | 0.9605 | 0.84341 | 0.75802 | 0.73415 | 0.71045
43602.5576 | 1.1181 | 1.3233 | 1.2476 | 0.95872 | 0.84312 | 0.75819 | 0.73469 | 0.71023
43602.5576 | 1.1147 | 1.3228 | 1.2473 | 0.96057 | 0.84366 | 0.75877 | 0.73729 | 0.71082
43602.5578 | 1.1017 | 1.3145 | 1.2416 | 0.95485 | 0.84096 | 0.75757 | 0.73481 | 0.71119
43602.5578 | 1.1146 | 1.3149 | 1.2396 | 0.95447 | 0.84032 | 0.75782 | 0.73471 | 0.71136
43602.5578 | 1.1091 | 1.3126 | 1.238 | 0.95345 | 0.83949 | 0.75722 | 0.7337 | 0.71134
43602.5578 | 1.1062 | 1.3106 | 1.2368 | 0.95241 | 0.83902 | 0.75643 | 0.73497 | 0.71204
43602.5579 | 1.0946 | 1.3034 | 1.2305 | 0.94634 | 0.8347 | 0.75388 | 0.7323 | 0.71198
43602.5579 | 1.0944 | 1.3001 | 1.2287 | 0.94561 | 0.83411 | 0.75312 | 0.73147 | 0.7115
43602.558 | 1.0903 | 1.298 | 1.2279 | 0.94415 | 0.83364 | 0.75251 | 0.73101 | 0.71129
43602.5579 | 1.0872 | 1.2943 | 1.2249 | 0.94162 | 0.83069 | 0.75067 | 0.72994 | 0.71071
43602.5581 | 1.0881 | 1.2939 | 1.2245 | 0.94005 | 0.82925 | 0.74908 | 0.72841 | 0.71069
43602.5581 | 1.0929 | 1.296 | 1.2248 | 0.94055 | 0.83046 | 0.74977 | 0.72841 | 0.71049
43602.5581 | 1.0898 | 1.2967 | 1.226 | 0.9416 | 0.83044 | 0.74967 | 0.72812 | 0.71049
43602.5581 | 1.094 | 1.2958 | 1.2255 | 0.94005 | 0.83049 | 0.74927 | 0.72768 | 0.71024
43602.5583 | 1.0945 | 1.3015 | 1.2288 | 0.94324 | 0.83173 | 0.74969 | 0.72859 | 0.70999
43602.5583 | 1.0941 | 1.3008 | 1.2284 | 0.94321 | 0.83096 | 0.74992 | 0.7286 | 0.71007
43602.5583 | 1.0981 | 1.3046 | 1.2302 | 0.94582 | 0.83227 | 0.75027 | 0.72891 | 0.70998
43602.5583 | 1.0965 | 1.3041 | 1.2301 | 0.94518 | 0.8328 | 0.75077 | 0.72916 | 0.71047
43602.5584 | 1.1055 | 1.3105 | 1.2349 | 0.94974 | 0.83566 | 0.75285 | 0.73049 | 0.7102
43602.5584 | 1.103 | 1.3136 | 1.2369 | 0.95129 | 0.83679 | 0.75377 | 0.73164 | 0.71004
43602.5585 | 1.1093 | 1.3148 | 1.2376 | 0.95276 | 0.83862 | 0.75515 | 0.73243 | 0.71069
43602.5584 | 1.1223 | 1.3242 | 1.2462 | 0.96009 | 0.84469 | 0.75911 | 0.73572 | 0.71129
43602.5586 | 1.1229 | 1.3277 | 1.2498 | 0.96334 | 0.84832 | 0.76245 | 0.73861 | 0.7128
43602.5586 | 1.129 | 1.3291 | 1.2502 | 0.96403 | 0.84831 | 0.76255 | 0.7385 | 0.71245
43602.5586 | 1.1199 | 1.3283 | 1.2512 | 0.96393 | 0.84807 | 0.76252 | 0.73907 | 0.71278
43602.5586 | 1.1238 | 1.3249 | 1.2477 | 0.96168 | 0.84802 | 0.76267 | 0.73891 | 0.71309
43602.5588 | 1.1156 | 1.3177 | 1.2423 | 0.95657 | 0.84371 | 0.75991 | 0.7367 | 0.7134
43602.5588 | 1.1157 | 1.3184 | 1.2411 | 0.95634 | 0.84235 | 0.75914 | 0.73644 | 0.7134
43602.5588 | 1.1112 | 1.3164 | 1.2405 | 0.95521 | 0.84247 | 0.7593 | 0.73741 | 0.71334
43602.5587 | 1.102 | 1.3081 | 1.2348 | 0.95058 | 0.83883 | 0.75652 | 0.73384 | 0.7124
43602.5589 | 1.0963 | 1.2981 | 1.2262 | 0.9443 | 0.83201 | 0.75113 | 0.73036 | 0.71107
43602.5589 | 1.0914 | 1.2972 | 1.2256 | 0.9438 | 0.83199 | 0.75167 | 0.73005 | 0.71116
43602.559 | 1.0924 | 1.2965 | 1.2252 | 0.94279 | 0.83168 | 0.75094 | 0.72919 | 0.71107
43602.5589 | 1.0905 | 1.2962 | 1.2242 | 0.94235 | 0.83104 | 0.7506 | 0.72893 | 0.71072
43602.5591 | 1.0916 | 1.2977 | 1.2242 | 0.9442 | 0.83056 | 0.74968 | 0.7282 | 0.70998
43602.5591 | 1.0956 | 1.2986 | 1.2245 | 0.94437 | 0.83193 | 0.75038 | 0.73086 | 0.7102
43602.5591 | 1.098 | 1.2981 | 1.2244 | 0.94348 | 0.83193 | 0.75003 | 0.72848 | 0.70989
43602.5591 | 1.0924 | 1.2983 | 1.2249 | 0.94508 | 0.83185 | 0.74982 | 0.72778 | 0.70912
43602.5593 | 1.1022 | 1.3003 | 1.2242 | 0.94641 | 0.83382 | 0.75104 | 0.72857 | 0.70899
43602.5593 | 1.1008 | 1.2995 | 1.2242 | 0.94644 | 0.8332 | 0.75076 | 0.72931 | 0.70881
43602.5593 | 1.1035 | 1.2994 | 1.2232 | 0.94608 | 0.83357 | 0.75109 | 0.72867 | 0.70914
43602.5592 | 1.0992 | 1.2955 | 1.2189 | 0.94422 | 0.83268 | 0.75013 | 0.72829 | 0.70851
43602.5594 | 1.1029 | 1.2956 | 1.2176 | 0.94711 | 0.8327 | 0.7504 | 0.72764 | 0.7084
43602.5594 | 1.1041 | 1.2978 | 1.2186 | 0.94781 | 0.83416 | 0.75117 | 0.72963 | 0.70822
43602.5594 | 1.0998 | 1.2933 | 1.216 | 0.94513 | 0.83331 | 0.75096 | 0.73204 | 0.70815
43602.5594 | 1.1142 | 1.3031 | 1.224 | 0.95325 | 0.83895 | 0.75489 | 0.73153 | 0.70884
43602.5596 | 1.1233 | 1.3086 | 1.2273 | 0.95601 | 0.84323 | 0.7579 | 0.73685 | 0.70931
43602.5596 | 1.13 | 1.3105 | 1.2287 | 0.95792 | 0.84295 | 0.75797 | 0.73492 | 0.70967
43602.5596 | 1.1352 | 1.312 | 1.2297 | 0.95919 | 0.84196 | 0.75693 | 0.73324 | 0.70884
43602.5596 | 1.1294 | 1.3109 | 1.2284 | 0.95739 | 0.84378 | 0.75857 | 0.73426 | 0.70975
43602.5598 | 1.1382 | 1.314 | 1.2307 | 0.9603 | 0.84516 | 0.75994 | 0.73804 | 0.71018
43602.5598 | 1.1375 | 1.319 | 1.2348 | 0.96427 | 0.847 | 0.76131 | 0.73702 | 0.71095
43602.5598 | 1.1383 | 1.3145 | 1.2307 | 0.96107 | 0.84537 | 0.75998 | 0.73576 | 0.71011
43602.5598 | 1.1488 | 1.3228 | 1.2372 | 0.96652 | 0.84656 | 0.76087 | 0.73654 | 0.71094
43602.5599 | 1.1411 | 1.3235 | 1.2398 | 0.96812 | 0.849 | 0.76286 | 0.73801 | 0.71162
43602.5599 | 1.1367 | 1.3231 | 1.2398 | 0.96757 | 0.85111 | 0.76454 | 0.74044 | 0.71267
43602.56 | 1.1507 | 1.3252 | 1.2404 | 0.96887 | 0.85204 | 0.76451 | 0.74403 | 0.71261
43602.5599 | 1.1378 | 1.3248 | 1.2402 | 0.96763 | 0.85135 | 0.76474 | 0.74263 | 0.71293
43602.5601 | 1.1357 | 1.3196 | 1.2378 | 0.96486 | 0.85052 | 0.76361 | 0.74093 | 0.71316
43602.5601 | 1.1276 | 1.3172 | 1.2363 | 0.964 | 0.84978 | 0.76345 | 0.73913 | 0.71326
43602.5601 | 1.1236 | 1.3185 | 1.2364 | 0.96339 | 0.84872 | 0.7628 | 0.73913 | 0.71332
43602.5601 | 1.1206 | 1.3109 | 1.2303 | 0.96009 | 0.84512 | 0.76027 | 0.73775 | 0.71312
43602.5603 | 1.109 | 1.3047 | 1.2246 | 0.95542 | 0.84102 | 0.75757 | 0.73528 | 0.71272
43602.5603 | 1.1015 | 1.3024 | 1.224 | 0.95413 | 0.83991 | 0.75656 | 0.73667 | 0.71249
43602.5603 | 1.1049 | 1.3018 | 1.2235 | 0.95403 | 0.83911 | 0.75621 | 0.73571 | 0.7122
43602.5603 | 1.099 | 1.2973 | 1.2197 | 0.95003 | 0.8381 | 0.75538 | 0.73301 | 0.71182
43602.5604 | 1.1028 | 1.2977 | 1.2178 | 0.95139 | 0.83745 | 0.75434 | 0.73243 | 0.71204
43602.5604 | 1.1019 | 1.2938 | 1.2148 | 0.94812 | 0.83456 | 0.75201 | 0.73069 | 0.71045
43602.5605 | 1.0967 | 1.2946 | 1.2157 | 0.94845 | 0.83522 | 0.75227 | 0.73129 | 0.71094
43602.5604 | 1.0933 | 1.2878 | 1.2096 | 0.94486 | 0.83172 | 0.75076 | 0.73005 | 0.71033
43602.5606 | 1.0926 | 1.2852 | 1.2068 | 0.94413 | 0.83056 | 0.74946 | 0.72868 | 0.70973
43602.5606 | 1.0952 | 1.2857 | 1.207 | 0.94422 | 0.83093 | 0.74935 | 0.72901 | 0.71027
43602.5606 | 1.0921 | 1.2864 | 1.2072 | 0.94459 | 0.83114 | 0.74995 | 0.73336 | 0.71031
43602.5606 | 1.0914 | 1.2853 | 1.2064 | 0.94478 | 0.83039 | 0.74893 | 0.73105 | 0.70954
43602.5608 | 1.0972 | 1.2862 | 1.2061 | 0.94543 | 0.83199 | 0.75008 | 0.72948 | 0.71005
43602.5608 | 1.1005 | 1.2843 | 1.2037 | 0.94475 | 0.83095 | 0.74964 | 0.72818 | 0.70967
43602.5608 | 1.1009 | 1.2838 | 1.2037 | 0.94497 | 0.82954 | 0.74847 | 0.72755 | 0.70928
43602.5608 | 1.0839 | 1.2805 | 1.2014 | 0.94247 | 0.82893 | 0.74804 | 0.72757 | 0.70915
43602.5609 | 1.0857 | 1.2714 | 1.1931 | 0.93781 | 0.82583 | 0.74566 | 0.72645 | 0.70872
43602.5609 | 1.095 | 1.2728 | 1.1928 | 0.93863 | 0.82561 | 0.74551 | 0.72556 | 0.70846
43602.561 | 1.0868 | 1.2742 | 1.1948 | 0.94007 | 0.82568 | 0.74555 | 0.72567 | 0.70852
43602.5609 | 1.0782 | 1.2701 | 1.1912 | 0.93734 | 0.82301 | 0.74401 | 0.72427 | 0.70795
43602.5611 | 1.0801 | 1.2642 | 1.1865 | 0.93423 | 0.82357 | 0.744 | 0.72421 | 0.70813
43602.5611 | 1.0838 | 1.2645 | 1.1864 | 0.93476 | 0.82227 | 0.74309 | 0.72314 | 0.70802
43602.5611 | 1.0795 | 1.2644 | 1.1855 | 0.9333 | 0.82215 | 0.74287 | 0.72302 | 0.70785
43602.5611 | 1.074 | 1.2607 | 1.1836 | 0.93162 | 0.82079 | 0.74172 | 0.72387 | 0.70732
43602.5613 | 1.0785 | 1.2579 | 1.1799 | 0.93007 | 0.81752 | 0.73907 | 0.72165 | 0.70632
43602.5613 | 1.0806 | 1.2624 | 1.1833 | 0.93327 | 0.82115 | 0.74205 | 0.72197 | 0.7079
43602.5613 | 1.0738 | 1.2591 | 1.1811 | 0.93089 | 0.82041 | 0.74119 | 0.72085 | 0.70719
43602.5613 | 1.0754 | 1.2599 | 1.1816 | 0.93175 | 0.81837 | 0.73992 | 0.72036 | 0.70681
43602.5614 | 1.07 | 1.2534 | 1.1772 | 0.92793 | 0.81914 | 0.74017 | 0.72074 | 0.70729
43602.5614 | 1.0717 | 1.255 | 1.1776 | 0.92864 | 0.81629 | 0.7383 | 0.71868 | 0.70644
43602.5615 | 1.0705 | 1.2525 | 1.1757 | 0.92685 | 0.81716 | 0.73956 | 0.71916 | 0.70711
43602.5614 | 1.0629 | 1.252 | 1.1759 | 0.92708 | 0.81494 | 0.7374 | 0.72018 | 0.70613
43602.5616 | 1.0561 | 1.2497 | 1.1748 | 0.92549 | 0.81429 | 0.73751 | 0.71743 | 0.70604
43602.5616 | 1.0545 | 1.2488 | 1.1728 | 0.92358 | 0.81238 | 0.73595 | 0.72229 | 0.70559
43602.5616 | 1.0661 | 1.2506 | 1.1739 | 0.92539 | 0.81249 | 0.73618 | 0.71826 | 0.70568
43602.5616 | 1.0599 | 1.2493 | 1.1732 | 0.92322 | 0.81352 | 0.73647 | 0.71802 | 0.70551
43602.5618 | 1.0611 | 1.2487 | 1.1728 | 0.92329 | 0.81281 | 0.73597 | 0.7169 | 0.70581
43602.5618 | 1.057 | 1.2459 | 1.1706 | 0.91975 | 0.81113 | 0.73455 | 0.71504 | 0.70497
43602.5618 | 1.0577 | 1.2486 | 1.1721 | 0.92173 | 0.81163 | 0.73488 | 0.71562 | 0.70548
43602.5618 | 1.0512 | 1.2471 | 1.1723 | 0.92005 | 0.81147 | 0.73499 | 0.71772 | 0.70555
43602.5619 | 1.0572 | 1.2483 | 1.1725 | 0.91987 | 0.81206 | 0.73526 | 0.71612 | 0.70561
43602.5619 | 1.0569 | 1.2505 | 1.1738 | 0.92232 | 0.8123 | 0.7354 | 0.71575 | 0.70613
43602.562 | 1.0524 | 1.2477 | 1.1732 | 0.92007 | 0.81075 | 0.73465 | 0.71498 | 0.70547
43602.5619 | 1.0504 | 1.2494 | 1.1756 | 0.92127 | 0.81183 | 0.7352 | 0.71526 | 0.70596
43602.5621 | 1.0546 | 1.2497 | 1.1758 | 0.91978 | 0.81127 | 0.73503 | 0.71618 | 0.706
43602.5621 | 1.0495 | 1.252 | 1.1771 | 0.92187 | 0.81053 | 0.73488 | 0.71526 | 0.70633
43602.5621 | 1.0473 | 1.2508 | 1.1777 | 0.92105 | 0.81218 | 0.73564 | 0.71572 | 0.70666
43602.5621 | 1.0446 | 1.2437 | 1.1712 | 0.91623 | 0.80728 | 0.73255 | 0.71432 | 0.70609
43602.5623 | 1.0382 | 1.2374 | 1.1668 | 0.91074 | 0.80381 | 0.73026 | 0.71189 | 0.70532
43602.5623 | 1.0344 | 1.2347 | 1.1664 | 0.91037 | 0.80297 | 0.72973 | 0.71097 | 0.70548
43602.5623 | 1.0339 | 1.2331 | 1.1654 | 0.90896 | 0.80171 | 0.72884 | 0.71082 | 0.70469
43602.5623 | 1.0346 | 1.2342 | 1.1648 | 0.90983 | 0.8013 | 0.72815 | 0.71005 | 0.70471
43602.5624 | 1.0295 | 1.233 | 1.1631 | 0.9083 | 0.80126 | 0.72749 | 0.70845 | 0.70403
43602.5625 | 1.0284 | 1.2309 | 1.1622 | 0.9076 | 0.80115 | 0.72764 | 0.70787 | 0.70387
43602.5625 | 1.0284 | 1.2309 | 1.1627 | 0.90691 | 0.80013 | 0.72681 | 0.70847 | 0.70362
43602.5624 | 1.0321 | 1.2335 | 1.163 | 0.91007 | 0.80159 | 0.72747 | 0.70862 | 0.70347
43602.5626 | 1.038 | 1.2364 | 1.1627 | 0.91051 | 0.80139 | 0.72693 | 0.70825 | 0.70292
43602.5626 | 1.0295 | 1.2317 | 1.1628 | 0.90803 | 0.80105 | 0.72653 | 0.70792 | 0.70229
43602.5626 | 1.0352 | 1.2338 | 1.1626 | 0.9092 | 0.80018 | 0.726 | 0.70728 | 0.70226
43602.5626 | 1.0408 | 1.2369 | 1.1631 | 0.91282 | 0.80268 | 0.72782 | 0.70983 | 0.70298
43602.5628 | 1.043 | 1.237 | 1.1635 | 0.91272 | 0.80491 | 0.72901 | 0.71302 | 0.70281
43602.5628 | 1.0454 | 1.2369 | 1.1627 | 0.91354 | 0.80271 | 0.72772 | 0.70923 | 0.70228
43602.5628 | 1.0451 | 1.2366 | 1.1625 | 0.91305 | 0.80377 | 0.72828 | 0.70954 | 0.70255
43602.5628 | 1.041 | 1.2333 | 1.1594 | 0.91102 | 0.8022 | 0.72715 | 0.70875 | 0.70205
43602.5629 | 1.0324 | 1.2278 | 1.1538 | 0.9091 | 0.79965 | 0.72559 | 0.70727 | 0.70244
43602.563 | 1.0337 | 1.2252 | 1.1506 | 0.90711 | 0.79948 | 0.72555 | 0.70798 | 0.702
43602.563 | 1.0303 | 1.2212 | 1.1488 | 0.9045 | 0.79758 | 0.72413 | 0.70671 | 0.70167
43602.5629 | 1.0234 | 1.2168 | 1.1441 | 0.9014 | 0.79477 | 0.72182 | 0.70459 | 0.70076
43602.5631 | 1.0378 | 1.2214 | 1.1462 | 0.90705 | 0.79716 | 0.72374 | 0.70584 | 0.70195
43602.5631 | 1.0288 | 1.2176 | 1.1446 | 0.90309 | 0.79704 | 0.72309 | 0.70525 | 0.70131
43602.5631 | 1.0339 | 1.2206 | 1.1458 | 0.90547 | 0.797 | 0.72324 | 0.70835 | 0.7019
43602.5631 | 1.0354 | 1.2238 | 1.1495 | 0.90735 | 0.80075 | 0.72602 | 0.70761 | 0.70245
43602.5633 | 1.0473 | 1.2325 | 1.1551 | 0.91291 | 0.8034 | 0.7274 | 0.70959 | 0.70217
43602.5633 | 1.0582 | 1.2356 | 1.1573 | 0.91494 | 0.80378 | 0.72815 | 0.70932 | 0.70209
43602.5633 | 1.0438 | 1.2315 | 1.1554 | 0.91184 | 0.80406 | 0.72819 | 0.70979 | 0.70219
43602.5633 | 1.0561 | 1.2371 | 1.1592 | 0.91586 | 0.80431 | 0.72873 | 0.7104 | 0.70246
43602.5635 | 1.0375 | 1.232 | 1.1574 | 0.91244 | 0.80306 | 0.72788 | 0.70959 | 0.70258
43602.5635 | 1.0366 | 1.2309 | 1.1566 | 0.9118 | 0.80236 | 0.72721 | 0.70813 | 0.70229
43602.5635 | 1.0399 | 1.2293 | 1.1551 | 0.90952 | 0.80207 | 0.72708 | 0.70833 | 0.7026
43602.5634 | 1.0359 | 1.2254 | 1.1509 | 0.90751 | 0.79851 | 0.72444 | 0.70637 | 0.70164
43602.5636 | 1.0256 | 1.2164 | 1.1429 | 0.90033 | 0.79303 | 0.72048 | 0.7034 | 0.70069
43602.5636 | 1.0258 | 1.2157 | 1.1425 | 0.90051 | 0.793 | 0.72049 | 0.70664 | 0.7008
43602.5636 | 1.0249 | 1.2156 | 1.1429 | 0.9006 | 0.79403 | 0.72114 | 0.70411 | 0.70142
43602.5636 | 1.0207 | 1.2134 | 1.1415 | 0.89973 | 0.79181 | 0.71977 | 0.70214 | 0.70071
43602.5638 | 1.0271 | 1.2142 | 1.1399 | 0.89987 | 0.79211 | 0.71942 | 0.70398 | 0.70057
43602.5638 | 1.021 | 1.212 | 1.1391 | 0.8986 | 0.79249 | 0.71969 | 0.70317 | 0.70063
43602.5638 | 1.0233 | 1.2148 | 1.1423 | 0.9013 | 0.79223 | 0.7198 | 0.70291 | 0.70032
43602.5638 | 1.0311 | 1.2174 | 1.1429 | 0.90219 | 0.79586 | 0.72199 | 0.70447 | 0.70131
43602.564 | 1.0294 | 1.2193 | 1.1451 | 0.90414 | 0.79472 | 0.72138 | 0.70426 | 0.70072
43602.564 | 1.0368 | 1.2212 | 1.1471 | 0.90638 | 0.79673 | 0.72298 | 0.70486 | 0.70138
43602.564 | 1.0379 | 1.2228 | 1.1469 | 0.90626 | 0.7983 | 0.72375 | 0.70614 | 0.70172
43602.5639 | 1.0334 | 1.2252 | 1.1508 | 0.90829 | 0.79922 | 0.72521 | 0.70668 | 0.70222
43602.5641 | 1.0406 | 1.2325 | 1.158 | 0.91412 | 0.80486 | 0.72945 | 0.71049 | 0.7043
43602.5641 | 1.0437 | 1.2324 | 1.1568 | 0.91304 | 0.80416 | 0.72907 | 0.71434 | 0.70396
43602.5641 | 1.0481 | 1.2341 | 1.1572 | 0.91395 | 0.80446 | 0.72895 | 0.71121 | 0.70371
43602.5641 | 1.0482 | 1.2396 | 1.1635 | 0.91667 | 0.80711 | 0.73139 | 0.71172 | 0.70477
43602.5643 | 1.0544 | 1.2457 | 1.1697 | 0.92114 | 0.80968 | 0.7339 | 0.71518 | 0.70596
43602.5643 | 1.053 | 1.2468 | 1.1713 | 0.92112 | 0.81215 | 0.73566 | 0.716 | 0.7069
43602.5643 | 1.0579 | 1.2508 | 1.1749 | 0.92442 | 0.81191 | 0.73537 | 0.71615 | 0.70662
43602.5643 | 1.0567 | 1.254 | 1.1792 | 0.92534 | 0.81414 | 0.73815 | 0.71864 | 0.70803
43602.5645 | 1.0594 | 1.2568 | 1.1816 | 0.92555 | 0.81583 | 0.73958 | 0.71954 | 0.70927
43602.5645 | 1.053 | 1.2545 | 1.1823 | 0.92412 | 0.81471 | 0.7387 | 0.71862 | 0.70865
43602.5645 | 1.057 | 1.2551 | 1.1823 | 0.92482 | 0.81513 | 0.73927 | 0.71978 | 0.70919
43602.5645 | 1.0541 | 1.2565 | 1.1851 | 0.92429 | 0.81468 | 0.73923 | 0.72004 | 0.70981
43602.5646 | 1.0474 | 1.2559 | 1.1881 | 0.92392 | 0.81475 | 0.73974 | 0.72354 | 0.71024
43602.5646 | 1.0526 | 1.259 | 1.1887 | 0.9248 | 0.81644 | 0.74095 | 0.72162 | 0.71119
43602.5647 | 1.0536 | 1.2556 | 1.1868 | 0.92095 | 0.8148 | 0.73986 | 0.71957 | 0.71012
43602.5646 | 1.0495 | 1.2575 | 1.1905 | 0.92301 | 0.81586 | 0.7402 | 0.71984 | 0.71031
43602.5648 | 1.0522 | 1.2611 | 1.1949 | 0.92392 | 0.81603 | 0.74028 | 0.72007 | 0.7102
43602.5648 | 1.0515 | 1.2621 | 1.1962 | 0.92411 | 0.81669 | 0.74052 | 0.72061 | 0.71038
43602.5648 | 1.0533 | 1.2636 | 1.1983 | 0.92551 | 0.81708 | 0.74101 | 0.72466 | 0.71042
43602.5648 | 1.0595 | 1.2682 | 1.2022 | 0.92625 | 0.81897 | 0.74229 | 0.72359 | 0.71034
43602.565 | 1.0551 | 1.2689 | 1.2072 | 0.92813 | 0.82005 | 0.74303 | 0.72154 | 0.71066
43602.565 | 1.0649 | 1.2734 | 1.2076 | 0.92839 | 0.82083 | 0.74351 | 0.72218 | 0.71106
43602.565 | 1.0661 | 1.2731 | 1.208 | 0.92776 | 0.82026 | 0.74252 | 0.72354 | 0.70991
43602.565 | 1.0715 | 1.2792 | 1.2151 | 0.93175 | 0.82283 | 0.74435 | 0.7231 | 0.71042
43602.5651 | 1.0761 | 1.2934 | 1.2264 | 0.9389 | 0.82728 | 0.74708 | 0.72492 | 0.71045
43602.5652 | 1.0825 | 1.2946 | 1.2281 | 0.93833 | 0.82859 | 0.74802 | 0.72553 | 0.71091
43602.5652 | 1.0839 | 1.2966 | 1.2289 | 0.93888 | 0.82787 | 0.74757 | 0.72522 | 0.71057
43602.5651 | 1.0958 | 1.3105 | 1.243 | 0.94666 | 0.83428 | 0.75219 | 0.72951 | 0.71158
43602.5653 | 1.099 | 1.3183 | 1.2498 | 0.95158 | 0.83861 | 0.75576 | 0.73595 | 0.7128
43602.5653 | 1.106 | 1.3193 | 1.2501 | 0.95201 | 0.83917 | 0.75554 | 0.73321 | 0.71276
43602.5653 | 1.1002 | 1.3175 | 1.2503 | 0.95158 | 0.83913 | 0.75584 | 0.73256 | 0.71253
43602.5653 | 1.1033 | 1.3163 | 1.2495 | 0.9512 | 0.83896 | 0.75607 | 0.73288 | 0.7132
43602.5655 | 1.1007 | 1.3136 | 1.2477 | 0.94944 | 0.83808 | 0.75541 | 0.73707 | 0.713
43602.5655 | 1.1041 | 1.3132 | 1.2469 | 0.94885 | 0.83785 | 0.75498 | 0.73309 | 0.71301
43602.5655 | 1.0979 | 1.313 | 1.2463 | 0.94798 | 0.83824 | 0.75527 | 0.73254 | 0.71276
43602.5655 | 1.0944 | 1.3089 | 1.2436 | 0.94614 | 0.83624 | 0.75385 | 0.73129 | 0.71255
43602.5657 | 1.0861 | 1.303 | 1.239 | 0.9431 | 0.8334 | 0.75126 | 0.72824 | 0.71156
43602.5657 | 1.0928 | 1.3049 | 1.2391 | 0.94353 | 0.83354 | 0.75125 | 0.72751 | 0.71144
43602.5657 | 1.097 | 1.3039 | 1.2385 | 0.94234 | 0.83268 | 0.75081 | 0.72788 | 0.71101
43602.5656 | 1.0897 | 1.3025 | 1.2371 | 0.94223 | 0.83185 | 0.75009 | 0.72941 | 0.71038
43602.5658 | 1.0918 | 1.3029 | 1.2367 | 0.94167 | 0.8314 | 0.7491 | 0.7263 | 0.709
43602.5658 | 1.0927 | 1.3071 | 1.2387 | 0.94424 | 0.83112 | 0.7493 | 0.72551 | 0.70922
43602.5658 | 1.0957 | 1.3074 | 1.2383 | 0.9442 | 0.83178 | 0.74951 | 0.72941 | 0.70913
43602.5658 | 1.1084 | 1.3158 | 1.2427 | 0.94953 | 0.83493 | 0.75135 | 0.72772 | 0.70869
43602.566 | 1.1204 | 1.3303 | 1.2525 | 0.95907 | 0.84153 | 0.75576 | 0.73155 | 0.70911
43602.566 | 1.117 | 1.3306 | 1.2549 | 0.96045 | 0.8434 | 0.75705 | 0.73279 | 0.70961
43602.566 | 1.1254 | 1.3322 | 1.2546 | 0.96144 | 0.84463 | 0.75768 | 0.73362 | 0.71002
43602.566 | 1.1306 | 1.3349 | 1.2569 | 0.9639 | 0.84687 | 0.75995 | 0.73603 | 0.71041
43602.5662 | 1.1316 | 1.3335 | 1.2552 | 0.96606 | 0.84857 | 0.7618 | 0.73872 | 0.71068
43602.5662 | 1.1261 | 1.3324 | 1.2541 | 0.96518 | 0.84817 | 0.76137 | 0.7372 | 0.71086
43602.5662 | 1.1245 | 1.3315 | 1.2532 | 0.96428 | 0.84763 | 0.76083 | 0.7371 | 0.71111
43602.5662 | 1.1226 | 1.3256 | 1.2468 | 0.96121 | 0.84476 | 0.75916 | 0.73594 | 0.71059
43602.5663 | 1.1062 | 1.3117 | 1.2343 | 0.95139 | 0.83765 | 0.75442 | 0.73146 | 0.7097
43602.5663 | 1.1062 | 1.3071 | 1.2312 | 0.94822 | 0.83579 | 0.75337 | 0.72972 | 0.70917
43602.5664 | 1.1047 | 1.3055 | 1.2292 | 0.94774 | 0.83507 | 0.75256 | 0.73 | 0.70926
43602.5663 | 1.0939 | 1.2935 | 1.2197 | 0.94186 | 0.82979 | 0.74853 | 0.72632 | 0.70828
43602.5665 | 1.0756 | 1.2775 | 1.2042 | 0.93169 | 0.82089 | 0.7413 | 0.72014 | 0.70558
43602.5665 | 1.0795 | 1.2741 | 1.2015 | 0.92886 | 0.81943 | 0.7403 | 0.72136 | 0.70504
43602.5665 | 1.0766 | 1.2759 | 1.2018 | 0.93017 | 0.81903 | 0.74002 | 0.71927 | 0.70532
43602.5665 | 1.0714 | 1.2665 | 1.1918 | 0.92449 | 0.81375 | 0.73529 | 0.71413 | 0.70262
43602.5667 | 1.0651 | 1.2626 | 1.1884 | 0.92498 | 0.81234 | 0.73451 | 0.71324 | 0.70131
43602.5667 | 1.0689 | 1.2642 | 1.1886 | 0.92621 | 0.81323 | 0.73438 | 0.71404 | 0.70105
43602.5667 | 1.0761 | 1.2656 | 1.1893 | 0.92726 | 0.81423 | 0.73472 | 0.71767 | 0.70118
43602.5667 | 1.092 | 1.2767 | 1.1967 | 0.93462 | 0.82007 | 0.73896 | 0.71737 | 0.70099
43602.5668 | 1.1256 | 1.3008 | 1.2165 | 0.95253 | 0.83261 | 0.74851 | 0.72541 | 0.70253
43602.5669 | 1.1197 | 1.2982 | 1.2154 | 0.95037 | 0.83528 | 0.75114 | 0.72708 | 0.70321
43602.5669 | 1.1465 | 1.3061 | 1.2192 | 0.95429 | 0.83595 | 0.75154 | 0.72826 | 0.70352
43602.5668 | 1.1442 | 1.3086 | 1.2217 | 0.9555 | 0.83869 | 0.75355 | 0.72996 | 0.70382
43602.567 | 1.1466 | 1.3162 | 1.2295 | 0.96048 | 0.84474 | 0.75848 | 0.73343 | 0.70544
43602.567 | 1.1532 | 1.3187 | 1.2307 | 0.96184 | 0.84206 | 0.75636 | 0.73062 | 0.70476
43602.567 | 1.1367 | 1.3183 | 1.2317 | 0.96132 | 0.84263 | 0.75731 | 0.73295 | 0.70477
43602.567 | 1.1502 | 1.3335 | 1.2454 | 0.97198 | 0.85066 | 0.76344 | 0.73765 | 0.70693
43602.5672 | 1.1723 | 1.346 | 1.2556 | 0.97872 | 0.85713 | 0.76767 | 0.74087 | 0.70889
43602.5672 | 1.1801 | 1.3472 | 1.2568 | 0.97945 | 0.85512 | 0.76668 | 0.74063 | 0.70824
43602.5672 | 1.1858 | 1.3537 | 1.2613 | 0.98337 | 0.85922 | 0.76937 | 0.74247 | 0.7094
43602.5672 | 1.1586 | 1.3437 | 1.2578 | 0.9763 | 0.85528 | 0.76709 | 0.74099 | 0.70976
43602.5674 | 1.1464 | 1.3365 | 1.254 | 0.97081 | 0.85118 | 0.76428 | 0.73923 | 0.71011
43602.5674 | 1.1386 | 1.3323 | 1.2518 | 0.96913 | 0.85035 | 0.76347 | 0.74033 | 0.70999
43602.5674 | 1.1248 | 1.3293 | 1.2498 | 0.96556 | 0.84668 | 0.76148 | 0.73798 | 0.70956
43602.5673 | 1.1166 | 1.3196 | 1.2432 | 0.95721 | 0.84331 | 0.75825 | 0.7338 | 0.70949
43602.5675 | 1.1065 | 1.3113 | 1.2379 | 0.95027 | 0.83681 | 0.7543 | 0.73115 | 0.70879
43602.5675 | 1.1034 | 1.3128 | 1.2382 | 0.95031 | 0.83509 | 0.75301 | 0.72942 | 0.70813
43602.5676 | 1.1068 | 1.3129 | 1.2382 | 0.95018 | 0.83536 | 0.75296 | 0.72984 | 0.70846
43602.5675 | 1.1036 | 1.3135 | 1.2397 | 0.95031 | 0.83513 | 0.75254 | 0.72928 | 0.70902
43602.5677 | 1.098 | 1.3129 | 1.241 | 0.94873 | 0.83333 | 0.75137 | 0.72759 | 0.70795
43602.5677 | 1.1007 | 1.313 | 1.2417 | 0.94872 | 0.83401 | 0.75151 | 0.72736 | 0.7081
43602.5677 | 1.0976 | 1.3122 | 1.2418 | 0.94795 | 0.83395 | 0.75186 | 0.72768 | 0.70847
43602.5677 | 1.1034 | 1.3183 | 1.2465 | 0.95181 | 0.83489 | 0.75256 | 0.73111 | 0.70861
43602.5679 | 1.1149 | 1.324 | 1.2501 | 0.95527 | 0.83759 | 0.75429 | 0.73277 | 0.7091
43602.5679 | 1.1124 | 1.3255 | 1.2518 | 0.95638 | 0.8398 | 0.75543 | 0.73185 | 0.70966
43602.5679 | 1.1114 | 1.3234 | 1.2503 | 0.95506 | 0.83903 | 0.75513 | 0.73111 | 0.70916
43602.5679 | 1.1158 | 1.3237 | 1.2503 | 0.95533 | 0.83892 | 0.75512 | 0.73109 | 0.70952
43602.568 | 1.1101 | 1.3196 | 1.2463 | 0.95277 | 0.83804 | 0.75392 | 0.73032 | 0.7089
43602.5681 | 1.1097 | 1.3188 | 1.2458 | 0.95199 | 0.83705 | 0.75347 | 0.72964 | 0.70906
43602.5681 | 1.1094 | 1.3198 | 1.2453 | 0.95302 | 0.83711 | 0.75346 | 0.72953 | 0.709
43602.568 | 1.1042 | 1.3112 | 1.2372 | 0.94816 | 0.83298 | 0.75019 | 0.72677 | 0.70763
43602.5682 | 1.1 | 1.308 | 1.2336 | 0.94681 | 0.83212 | 0.74913 | 0.7284 | 0.70683
43602.5682 | 1.0995 | 1.3055 | 1.2325 | 0.94645 | 0.83172 | 0.74899 | 0.72625 | 0.70712
43602.5682 | 1.1004 | 1.3046 | 1.2313 | 0.9453 | 0.83098 | 0.74822 | 0.72568 | 0.70693
43602.5682 | 1.1114 | 1.3119 | 1.2343 | 0.95104 | 0.83391 | 0.74986 | 0.72679 | 0.70686
43602.5684 | 1.1139 | 1.3148 | 1.2379 | 0.95371 | 0.83708 | 0.75184 | 0.73043 | 0.70689
43602.5684 | 1.1216 | 1.319 | 1.2397 | 0.95702 | 0.83856 | 0.75308 | 0.72974 | 0.70751
43602.5684 | 1.1148 | 1.3185 | 1.2407 | 0.95678 | 0.83953 | 0.75361 | 0.73009 | 0.70735
43602.5684 | 1.125 | 1.3224 | 1.2435 | 0.96015 | 0.84276 | 0.75653 | 0.73629 | 0.70866
43602.5686 | 1.1148 | 1.317 | 1.2395 | 0.95762 | 0.84145 | 0.75594 | 0.73303 | 0.70835
43602.5686 | 1.1202 | 1.3183 | 1.2398 | 0.95805 | 0.84157 | 0.75568 | 0.73153 | 0.70851
43602.5686 | 1.1197 | 1.3178 | 1.2394 | 0.95777 | 0.84064 | 0.75562 | 0.73356 | 0.70813
43602.5685 | 1.1092 | 1.3152 | 1.2392 | 0.95554 | 0.84113 | 0.75605 | 0.73304 | 0.70936
43602.5687 | 1.1103 | 1.3121 | 1.2363 | 0.95386 | 0.83804 | 0.75444 | 0.73481 | 0.70933
43602.5687 | 1.1093 | 1.3103 | 1.2349 | 0.95158 | 0.8378 | 0.75484 | 0.73189 | 0.709
43602.5688 | 1.1102 | 1.3097 | 1.234 | 0.95147 | 0.8365 | 0.75361 | 0.73085 | 0.70892
43602.5687 | 1.1019 | 1.3062 | 1.2296 | 0.9476 | 0.8334 | 0.75142 | 0.7293 | 0.7085
43602.5689 | 1.0903 | 1.2958 | 1.2227 | 0.94078 | 0.82842 | 0.74792 | 0.72572 | 0.70756
43602.5689 | 1.0913 | 1.2948 | 1.2217 | 0.94037 | 0.82815 | 0.74729 | 0.72833 | 0.7077
43602.5689 | 1.0884 | 1.2934 | 1.2203 | 0.93964 | 0.82738 | 0.74709 | 0.72577 | 0.70715
43602.5689 | 1.0861 | 1.2886 | 1.2159 | 0.93595 | 0.82469 | 0.74498 | 0.72221 | 0.70686
43602.5691 | 1.0789 | 1.2811 | 1.209 | 0.93084 | 0.82118 | 0.74218 | 0.72342 | 0.70592
43602.5691 | 1.0804 | 1.2816 | 1.2091 | 0.93161 | 0.82078 | 0.74143 | 0.71995 | 0.70541
43602.5691 | 1.0683 | 1.279 | 1.2096 | 0.93147 | 0.82068 | 0.74229 | 0.72048 | 0.70613
43602.5691 | 1.0676 | 1.2724 | 1.2007 | 0.92629 | 0.81609 | 0.73835 | 0.71979 | 0.70494
43602.5693 | 1.0742 | 1.2781 | 1.2054 | 0.92953 | 0.81811 | 0.73948 | 0.7223 | 0.70486
43602.5693 | 1.0695 | 1.2788 | 1.2075 | 0.93052 | 0.81941 | 0.74025 | 0.72013 | 0.70494
43602.5693 | 1.0762 | 1.2827 | 1.2092 | 0.93292 | 0.82002 | 0.74127 | 0.71993 | 0.70567
43602.5692 | 1.0835 | 1.2898 | 1.215 | 0.93774 | 0.82519 | 0.74469 | 0.72304 | 0.70632
43602.5694 | 1.092 | 1.2933 | 1.2165 | 0.93974 | 0.82612 | 0.74498 | 0.72342 | 0.70632
43602.5694 | 1.0869 | 1.2913 | 1.2166 | 0.93767 | 0.82615 | 0.74511 | 0.72256 | 0.70599
43602.5695 | 1.0922 | 1.2935 | 1.2182 | 0.93967 | 0.82585 | 0.74544 | 0.7242 | 0.7067
43602.5694 | 1.0881 | 1.2921 | 1.2176 | 0.93905 | 0.82599 | 0.74549 | 0.72379 | 0.7067
43602.5696 | 1.0934 | 1.2973 | 1.222 | 0.94318 | 0.82879 | 0.74716 | 0.72697 | 0.70737
43602.5696 | 1.0917 | 1.297 | 1.2221 | 0.94123 | 0.82885 | 0.74773 | 0.72534 | 0.70741
43602.5696 | 1.0924 | 1.2976 | 1.2229 | 0.9425 | 0.82931 | 0.74805 | 0.72545 | 0.70745
43602.5696 | 1.0864 | 1.2963 | 1.2231 | 0.94208 | 0.82895 | 0.74788 | 0.7254 | 0.70794
43602.5698 | 1.084 | 1.2907 | 1.2187 | 0.93768 | 0.82599 | 0.74594 | 0.72393 | 0.70692
43602.5698 | 1.0868 | 1.2921 | 1.2189 | 0.93869 | 0.82642 | 0.74621 | 0.72392 | 0.70748
43602.5698 | 1.082 | 1.2884 | 1.2174 | 0.93598 | 0.82555 | 0.74542 | 0.72382 | 0.70723
43602.5698 | 1.0788 | 1.2835 | 1.2133 | 0.93365 | 0.8221 | 0.74296 | 0.72194 | 0.70662
43602.57 | 1.076 | 1.2845 | 1.2142 | 0.93297 | 0.82276 | 0.74311 | 0.72143 | 0.7063
43602.57 | 1.0819 | 1.2877 | 1.2138 | 0.9348 | 0.82357 | 0.74371 | 0.72117 | 0.70717
43602.57 | 1.0788 | 1.286 | 1.2151 | 0.93434 | 0.82356 | 0.74353 | 0.72448 | 0.7067
43602.5699 | 1.0809 | 1.2868 | 1.2157 | 0.93472 | 0.82441 | 0.7442 | 0.72289 | 0.70699
43602.5701 | 1.073 | 1.2831 | 1.2145 | 0.93373 | 0.82378 | 0.74383 | 0.72182 | 0.70695
43602.5701 | 1.0716 | 1.2824 | 1.2142 | 0.93293 | 0.82361 | 0.74435 | 0.72271 | 0.70724
43602.5701 | 1.0756 | 1.2844 | 1.2149 | 0.93356 | 0.82403 | 0.74421 | 0.72249 | 0.70751
43602.5701 | 1.076 | 1.2813 | 1.2112 | 0.93183 | 0.82136 | 0.7423 | 0.72556 | 0.70668
43602.5703 | 1.0697 | 1.2779 | 1.2097 | 0.9314 | 0.81995 | 0.74106 | 0.71921 | 0.70641
43602.5703 | 1.073 | 1.2783 | 1.2094 | 0.93078 | 0.82109 | 0.74248 | 0.72278 | 0.70705
43602.5703 | 1.0749 | 1.2788 | 1.2099 | 0.93121 | 0.82117 | 0.74239 | 0.72105 | 0.70661
43602.5703 | 1.0811 | 1.2819 | 1.2108 | 0.93207 | 0.8224 | 0.74273 | 0.72234 | 0.70677
43602.5705 | 1.0855 | 1.289 | 1.218 | 0.93722 | 0.82595 | 0.74533 | 0.72395 | 0.70735
43602.5705 | 1.092 | 1.2923 | 1.2199 | 0.9386 | 0.82724 | 0.7462 | 0.72417 | 0.70788
43602.5705 | 1.0899 | 1.2918 | 1.2189 | 0.93917 | 0.8272 | 0.74623 | 0.72386 | 0.70784
43602.5705 | 1.0914 | 1.2926 | 1.221 | 0.93981 | 0.82808 | 0.74728 | 0.725 | 0.70772
43602.5706 | 1.095 | 1.2957 | 1.225 | 0.94092 | 0.83201 | 0.74995 | 0.72742 | 0.70925
43602.5707 | 1.0925 | 1.296 | 1.2257 | 0.94093 | 0.82946 | 0.74876 | 0.72666 | 0.70853
43602.5707 | 1.0912 | 1.299 | 1.2276 | 0.94314 | 0.83078 | 0.74938 | 0.73079 | 0.70936
43602.5706 | 1.0976 | 1.3016 | 1.2284 | 0.94391 | 0.83202 | 0.75058 | 0.73051 | 0.70964
43602.5708 | 1.0935 | 1.301 | 1.2298 | 0.94353 | 0.83141 | 0.75067 | 0.73006 | 0.7098
43602.5708 | 1.0896 | 1.3033 | 1.2317 | 0.94556 | 0.83259 | 0.7516 | 0.72947 | 0.71052
43602.5708 | 1.0976 | 1.3039 | 1.2304 | 0.9448 | 0.83314 | 0.75175 | 0.7295 | 0.71013
43602.5708 | 1.0876 | 1.3001 | 1.2305 | 0.94273 | 0.83297 | 0.75215 | 0.72989 | 0.71025
43602.571 | 1.086 | 1.2952 | 1.2256 | 0.93956 | 0.82978 | 0.74968 | 0.72769 | 0.71038
43602.571 | 1.0886 | 1.2947 | 1.2249 | 0.93909 | 0.82994 | 0.74972 | 0.72779 | 0.71031
43602.571 | 1.0694 | 1.2781 | 1.2113 | 0.92901 | 0.82066 | 0.74248 | 0.72219 | 0.70835
43602.5714 | 1.0661 | 1.2721 | 1.2058 | 0.92474 | 0.8172 | 0.7393 | 0.71946 | 0.70631
43602.5714 | 1.072 | 1.2732 | 1.2052 | 0.92495 | 0.81702 | 0.73931 | 0.71841 | 0.70608
43602.5714 | 1.0694 | 1.2737 | 1.2045 | 0.92566 | 0.81737 | 0.73913 | 0.7181 | 0.70641
43602.5714 | 1.0703 | 1.2718 | 1.2008 | 0.92375 | 0.81589 | 0.73742 | 0.71655 | 0.70454
43602.5716 | 1.0789 | 1.2824 | 1.2095 | 0.93184 | 0.81953 | 0.73948 | 0.71871 | 0.7042
43602.5716 | 1.0837 | 1.2858 | 1.2113 | 0.93345 | 0.82124 | 0.74049 | 0.71931 | 0.70448
43602.5716 | 1.0849 | 1.2887 | 1.2152 | 0.93551 | 0.8227 | 0.74184 | 0.71835 | 0.70493
43602.5716 | 1.1071 | 1.3098 | 1.2317 | 0.95197 | 0.83604 | 0.75161 | 0.72874 | 0.7074
43602.5718 | 1.1174 | 1.3155 | 1.2357 | 0.9573 | 0.84087 | 0.75538 | 0.73228 | 0.70829
43602.5718 | 1.1254 | 1.3157 | 1.2356 | 0.95717 | 0.84237 | 0.75653 | 0.73293 | 0.70873
43602.5718 | 1.1187 | 1.3159 | 1.2361 | 0.95809 | 0.84103 | 0.75569 | 0.73343 | 0.70845
43602.5717 | 1.1183 | 1.3173 | 1.2376 | 0.95974 | 0.84314 | 0.7577 | 0.73608 | 0.71002
43602.5719 | 1.1083 | 1.3152 | 1.2363 | 0.95698 | 0.8412 | 0.75773 | 0.73729 | 0.71124
43602.5719 | 1.112 | 1.3111 | 1.2348 | 0.95501 | 0.84166 | 0.7582 | 0.73537 | 0.71146
43602.572 | 1.1089 | 1.3123 | 1.2351 | 0.9554 | 0.83983 | 0.75737 | 0.73442 | 0.71149
43602.5719 | 1.0998 | 1.3007 | 1.227 | 0.94621 | 0.83514 | 0.75408 | 0.73179 | 0.712
43602.5721 | 1.0915 | 1.2932 | 1.2219 | 0.94018 | 0.83053 | 0.7508 | 0.72974 | 0.71113
43602.5721 | 1.0835 | 1.2909 | 1.2211 | 0.93906 | 0.83017 | 0.75074 | 0.72962 | 0.71108
43602.5721 | 1.083 | 1.2909 | 1.2209 | 0.93877 | 0.82982 | 0.75025 | 0.72859 | 0.71079
43602.5721 | 1.0783 | 1.287 | 1.2174 | 0.93482 | 0.82674 | 0.74769 | 0.72705 | 0.71016
43602.5723 | 1.0783 | 1.2917 | 1.2226 | 0.93728 | 0.82675 | 0.74772 | 0.72986 | 0.70989
43602.5723 | 1.082 | 1.2936 | 1.2245 | 0.93772 | 0.8284 | 0.7487 | 0.72745 | 0.71001
43602.5723 | 1.0842 | 1.2969 | 1.2261 | 0.93894 | 0.82849 | 0.74841 | 0.72653 | 0.71005
43602.5723 | 1.0946 | 1.3079 | 1.238 | 0.94597 | 0.8346 | 0.75306 | 0.73018 | 0.71147
43602.5725 | 1.1072 | 1.318 | 1.2467 | 0.95171 | 0.83892 | 0.75613 | 0.7364 | 0.71169
43602.5725 | 1.1118 | 1.321 | 1.2468 | 0.95339 | 0.83968 | 0.75669 | 0.73555 | 0.71242
43602.5725 | 1.105 | 1.3203 | 1.2488 | 0.95318 | 0.84073 | 0.7574 | 0.734 | 0.71209
43602.5725 | 1.1139 | 1.3249 | 1.2516 | 0.95694 | 0.84294 | 0.75942 | 0.73589 | 0.71321
43602.5726 | 1.1162 | 1.3239 | 1.2511 | 0.9564 | 0.84235 | 0.75943 | 0.73764 | 0.71286
43602.5727 | 1.1112 | 1.3198 | 1.2501 | 0.95435 | 0.84229 | 0.75931 | 0.73942 | 0.71289
43602.5727 | 1.1142 | 1.3228 | 1.2497 | 0.95432 | 0.84187 | 0.75889 | 0.73634 | 0.71303
43602.5726 | 1.1106 | 1.3211 | 1.2488 | 0.95494 | 0.84205 | 0.75885 | 0.73751 | 0.71315
43602.5728 | 1.1058 | 1.3187 | 1.2491 | 0.95425 | 0.84226 | 0.75936 | 0.7347 | 0.71338
43602.5728 | 1.1162 | 1.3236 | 1.2499 | 0.95662 | 0.84277 | 0.75976 | 0.7381 | 0.71342
43602.5728 | 1.1066 | 1.3214 | 1.2499 | 0.95597 | 0.8441 | 0.76011 | 0.73662 | 0.71331
43602.5728 | 1.1117 | 1.3217 | 1.2481 | 0.95587 | 0.84279 | 0.7598 | 0.73694 | 0.71319
43602.573 | 1.1094 | 1.323 | 1.2482 | 0.95723 | 0.84418 | 0.7598 | 0.73608 | 0.71257
43602.573 | 1.1153 | 1.3217 | 1.2478 | 0.95558 | 0.84292 | 0.75972 | 0.73623 | 0.71303
43602.573 | 1.109 | 1.3217 | 1.2472 | 0.95661 | 0.84337 | 0.76005 | 0.7362 | 0.71303
43602.573 | 1.12 | 1.3253 | 1.249 | 0.95807 | 0.8442 | 0.76091 | 0.73767 | 0.71306
43602.5732 | 1.1173 | 1.3277 | 1.2511 | 0.96057 | 0.84582 | 0.76185 | 0.73894 | 0.71406
43602.5732 | 1.1222 | 1.3283 | 1.2508 | 0.96097 | 0.84694 | 0.76257 | 0.73905 | 0.71373
43602.5732 | 1.1179 | 1.3269 | 1.2511 | 0.96071 | 0.8467 | 0.7625 | 0.73868 | 0.71387
43602.5732 | 1.1164 | 1.3289 | 1.2525 | 0.96152 | 0.84739 | 0.76333 | 0.74116 | 0.71433
43602.5733 | 1.1213 | 1.3279 | 1.2515 | 0.96081 | 0.84779 | 0.76343 | 0.74346 | 0.71373
43602.5734 | 1.1195 | 1.3291 | 1.2512 | 0.96237 | 0.84816 | 0.76388 | 0.74008 | 0.71473
43602.5734 | 1.1188 | 1.3263 | 1.2499 | 0.96124 | 0.84792 | 0.76368 | 0.7395 | 0.71422
43602.5733 | 1.1195 | 1.3252 | 1.2488 | 0.95969 | 0.84676 | 0.7625 | 0.73958 | 0.71376
43602.5735 | 1.1217 | 1.3299 | 1.2522 | 0.96312 | 0.84815 | 0.76349 | 0.73985 | 0.7136
43602.5735 | 1.1238 | 1.3285 | 1.251 | 0.96147 | 0.84757 | 0.76344 | 0.74062 | 0.71353
43602.5735 | 1.1252 | 1.3299 | 1.2524 | 0.9631 | 0.84751 | 0.76313 | 0.73993 | 0.71332
43602.5735 | 1.1263 | 1.3332 | 1.2559 | 0.96558 | 0.85008 | 0.76514 | 0.74107 | 0.71424
43602.5737 | 1.1189 | 1.3283 | 1.2535 | 0.96269 | 0.85004 | 0.76475 | 0.74051 | 0.71422
43602.5737 | 1.1222 | 1.3296 | 1.2521 | 0.96353 | 0.8481 | 0.76347 | 0.74109 | 0.71373
43602.5737 | 1.1238 | 1.3256 | 1.2498 | 0.96047 | 0.84712 | 0.76268 | 0.74199 | 0.71292
43602.5737 | 1.1138 | 1.319 | 1.2436 | 0.95659 | 0.84325 | 0.75982 | 0.73656 | 0.71222
43602.5739 | 1.1109 | 1.3167 | 1.2418 | 0.95544 | 0.84229 | 0.75864 | 0.73724 | 0.71203
43602.5739 | 1.118 | 1.3184 | 1.2422 | 0.95663 | 0.84212 | 0.75868 | 0.73726 | 0.71175
43602.5739 | 1.1113 | 1.3185 | 1.2426 | 0.95635 | 0.84281 | 0.75909 | 0.73618 | 0.71194
43602.5739 | 1.1203 | 1.3225 | 1.2447 | 0.95908 | 0.84513 | 0.7603 | 0.73665 | 0.71206
43602.5741 | 1.1234 | 1.3278 | 1.2496 | 0.96273 | 0.84598 | 0.76162 | 0.73814 | 0.71274
43602.5741 | 1.1268 | 1.3301 | 1.2517 | 0.96431 | 0.84836 | 0.76278 | 0.7389 | 0.71276
43602.5741 | 1.1276 | 1.332 | 1.252 | 0.96571 | 0.84969 | 0.76362 | 0.73981 | 0.71328
43602.574 | 1.1296 | 1.3316 | 1.2533 | 0.96463 | 0.84902 | 0.76335 | 0.74038 | 0.71293
43602.5742 | 1.1286 | 1.3314 | 1.2527 | 0.96483 | 0.85044 | 0.76375 | 0.73965 | 0.71275
43602.5742 | 1.1263 | 1.3301 | 1.2525 | 0.96493 | 0.84974 | 0.76336 | 0.73976 | 0.71238
43602.5743 | 1.1307 | 1.3319 | 1.2531 | 0.96497 | 0.84998 | 0.76381 | 0.74332 | 0.71291
43602.5742 | 1.1194 | 1.3268 | 1.2498 | 0.96231 | 0.8485 | 0.76332 | 0.74311 | 0.71374
43602.5744 | 1.1205 | 1.3212 | 1.2446 | 0.95789 | 0.84469 | 0.76041 | 0.73693 | 0.71244
43602.5744 | 1.1208 | 1.3225 | 1.245 | 0.95837 | 0.8453 | 0.76064 | 0.74052 | 0.71239
43602.5744 | 1.1193 | 1.3209 | 1.2442 | 0.95709 | 0.84376 | 0.75955 | 0.73621 | 0.71159
43602.5744 | 1.1141 | 1.3148 | 1.2389 | 0.94989 | 0.83661 | 0.7528 | 0.72866 | 0.70762
43602.5746 | 1.1144 | 1.3162 | 1.2404 | 0.95185 | 0.83543 | 0.75137 | 0.72877 | 0.70607
43602.5746 | 1.1143 | 1.3179 | 1.2408 | 0.95203 | 0.83709 | 0.75221 | 0.72848 | 0.70628
43602.5746 | 1.1104 | 1.3177 | 1.2417 | 0.95221 | 0.83631 | 0.75187 | 0.72858 | 0.70626
43602.5746 | 1.1129 | 1.3206 | 1.2436 | 0.9536 | 0.8375 | 0.75271 | 0.72848 | 0.70564
43602.5748 | 1.1129 | 1.3157 | 1.2394 | 0.94991 | 0.83424 | 0.75008 | 0.72564 | 0.70437
43602.5748 | 1.1101 | 1.3131 | 1.2372 | 0.94776 | 0.83272 | 0.74866 | 0.72467 | 0.70393
43602.5748 | 1.1132 | 1.3137 | 1.2375 | 0.94783 | 0.83245 | 0.74843 | 0.72321 | 0.70357
43602.5747 | 1.1085 | 1.3113 | 1.2362 | 0.94607 | 0.83134 | 0.74708 | 0.72277 | 0.70301
43602.5749 | 1.1048 | 1.309 | 1.2342 | 0.94417 | 0.83057 | 0.74574 | 0.72234 | 0.70218
43602.5749 | 1.1062 | 1.3089 | 1.2339 | 0.9438 | 0.82913 | 0.74537 | 0.72138 | 0.70181
43602.575 | 1.1001 | 1.3083 | 1.2339 | 0.94376 | 0.8291 | 0.74498 | 0.72199 | 0.70181
43602.5749 | 1.1025 | 1.308 | 1.2321 | 0.94299 | 0.82754 | 0.74386 | 0.72368 | 0.70138
43602.5751 | 1.1031 | 1.3033 | 1.2289 | 0.94108 | 0.82578 | 0.74204 | 0.71801 | 0.7005
43602.5751 | 1.1037 | 1.3034 | 1.2288 | 0.9409 | 0.82496 | 0.74196 | 0.71809 | 0.7002
43602.5751 | 1.109 | 1.3044 | 1.229 | 0.94122 | 0.8251 | 0.74219 | 0.72131 | 0.69987
43602.5751 | 1.1049 | 1.3017 | 1.2263 | 0.9394 | 0.8239 | 0.74079 | 0.71719 | 0.69931
43602.5753 | 1.1081 | 1.2994 | 1.2231 | 0.93866 | 0.82308 | 0.73966 | 0.71659 | 0.69909
43602.5753 | 1.1009 | 1.3003 | 1.224 | 0.93945 | 0.82231 | 0.73934 | 0.71661 | 0.69848
43602.5753 | 1.0946 | 1.2971 | 1.2235 | 0.93742 | 0.82273 | 0.73958 | 0.71657 | 0.69886
43602.5753 | 1.1017 | 1.2994 | 1.2237 | 0.93903 | 0.82413 | 0.74022 | 0.71712 | 0.69915
43602.5755 | 1.0978 | 1.3024 | 1.2263 | 0.94144 | 0.82576 | 0.74146 | 0.71788 | 0.69923
43602.5755 | 1.0981 | 1.304 | 1.2274 | 0.94276 | 0.82512 | 0.74131 | 0.71825 | 0.69922
43602.5755 | 1.1094 | 1.3066 | 1.229 | 0.94459 | 0.82668 | 0.74229 | 0.72301 | 0.69927
43602.5755 | 1.1109 | 1.3113 | 1.233 | 0.94766 | 0.82939 | 0.74453 | 0.72303 | 0.69957
43602.5756 | 1.1159 | 1.3161 | 1.2366 | 0.95047 | 0.83267 | 0.74658 | 0.72242 | 0.70042
43602.5757 | 1.1237 | 1.3149 | 1.2361 | 0.94996 | 0.83238 | 0.74654 | 0.72112 | 0.70016
43602.5757 | 1.122 | 1.3175 | 1.2386 | 0.95168 | 0.83321 | 0.74655 | 0.72191 | 0.70026
43602.5756 | 1.1272 | 1.3227 | 1.2431 | 0.95392 | 0.836 | 0.74899 | 0.72425 | 0.70126
43602.5758 | 1.1251 | 1.3266 | 1.2476 | 0.95671 | 0.83801 | 0.75048 | 0.72903 | 0.70202
43602.5758 | 1.1214 | 1.3242 | 1.2463 | 0.95462 | 0.83727 | 0.75028 | 0.72596 | 0.70197
43602.5758 | 1.1341 | 1.3258 | 1.2468 | 0.95643 | 0.83736 | 0.75037 | 0.72508 | 0.70186
43602.5758 | 1.1316 | 1.3281 | 1.2491 | 0.95627 | 0.83803 | 0.75082 | 0.72667 | 0.70297
43602.576 | 1.1232 | 1.3248 | 1.2472 | 0.95362 | 0.8346 | 0.74887 | 0.72488 | 0.70235
43602.576 | 1.1198 | 1.3217 | 1.246 | 0.95182 | 0.83575 | 0.74972 | 0.72545 | 0.70265
43602.576 | 1.1178 | 1.321 | 1.2457 | 0.9513 | 0.83412 | 0.74839 | 0.72415 | 0.70248
43602.576 | 1.1084 | 1.3162 | 1.2409 | 0.9475 | 0.83066 | 0.74596 | 0.72237 | 0.70175
43602.5762 | 1.1013 | 1.3074 | 1.2343 | 0.94115 | 0.82672 | 0.74315 | 0.71926 | 0.70032
43602.5762 | 1.0988 | 1.3075 | 1.2349 | 0.94083 | 0.82601 | 0.74249 | 0.71978 | 0.70032
43602.5762 | 1.0974 | 1.3062 | 1.2337 | 0.93995 | 0.82534 | 0.74227 | 0.71815 | 0.70037
43602.5762 | 1.1005 | 1.3056 | 1.2324 | 0.93864 | 0.82349 | 0.74056 | 0.71869 | 0.6996
43602.5764 | 1.0992 | 1.3049 | 1.2309 | 0.93919 | 0.82324 | 0.73986 | 0.71665 | 0.69917
43602.5764 | 1.0994 | 1.3059 | 1.2313 | 0.94023 | 0.82415 | 0.73992 | 0.71957 | 0.69958
43602.5764 | 1.0991 | 1.3032 | 1.2297 | 0.9381 | 0.82323 | 0.73953 | 0.71701 | 0.69902
43602.5763 | 1.1028 | 1.3053 | 1.2306 | 0.9412 | 0.82493 | 0.74106 | 0.7173 | 0.69907
43602.5765 | 1.1118 | 1.3121 | 1.2345 | 0.94566 | 0.82702 | 0.74269 | 0.72167 | 0.69965
43602.5765 | 1.1158 | 1.3123 | 1.2347 | 0.94622 | 0.82898 | 0.7439 | 0.72081 | 0.69988
43602.5766 | 1.1144 | 1.3126 | 1.2351 | 0.94652 | 0.82935 | 0.74401 | 0.72021 | 0.69995
43602.5765 | 1.1178 | 1.3114 | 1.2335 | 0.94661 | 0.82876 | 0.74372 | 0.71992 | 0.69968
43602.5767 | 1.1098 | 1.3076 | 1.2306 | 0.94419 | 0.82644 | 0.74196 | 0.7189 | 0.69921
43602.5767 | 1.1124 | 1.3081 | 1.2308 | 0.94495 | 0.82676 | 0.74179 | 0.71869 | 0.69929
43602.5767 | 1.104 | 1.3063 | 1.2299 | 0.94448 | 0.82734 | 0.74256 | 0.7195 | 0.69938
43602.5767 | 1.0987 | 1.2988 | 1.2238 | 0.93804 | 0.82238 | 0.73926 | 0.7174 | 0.69826
43602.5769 | 1.098 | 1.2929 | 1.2169 | 0.93482 | 0.8194 | 0.73705 | 0.71532 | 0.69776
43602.5769 | 1.0918 | 1.2893 | 1.215 | 0.93247 | 0.81765 | 0.73566 | 0.71387 | 0.6973
43602.5769 | 1.0923 | 1.2898 | 1.2147 | 0.93302 | 0.81747 | 0.73556 | 0.71315 | 0.69739
43602.5769 | 1.0895 | 1.2894 | 1.213 | 0.93208 | 0.81558 | 0.73386 | 0.71472 | 0.69687
43602.5771 | 1.0919 | 1.2895 | 1.2119 | 0.93166 | 0.81652 | 0.73449 | 0.71537 | 0.69684
43602.5771 | 1.0877 | 1.2893 | 1.2135 | 0.93242 | 0.81644 | 0.73452 | 0.71272 | 0.69658
43602.5771 | 1.0898 | 1.2892 | 1.213 | 0.93144 | 0.81568 | 0.73391 | 0.71218 | 0.69649
43602.5771 | 1.0961 | 1.2939 | 1.2165 | 0.93554 | 0.81794 | 0.73548 | 0.71346 | 0.69678
43602.5772 | 1.0982 | 1.2962 | 1.2191 | 0.93756 | 0.82032 | 0.73681 | 0.71775 | 0.69718
43602.5773 | 1.0942 | 1.2934 | 1.2174 | 0.93523 | 0.8193 | 0.73621 | 0.71489 | 0.69695
43602.5773 | 1.0983 | 1.296 | 1.2184 | 0.93632 | 0.81945 | 0.7365 | 0.71381 | 0.69729
43602.5772 | 1.1004 | 1.3011 | 1.2238 | 0.93872 | 0.82182 | 0.73824 | 0.71758 | 0.69788
43602.5774 | 1.104 | 1.3068 | 1.229 | 0.94214 | 0.8243 | 0.73985 | 0.71777 | 0.69871
43602.5774 | 1.105 | 1.3038 | 1.2276 | 0.93979 | 0.82438 | 0.74037 | 0.71835 | 0.69912
43602.5775 | 1.1079 | 1.3054 | 1.2286 | 0.94056 | 0.82379 | 0.74007 | 0.71759 | 0.69892
43602.5774 | 1.0989 | 1.3035 | 1.2273 | 0.93822 | 0.82192 | 0.73909 | 0.71711 | 0.69904
43602.5776 | 1.0852 | 1.2943 | 1.2235 | 0.93182 | 0.81876 | 0.73752 | 0.7156 | 0.69909
43602.5776 | 1.0817 | 1.2912 | 1.2221 | 0.92972 | 0.81686 | 0.73561 | 0.71399 | 0.69839
43602.5776 | 1.0869 | 1.2933 | 1.2223 | 0.93063 | 0.81675 | 0.73567 | 0.71374 | 0.69841
43602.5776 | 1.0827 | 1.2918 | 1.2221 | 0.92922 | 0.81527 | 0.73457 | 0.71291 | 0.69932
43602.5778 | 1.0746 | 1.2882 | 1.2211 | 0.92593 | 0.81384 | 0.73372 | 0.71186 | 0.69897
43602.5778 | 1.0773 | 1.2884 | 1.2211 | 0.92571 | 0.81303 | 0.7333 | 0.71164 | 0.69864
43602.5778 | 1.0743 | 1.2894 | 1.2209 | 0.92648 | 0.81388 | 0.7332 | 0.71132 | 0.69877
43602.5778 | 1.0778 | 1.2938 | 1.2261 | 0.92829 | 0.81604 | 0.73468 | 0.71214 | 0.69917
43602.578 | 1.084 | 1.2995 | 1.2315 | 0.93236 | 0.81822 | 0.73604 | 0.71608 | 0.69933
43602.578 | 1.0873 | 1.302 | 1.2326 | 0.93331 | 0.81932 | 0.73682 | 0.71401 | 0.69959
43602.578 | 1.0848 | 1.3009 | 1.2335 | 0.93291 | 0.81969 | 0.73709 | 0.71406 | 0.69971
43602.578 | 1.096 | 1.3153 | 1.245 | 0.94086 | 0.82531 | 0.742 | 0.71806 | 0.70079
43602.5781 | 1.1002 | 1.3189 | 1.2491 | 0.94451 | 0.82816 | 0.74415 | 0.72085 | 0.70164
43602.5782 | 1.0978 | 1.3183 | 1.2491 | 0.94392 | 0.8282 | 0.7444 | 0.72014 | 0.70161
43602.5782 | 1.0996 | 1.3176 | 1.2481 | 0.94236 | 0.82738 | 0.74374 | 0.71964 | 0.70125
43602.5781 | 1.1001 | 1.3176 | 1.2482 | 0.9423 | 0.82646 | 0.7429 | 0.71902 | 0.70082
43602.5783 | 1.0969 | 1.3143 | 1.2464 | 0.94017 | 0.82559 | 0.74236 | 0.71869 | 0.70101
43602.5783 | 1.0943 | 1.3149 | 1.2475 | 0.94057 | 0.82588 | 0.74238 | 0.71824 | 0.70116
43602.5783 | 1.0949 | 1.3139 | 1.2458 | 0.9395 | 0.82414 | 0.74193 | 0.71796 | 0.70059
43602.5783 | 1.0907 | 1.3078 | 1.2417 | 0.93535 | 0.82175 | 0.73996 | 0.71626 | 0.70006
43602.5785 | 1.0844 | 1.3014 | 1.2362 | 0.93279 | 0.81976 | 0.73796 | 0.71602 | 0.6993
43602.5785 | 1.0813 | 1.3 | 1.2352 | 0.93084 | 0.81838 | 0.73675 | 0.71426 | 0.69917
43602.5785 | 1.0868 | 1.3011 | 1.2351 | 0.93096 | 0.81748 | 0.73623 | 0.713 | 0.69907
43602.5785 | 1.0759 | 1.2946 | 1.2293 | 0.92781 | 0.81414 | 0.73332 | 0.71143 | 0.69752
43602.5787 | 1.082 | 1.2937 | 1.2275 | 0.92639 | 0.81341 | 0.73283 | 0.71104 | 0.69756
43602.5787 | 1.0805 | 1.2944 | 1.2278 | 0.92753 | 0.81342 | 0.7322 | 0.71048 | 0.69713
43602.5787 | 1.0779 | 1.2924 | 1.2277 | 0.92666 | 0.81389 | 0.7329 | 0.71149 | 0.69765
43602.5787 | 1.088 | 1.299 | 1.2311 | 0.93011 | 0.81539 | 0.73374 | 0.71148 | 0.69666
43602.5789 | 1.0924 | 1.3041 | 1.2355 | 0.93414 | 0.81841 | 0.73589 | 0.71348 | 0.69691
43602.5789 | 1.1001 | 1.3074 | 1.2367 | 0.93584 | 0.81951 | 0.73682 | 0.71398 | 0.69752
43602.5789 | 1.0968 | 1.3066 | 1.2372 | 0.93602 | 0.82039 | 0.73724 | 0.71333 | 0.69734
43602.5788 | 1.0994 | 1.3084 | 1.2394 | 0.9386 | 0.82336 | 0.73951 | 0.71587 | 0.69812
43602.579 | 1.0993 | 1.3059 | 1.2353 | 0.93818 | 0.82361 | 0.73957 | 0.71606 | 0.69787
43602.5791 | 1.101 | 1.3059 | 1.235 | 0.93728 | 0.82114 | 0.73836 | 0.71447 | 0.69722
43602.5791 | 1.1062 | 1.3083 | 1.2356 | 0.93914 | 0.82239 | 0.73843 | 0.71445 | 0.69757
43602.579 | 1.0985 | 1.3065 | 1.2352 | 0.9396 | 0.8228 | 0.73872 | 0.71617 | 0.69769
43602.5792 | 1.097 | 1.3019 | 1.2298 | 0.93641 | 0.82046 | 0.73677 | 0.71312 | 0.6966
43602.5792 | 1.1003 | 1.3009 | 1.2286 | 0.93618 | 0.82012 | 0.73667 | 0.71713 | 0.69708
43602.5792 | 1.0973 | 1.2992 | 1.2279 | 0.93498 | 0.81912 | 0.73593 | 0.71321 | 0.69679
43602.5792 | 1.0934 | 1.2967 | 1.2245 | 0.93224 | 0.81761 | 0.73445 | 0.71204 | 0.69626
43602.5794 | 1.0901 | 1.2888 | 1.2176 | 0.92835 | 0.81384 | 0.73208 | 0.70933 | 0.69544
43602.5794 | 1.0913 | 1.2892 | 1.2175 | 0.92773 | 0.81355 | 0.73164 | 0.71356 | 0.69466
43602.5794 | 1.0873 | 1.2874 | 1.2165 | 0.92739 | 0.81333 | 0.73125 | 0.70945 | 0.695
43602.5794 | 1.0826 | 1.2818 | 1.2108 | 0.92414 | 0.81095 | 0.729 | 0.70676 | 0.69392
43602.5796 | 1.0781 | 1.2827 | 1.2116 | 0.92482 | 0.8097 | 0.72799 | 0.70585 | 0.69322
43602.5796 | 1.0872 | 1.2839 | 1.2116 | 0.92587 | 0.81108 | 0.72882 | 0.7065 | 0.69354
43602.5796 | 1.0838 | 1.2833 | 1.2118 | 0.92534 | 0.81046 | 0.72858 | 0.70687 | 0.69327
43602.5796 | 1.0922 | 1.2891 | 1.2147 | 0.93051 | 0.81285 | 0.73037 | 0.70997 | 0.69348
43602.5798 | 1.099 | 1.2938 | 1.2189 | 0.93395 | 0.81668 | 0.73278 | 0.71285 | 0.69459
43602.5798 | 1.0976 | 1.2928 | 1.2185 | 0.93311 | 0.81645 | 0.73269 | 0.71098 | 0.69393
43602.5798 | 1.0973 | 1.2917 | 1.2179 | 0.93276 | 0.81638 | 0.73299 | 0.71047 | 0.69411
43602.5797 | 1.096 | 1.2954 | 1.2215 | 0.93566 | 0.81824 | 0.73434 | 0.71557 | 0.69556
43602.5799 | 1.0983 | 1.2927 | 1.2198 | 0.93337 | 0.81735 | 0.73404 | 0.71181 | 0.69536
43602.5799 | 1.098 | 1.2938 | 1.22 | 0.93404 | 0.81663 | 0.73356 | 0.71103 | 0.69532
43602.58 | 1.1005 | 1.2942 | 1.2203 | 0.93544 | 0.8179 | 0.73445 | 0.71151 | 0.6959
43602.5799 | 1.0853 | 1.2863 | 1.2152 | 0.92938 | 0.81334 | 0.73133 | 0.70813 | 0.69515
43602.5801 | 1.0779 | 1.2844 | 1.2149 | 0.92639 | 0.81103 | 0.72995 | 0.71075 | 0.69448
43602.5801 | 1.0863 | 1.2876 | 1.2164 | 0.92849 | 0.81203 | 0.73061 | 0.70951 | 0.69521
43602.5801 | 1.0917 | 1.2893 | 1.2173 | 0.92925 | 0.8132 | 0.73077 | 0.70876 | 0.69526
43602.5801 | 1.096 | 1.2964 | 1.2234 | 0.93334 | 0.81641 | 0.7341 | 0.7109 | 0.69629
43602.5803 | 1.0877 | 1.2935 | 1.2246 | 0.93167 | 0.81688 | 0.73473 | 0.71118 | 0.69666
43602.5803 | 1.0895 | 1.2941 | 1.2239 | 0.9311 | 0.81655 | 0.73441 | 0.71396 | 0.69647
43602.5803 | 1.0915 | 1.2941 | 1.2232 | 0.93125 | 0.81585 | 0.73389 | 0.71376 | 0.69635
43602.5803 | 1.087 | 1.2926 | 1.2227 | 0.92985 | 0.81351 | 0.732 | 0.70848 | 0.69615
43602.5805 | 1.079 | 1.2858 | 1.2181 | 0.92521 | 0.81043 | 0.7302 | 0.70727 | 0.69547
43602.5805 | 1.0826 | 1.2867 | 1.2184 | 0.9254 | 0.81153 | 0.73022 | 0.7079 | 0.69575
43602.5805 | 1.0753 | 1.2831 | 1.2166 | 0.923 | 0.8108 | 0.72994 | 0.7115 | 0.69547
43602.5805 | 1.0687 | 1.2782 | 1.2137 | 0.91888 | 0.80744 | 0.72782 | 0.70634 | 0.69488
43602.5807 | 1.0684 | 1.2738 | 1.209 | 0.91638 | 0.80414 | 0.72518 | 0.70572 | 0.69392
43602.5807 | 1.0665 | 1.2729 | 1.2081 | 0.91557 | 0.80453 | 0.72564 | 0.70357 | 0.69381
43602.5807 | 1.0607 | 1.2683 | 1.2033 | 0.91265 | 0.80136 | 0.72281 | 0.70133 | 0.69325
43602.5809 | 1.0568 | 1.2634 | 1.2006 | 0.91006 | 0.80004 | 0.72154 | 0.70033 | 0.69224
43602.5809 | 1.0662 | 1.2682 | 1.2019 | 0.91192 | 0.80004 | 0.7219 | 0.7005 | 0.69247
43602.5809 | 1.0666 | 1.2735 | 1.2065 | 0.91547 | 0.8029 | 0.72368 | 0.70116 | 0.69285
43602.581 | 1.0723 | 1.277 | 1.2115 | 0.91908 | 0.80759 | 0.72745 | 0.70479 | 0.69356
43602.581 | 1.0747 | 1.282 | 1.2141 | 0.92252 | 0.80811 | 0.7279 | 0.70912 | 0.69409
43602.5811 | 1.0821 | 1.2835 | 1.2146 | 0.92261 | 0.80939 | 0.72848 | 0.70655 | 0.69451
43602.581 | 1.0848 | 1.2897 | 1.2199 | 0.9261 | 0.81157 | 0.73041 | 0.70716 | 0.69491
43602.5812 | 1.0877 | 1.2942 | 1.225 | 0.92824 | 0.81574 | 0.73355 | 0.71181 | 0.69584
43602.5812 | 1.0897 | 1.2963 | 1.2267 | 0.92996 | 0.81589 | 0.7337 | 0.71198 | 0.69601
43602.5812 | 1.0914 | 1.2986 | 1.228 | 0.9319 | 0.81725 | 0.7346 | 0.71107 | 0.69629
43602.5812 | 1.0978 | 1.3011 | 1.2302 | 0.93323 | 0.8177 | 0.73538 | 0.7118 | 0.69669
43602.5814 | 1.0764 | 1.29 | 1.2236 | 0.92543 | 0.81359 | 0.73275 | 0.7133 | 0.69587
43602.5814 | 1.074 | 1.2889 | 1.223 | 0.92582 | 0.81289 | 0.73214 | 0.70944 | 0.69535
43602.5814 | 1.0766 | 1.288 | 1.2213 | 0.92462 | 0.81274 | 0.73212 | 0.70849 | 0.69569
43602.5814 | 1.0697 | 1.2801 | 1.2153 | 0.91996 | 0.80812 | 0.72865 | 0.70599 | 0.69439
43602.5816 | 1.0704 | 1.2794 | 1.2159 | 0.9199 | 0.808 | 0.72857 | 0.7056 | 0.69438
43602.5816 | 1.0689 | 1.2784 | 1.2152 | 0.91905 | 0.80791 | 0.72821 | 0.70501 | 0.69439
43602.5816 | 1.0648 | 1.2786 | 1.2148 | 0.9195 | 0.80707 | 0.72815 | 0.70418 | 0.6942
43602.5816 | 1.0619 | 1.2751 | 1.2126 | 0.91687 | 0.80579 | 0.72666 | 0.70376 | 0.69395
43602.5818 | 1.0599 | 1.2702 | 1.2088 | 0.91408 | 0.80371 | 0.72484 | 0.7043 | 0.69289
43602.5818 | 1.0568 | 1.2695 | 1.2085 | 0.91313 | 0.80286 | 0.72491 | 0.70248 | 0.693
43602.5818 | 1.062 | 1.271 | 1.2083 | 0.91325 | 0.80324 | 0.72477 | 0.70243 | 0.69284
43602.5817 | 1.0609 | 1.2701 | 1.2079 | 0.91207 | 0.80246 | 0.72402 | 0.70193 | 0.69231
43602.5819 | 1.065 | 1.2715 | 1.2084 | 0.91325 | 0.80235 | 0.72312 | 0.70129 | 0.69157
43602.5819 | 1.0644 | 1.2735 | 1.2092 | 0.91493 | 0.80316 | 0.72394 | 0.70073 | 0.69184
43602.582 | 1.068 | 1.2733 | 1.2088 | 0.91439 | 0.80338 | 0.72407 | 0.7017 | 0.69195
43602.5819 | 1.0749 | 1.279 | 1.2122 | 0.91796 | 0.80559 | 0.72515 | 0.70119 | 0.6917
43602.5821 | 1.0832 | 1.2845 | 1.2153 | 0.92243 | 0.80844 | 0.72704 | 0.70299 | 0.69146
43602.5821 | 1.082 | 1.2831 | 1.2148 | 0.92114 | 0.808 | 0.72682 | 0.70328 | 0.69157
43602.5821 | 1.076 | 1.2837 | 1.2156 | 0.92229 | 0.80759 | 0.72698 | 0.70774 | 0.69143
43602.5821 | 1.0823 | 1.2844 | 1.2144 | 0.92393 | 0.80768 | 0.72699 | 0.70447 | 0.69144
43602.5823 | 1.0832 | 1.2814 | 1.2132 | 0.92296 | 0.80789 | 0.72679 | 0.70428 | 0.69134
43602.5823 | 1.0816 | 1.2811 | 1.2123 | 0.92279 | 0.80774 | 0.72679 | 0.70407 | 0.69083
43602.5823 | 1.0852 | 1.2825 | 1.2127 | 0.92352 | 0.80827 | 0.72701 | 0.70612 | 0.69111
43602.5823 | 1.0934 | 1.2899 | 1.2188 | 0.92881 | 0.8127 | 0.73027 | 0.70657 | 0.69231
43602.5825 | 1.092 | 1.2907 | 1.2197 | 0.92913 | 0.81432 | 0.73161 | 0.70866 | 0.69292
43602.5825 | 1.0959 | 1.2926 | 1.2208 | 0.93051 | 0.81421 | 0.73162 | 0.70808 | 0.69286
43602.5825 | 1.0999 | 1.2931 | 1.2215 | 0.93119 | 0.81511 | 0.73224 | 0.71074 | 0.6931
43602.5825 | 1.0871 | 1.2853 | 1.2157 | 0.92599 | 0.81158 | 0.73011 | 0.70709 | 0.69268
43602.5827 | 1.0773 | 1.2775 | 1.2096 | 0.92008 | 0.80734 | 0.72757 | 0.70767 | 0.69231
43602.5827 | 1.0725 | 1.274 | 1.2075 | 0.91861 | 0.80614 | 0.7266 | 0.70479 | 0.69197
43602.5827 | 1.072 | 1.2744 | 1.2076 | 0.9196 | 0.80559 | 0.72637 | 0.70397 | 0.69191
43602.5826 | 1.0595 | 1.2658 | 1.2005 | 0.91394 | 0.80131 | 0.72242 | 0.70174 | 0.69095
43602.5828 | 1.0551 | 1.2566 | 1.1932 | 0.90699 | 0.7964 | 0.71892 | 0.69896 | 0.68924
43602.5829 | 1.0553 | 1.2588 | 1.1935 | 0.90704 | 0.79592 | 0.71824 | 0.69816 | 0.68901
43602.5829 | 1.055 | 1.2599 | 1.1939 | 0.90872 | 0.79677 | 0.71876 | 0.69796 | 0.68908
43602.5828 | 1.0616 | 1.2673 | 1.2001 | 0.91244 | 0.79959 | 0.72032 | 0.69845 | 0.6891
43602.583 | 1.0811 | 1.2815 | 1.2113 | 0.92304 | 0.80745 | 0.72565 | 0.70416 | 0.69077
43602.583 | 1.0825 | 1.2837 | 1.2126 | 0.92453 | 0.80846 | 0.72634 | 0.70444 | 0.69066
43602.583 | 1.0853 | 1.286 | 1.2149 | 0.92681 | 0.81054 | 0.72759 | 0.70498 | 0.69107
43602.583 | 1.0953 | 1.2906 | 1.2176 | 0.93006 | 0.81369 | 0.73034 | 0.7074 | 0.69138
43602.5832 | 1.0947 | 1.2874 | 1.2147 | 0.92915 | 0.81414 | 0.7308 | 0.71087 | 0.69125
43602.5832 | 1.0955 | 1.2883 | 1.2143 | 0.92934 | 0.81176 | 0.7294 | 0.70679 | 0.69054
43602.5832 | 1.0914 | 1.2891 | 1.2151 | 0.93041 | 0.81379 | 0.73042 | 0.70684 | 0.69091
43602.5832 | 1.0913 | 1.2855 | 1.2114 | 0.92773 | 0.81139 | 0.72844 | 0.7056 | 0.69034
43602.5834 | 1.0958 | 1.2822 | 1.2067 | 0.92659 | 0.81028 | 0.72766 | 0.70537 | 0.69051
43602.5834 | 1.0913 | 1.2791 | 1.2052 | 0.92521 | 0.81108 | 0.72806 | 0.70558 | 0.69044
43602.5834 | 1.0886 | 1.2819 | 1.2071 | 0.92701 | 0.80984 | 0.72735 | 0.70509 | 0.6901
43602.5834 | 1.0992 | 1.2834 | 1.2079 | 0.9296 | 0.81354 | 0.72989 | 0.70996 | 0.69069
43602.5836 | 1.1238 | 1.3033 | 1.2225 | 0.94255 | 0.82139 | 0.73557 | 0.71357 | 0.6928
43602.5836 | 1.1131 | 1.2986 | 1.22 | 0.93961 | 0.82436 | 0.73791 | 0.71505 | 0.69336
43602.5836 | 1.1147 | 1.3051 | 1.2249 | 0.944 | 0.82429 | 0.73825 | 0.71483 | 0.69362
43602.5836 | 1.1368 | 1.3175 | 1.2366 | 0.9529 | 0.83317 | 0.74508 | 0.72084 | 0.69575
43602.5838 | 1.1471 | 1.3211 | 1.2398 | 0.95569 | 0.83553 | 0.74731 | 0.72336 | 0.69682
43602.5838 | 1.1144 | 1.3169 | 1.2385 | 0.95308 | 0.83468 | 0.74696 | 0.72214 | 0.69719
43602.5838 | 1.1289 | 1.317 | 1.2377 | 0.9526 | 0.83378 | 0.74689 | 0.72332 | 0.69726
43602.5837 | 1.1328 | 1.3154 | 1.2368 | 0.95081 | 0.8321 | 0.74505 | 0.72058 | 0.69722
43602.5839 | 1.1169 | 1.3109 | 1.2341 | 0.94741 | 0.82997 | 0.74394 | 0.72046 | 0.69744
43602.5839 | 1.1142 | 1.3092 | 1.2337 | 0.94766 | 0.83038 | 0.74405 | 0.72319 | 0.69741
43602.584 | 1.1137 | 1.3079 | 1.2318 | 0.94535 | 0.8271 | 0.74205 | 0.71958 | 0.6966
43602.5839 | 1.1063 | 1.2983 | 1.2242 | 0.93751 | 0.82302 | 0.73877 | 0.71555 | 0.69643
43602.5841 | 1.0866 | 1.2891 | 1.217 | 0.93112 | 0.81794 | 0.73437 | 0.71275 | 0.69471
43602.5841 | 1.0821 | 1.2863 | 1.2152 | 0.9289 | 0.81557 | 0.73359 | 0.71174 | 0.69472
43602.5841 | 1.0878 | 1.2884 | 1.2152 | 0.92978 | 0.8161 | 0.73298 | 0.71031 | 0.69447
43602.5841 | 1.0828 | 1.2824 | 1.211 | 0.92636 | 0.81337 | 0.73064 | 0.70834 | 0.69381
43602.5843 | 1.0795 | 1.2782 | 1.2066 | 0.92398 | 0.81005 | 0.72768 | 0.70619 | 0.6931
43602.5843 | 1.0755 | 1.2756 | 1.2061 | 0.92341 | 0.80952 | 0.72798 | 0.70637 | 0.69221
43602.5843 | 1.0815 | 1.2765 | 1.2041 | 0.92219 | 0.80898 | 0.72748 | 0.70608 | 0.6924
43602.5843 | 1.0862 | 1.2816 | 1.2076 | 0.92799 | 0.81214 | 0.72921 | 0.70736 | 0.69295
43602.5845 | 1.0878 | 1.2799 | 1.206 | 0.92728 | 0.81317 | 0.72948 | 0.70787 | 0.69227
43602.5845 | 1.0827 | 1.2804 | 1.2066 | 0.92752 | 0.81269 | 0.72975 | 0.70696 | 0.69213
43602.5845 | 1.0815 | 1.2803 | 1.2062 | 0.92759 | 0.81177 | 0.72919 | 0.70961 | 0.69212
43602.5845 | 1.0876 | 1.2783 | 1.2028 | 0.92712 | 0.81184 | 0.72876 | 0.70701 | 0.69151
43602.5847 | 1.0858 | 1.274 | 1.1991 | 0.92459 | 0.81046 | 0.72783 | 0.706 | 0.69099
43602.5847 | 1.0863 | 1.2729 | 1.1981 | 0.92421 | 0.80994 | 0.72762 | 0.70562 | 0.69131
43602.5847 | 1.0829 | 1.2711 | 1.1975 | 0.92369 | 0.80954 | 0.72696 | 0.70466 | 0.69116
43602.5847 | 1.0763 | 1.2747 | 1.2008 | 0.92521 | 0.81039 | 0.72817 | 0.70651 | 0.69128
43602.5849 | 1.0948 | 1.2834 | 1.2069 | 0.93047 | 0.81583 | 0.73207 | 0.70893 | 0.69235
43602.5849 | 1.0905 | 1.2831 | 1.2074 | 0.9305 | 0.81588 | 0.73199 | 0.71041 | 0.69219
43602.5849 | 1.0967 | 1.2859 | 1.2092 | 0.93238 | 0.81524 | 0.73189 | 0.71328 | 0.6921
43602.5848 | 1.0992 | 1.2853 | 1.2091 | 0.93083 | 0.81548 | 0.7326 | 0.71118 | 0.69281
43602.585 | 1.0879 | 1.283 | 1.2093 | 0.92937 | 0.81413 | 0.73123 | 0.71014 | 0.69288
43602.585 | 1.0879 | 1.2814 | 1.2081 | 0.92755 | 0.8136 | 0.73111 | 0.71 | 0.693
43602.5851 | 1.0806 | 1.2817 | 1.2095 | 0.9282 | 0.81317 | 0.73072 | 0.70914 | 0.69307
43602.585 | 1.0771 | 1.2732 | 1.2023 | 0.92075 | 0.80629 | 0.7262 | 0.70547 | 0.69218
43602.5852 | 1.0613 | 1.2602 | 1.1942 | 0.91141 | 0.7998 | 0.72113 | 0.70064 | 0.69047
43602.5852 | 1.0609 | 1.2615 | 1.1949 | 0.91289 | 0.80025 | 0.72133 | 0.70382 | 0.69068
43602.5852 | 1.0555 | 1.2571 | 1.1934 | 0.90923 | 0.80005 | 0.72114 | 0.70129 | 0.69053
43602.5852 | 1.0494 | 1.2548 | 1.191 | 0.90697 | 0.79693 | 0.71848 | 0.69833 | 0.68974
43602.5854 | 1.0491 | 1.2591 | 1.1948 | 0.90772 | 0.79731 | 0.71905 | 0.6979 | 0.68934
43602.5854 | 1.0565 | 1.2621 | 1.1961 | 0.90944 | 0.79761 | 0.71915 | 0.69851 | 0.68965
43602.5854 | 1.0545 | 1.2613 | 1.1951 | 0.9091 | 0.79771 | 0.71927 | 0.69812 | 0.68933
43602.5854 | 1.0558 | 1.262 | 1.1967 | 0.90796 | 0.79806 | 0.71967 | 0.70039 | 0.68935
43602.5856 | 1.0674 | 1.2712 | 1.2057 | 0.91603 | 0.80414 | 0.72349 | 0.70164 | 0.69046
43602.5856 | 1.0694 | 1.276 | 1.2068 | 0.91778 | 0.80465 | 0.72406 | 0.7024 | 0.69101
43602.5856 | 1.0708 | 1.2774 | 1.2073 | 0.91886 | 0.80576 | 0.72464 | 0.70213 | 0.69066
43602.5856 | 1.0739 | 1.2818 | 1.2122 | 0.922 | 0.80878 | 0.7271 | 0.70579 | 0.69167
43602.5858 | 1.0727 | 1.2775 | 1.209 | 0.91866 | 0.80842 | 0.72722 | 0.7074 | 0.69161
43602.5858 | 1.0713 | 1.2772 | 1.2077 | 0.91767 | 0.8063 | 0.72582 | 0.70412 | 0.69137
43602.5858 | 1.0639 | 1.2738 | 1.2071 | 0.91772 | 0.80613 | 0.72536 | 0.70391 | 0.69123
43602.5858 | 1.0589 | 1.2645 | 1.1977 | 0.91015 | 0.80078 | 0.72198 | 0.70134 | 0.69076
43602.586 | 1.0447 | 1.2511 | 1.1871 | 0.90278 | 0.79553 | 0.71737 | 0.69699 | 0.68949
43602.586 | 1.0485 | 1.2523 | 1.1868 | 0.90272 | 0.79328 | 0.71647 | 0.69578 | 0.68898
43602.586 | 1.0496 | 1.2531 | 1.1864 | 0.90365 | 0.79497 | 0.71684 | 0.69662 | 0.68928
43602.586 | 1.0491 | 1.2454 | 1.1807 | 0.89922 | 0.7906 | 0.71375 | 0.6931 | 0.68782
43602.5861 | 1.0504 | 1.2501 | 1.1814 | 0.90217 | 0.79218 | 0.71512 | 0.69803 | 0.68817
43602.5862 | 1.0501 | 1.2494 | 1.1817 | 0.90169 | 0.79269 | 0.71506 | 0.69525 | 0.68753
43602.5862 | 1.0494 | 1.2519 | 1.1832 | 0.90448 | 0.79293 | 0.71549 | 0.69494 | 0.68758
43602.5861 | 1.0586 | 1.257 | 1.1864 | 0.90892 | 0.79842 | 0.71866 | 0.69867 | 0.68827
43602.5863 | 1.063 | 1.255 | 1.1832 | 0.90979 | 0.79857 | 0.71898 | 0.69812 | 0.68817
43602.5863 | 1.0562 | 1.2506 | 1.1796 | 0.90704 | 0.79657 | 0.71805 | 0.69748 | 0.6878
43602.5864 | 1.064 | 1.2533 | 1.1805 | 0.90915 | 0.79646 | 0.71761 | 0.69704 | 0.68766
43602.5863 | 1.0612 | 1.2493 | 1.1778 | 0.90929 | 0.79642 | 0.71758 | 0.69741 | 0.68768
43602.5865 | 1.0579 | 1.2434 | 1.1704 | 0.90446 | 0.79482 | 0.71664 | 0.69533 | 0.68732
43602.5865 | 1.0558 | 1.2443 | 1.1708 | 0.90509 | 0.7929 | 0.71492 | 0.6944 | 0.68644
43602.5865 | 1.055 | 1.2399 | 1.1686 | 0.90387 | 0.7935 | 0.71544 | 0.69712 | 0.68677
43602.5865 | 1.0559 | 1.2417 | 1.1684 | 0.90531 | 0.79288 | 0.7146 | 0.69734 | 0.68646
43602.5867 | 1.0529 | 1.2341 | 1.1624 | 0.90095 | 0.79198 | 0.71371 | 0.69607 | 0.68579
43602.5867 | 1.0527 | 1.2374 | 1.164 | 0.90246 | 0.7916 | 0.71405 | 0.69382 | 0.68574
43602.5867 | 1.059 | 1.2358 | 1.1617 | 0.9016 | 0.79149 | 0.71303 | 0.69375 | 0.68536
43602.5867 | 1.0626 | 1.2414 | 1.1665 | 0.90509 | 0.79337 | 0.71474 | 0.69508 | 0.68569
43602.5869 | 1.0882 | 1.26 | 1.1817 | 0.91726 | 0.80263 | 0.72253 | 0.70126 | 0.68803
43602.5869 | 1.0817 | 1.257 | 1.18 | 0.91469 | 0.8019 | 0.72135 | 0.70028 | 0.68727
43602.5869 | 1.1005 | 1.2664 | 1.1868 | 0.92107 | 0.80523 | 0.72389 | 0.70176 | 0.68842
43602.5869 | 1.0916 | 1.2707 | 1.1927 | 0.92362 | 0.81074 | 0.72813 | 0.70593 | 0.68982
43602.5871 | 1.0837 | 1.2697 | 1.1939 | 0.92244 | 0.80867 | 0.72729 | 0.70764 | 0.6904
43602.5871 | 1.0827 | 1.269 | 1.1932 | 0.92162 | 0.8091 | 0.72767 | 0.70601 | 0.69073
43602.5871 | 1.082 | 1.2686 | 1.1935 | 0.92136 | 0.81053 | 0.72859 | 0.70667 | 0.69124
43602.5871 | 1.0698 | 1.2634 | 1.1914 | 0.91672 | 0.80547 | 0.72533 | 0.70402 | 0.69017
43602.5872 | 1.0736 | 1.2658 | 1.1922 | 0.91632 | 0.80488 | 0.72482 | 0.7041 | 0.69083
43602.5873 | 1.0629 | 1.2619 | 1.1921 | 0.91374 | 0.8048 | 0.72435 | 0.70475 | 0.6906
43602.5873 | 1.0736 | 1.2659 | 1.193 | 0.91633 | 0.8041 | 0.72419 | 0.70288 | 0.69075
43602.5872 | 1.0631 | 1.2621 | 1.1928 | 0.91273 | 0.80169 | 0.72302 | 0.70192 | 0.69061
43602.5874 | 1.0589 | 1.2593 | 1.1911 | 0.90905 | 0.79925 | 0.72157 | 0.70131 | 0.69074
43602.5874 | 1.0497 | 1.2557 | 1.1903 | 0.90697 | 0.7992 | 0.72127 | 0.70096 | 0.69059
43602.5875 | 1.0539 | 1.2538 | 1.1892 | 0.90628 | 0.79758 | 0.72067 | 0.69999 | 0.69032
43602.5874 | 1.0423 | 1.2472 | 1.1859 | 0.90114 | 0.79357 | 0.71761 | 0.69671 | 0.68974
43602.5876 | 1.0331 | 1.2393 | 1.18 | 0.89616 | 0.79013 | 0.71464 | 0.69435 | 0.68824
43602.5876 | 1.0359 | 1.239 | 1.1791 | 0.89552 | 0.78903 | 0.71401 | 0.69365 | 0.68807
43602.5876 | 1.0342 | 1.24 | 1.1791 | 0.89691 | 0.78892 | 0.71353 | 0.69939 | 0.68804
43602.5876 | 1.0325 | 1.2403 | 1.1788 | 0.89647 | 0.78797 | 0.71254 | 0.69143 | 0.68737
43602.5878 | 1.0309 | 1.2422 | 1.1804 | 0.8965 | 0.78861 | 0.71225 | 0.69205 | 0.68656
43602.5878 | 1.0389 | 1.2434 | 1.1792 | 0.89753 | 0.78806 | 0.71234 | 0.6925 | 0.68664
43602.5878 | 1.0423 | 1.2453 | 1.1809 | 0.8984 | 0.78885 | 0.71226 | 0.69184 | 0.68655
43602.5878 | 1.0472 | 1.2489 | 1.1831 | 0.9021 | 0.79131 | 0.71352 | 0.69301 | 0.68654
43602.588 | 1.0492 | 1.2494 | 1.1815 | 0.90326 | 0.79285 | 0.71456 | 0.69374 | 0.68631
43602.588 | 1.0536 | 1.252 | 1.1815 | 0.9054 | 0.79259 | 0.71448 | 0.69394 | 0.68606
43602.588 | 1.0546 | 1.2529 | 1.182 | 0.90506 | 0.79342 | 0.71494 | 0.69356 | 0.68596
43602.588 | 1.0642 | 1.2598 | 1.1869 | 0.91127 | 0.79753 | 0.7183 | 0.69686 | 0.68724
43602.5882 | 1.0795 | 1.2669 | 1.193 | 0.91752 | 0.80372 | 0.72242 | 0.70032 | 0.68823
43602.5882 | 1.0777 | 1.2675 | 1.1941 | 0.91809 | 0.80434 | 0.72313 | 0.70128 | 0.68849
43602.5882 | 1.0848 | 1.2727 | 1.1965 | 0.92109 | 0.80487 | 0.72366 | 0.70726 | 0.68887
43602.5882 | 1.0778 | 1.2684 | 1.1947 | 0.91871 | 0.80544 | 0.72426 | 0.70562 | 0.689
43602.5884 | 1.0686 | 1.2624 | 1.191 | 0.91411 | 0.80132 | 0.72132 | 0.69968 | 0.68828
43602.5884 | 1.0715 | 1.262 | 1.1908 | 0.91457 | 0.802 | 0.72155 | 0.70069 | 0.68899
43602.5884 | 1.0692 | 1.2604 | 1.1896 | 0.91363 | 0.8005 | 0.72088 | 0.69934 | 0.68801
43602.5883 | 1.0638 | 1.2581 | 1.1884 | 0.91173 | 0.79876 | 0.71882 | 0.69899 | 0.68736
43602.5886 | 1.0711 | 1.264 | 1.1919 | 0.91307 | 0.80056 | 0.72063 | 0.70033 | 0.68809
43602.5886 | 1.0691 | 1.2645 | 1.192 | 0.91252 | 0.80073 | 0.72088 | 0.69982 | 0.68829
43602.5886 | 1.0677 | 1.2634 | 1.1924 | 0.91311 | 0.80044 | 0.72065 | 0.69945 | 0.68818
43602.5885 | 1.0642 | 1.2655 | 1.194 | 0.91495 | 0.80154 | 0.72207 | 0.70086 | 0.68918
43602.5887 | 1.0633 | 1.2603 | 1.1905 | 0.91022 | 0.79967 | 0.72074 | 0.70267 | 0.68943
43602.5888 | 1.0547 | 1.257 | 1.1896 | 0.90979 | 0.79917 | 0.72078 | 0.70048 | 0.68883
43602.5888 | 1.0639 | 1.2614 | 1.1899 | 0.91109 | 0.79906 | 0.72038 | 0.69998 | 0.6892
43602.5887 | 1.0486 | 1.2521 | 1.1854 | 0.90564 | 0.79551 | 0.71818 | 0.69834 | 0.6884
43602.5889 | 1.0521 | 1.2525 | 1.1841 | 0.90543 | 0.79505 | 0.71779 | 0.69892 | 0.68833
43602.5889 | 1.0442 | 1.2515 | 1.1851 | 0.90557 | 0.79566 | 0.71761 | 0.69753 | 0.68888
43602.5889 | 1.0511 | 1.2525 | 1.1854 | 0.90619 | 0.79612 | 0.71812 | 0.69806 | 0.68895
43602.5889 | 1.0551 | 1.2554 | 1.188 | 0.90725 | 0.79873 | 0.72022 | 0.69949 | 0.68966
43602.5891 | 1.0574 | 1.2575 | 1.1896 | 0.90876 | 0.79947 | 0.72106 | 0.7007 | 0.68998
43602.5891 | 1.0607 | 1.2601 | 1.1903 | 0.91133 | 0.7991 | 0.72046 | 0.70009 | 0.68952
43602.5891 | 1.0546 | 1.2571 | 1.1895 | 0.90927 | 0.79849 | 0.72066 | 0.70018 | 0.68958
43602.5891 | 1.0564 | 1.2577 | 1.1886 | 0.90926 | 0.79919 | 0.72038 | 0.70066 | 0.68992
43602.5893 | 1.0495 | 1.2497 | 1.1823 | 0.9039 | 0.7951 | 0.71792 | 0.69811 | 0.68902
43602.5893 | 1.0505 | 1.2506 | 1.1829 | 0.9056 | 0.79423 | 0.7175 | 0.69696 | 0.68889
43602.5893 | 1.0518 | 1.2504 | 1.1827 | 0.90549 | 0.79546 | 0.71803 | 0.69774 | 0.6891
43602.5893 | 1.0495 | 1.2459 | 1.1789 | 0.9033 | 0.79401 | 0.71669 | 0.69661 | 0.68884
43602.5895 | 1.0457 | 1.2445 | 1.1763 | 0.90149 | 0.792 | 0.71521 | 0.69597 | 0.6883
43602.5895 | 1.0443 | 1.2453 | 1.1774 | 0.90202 | 0.79239 | 0.71517 | 0.69496 | 0.68817
43602.5895 | 1.0498 | 1.2454 | 1.1788 | 0.90297 | 0.79341 | 0.71551 | 0.69821 | 0.68816
43602.5895 | 1.0564 | 1.2549 | 1.1835 | 0.90939 | 0.79708 | 0.71843 | 0.70276 | 0.6895
43602.5897 | 1.0655 | 1.2598 | 1.1871 | 0.91209 | 0.80009 | 0.72132 | 0.69986 | 0.68985
43602.5897 | 1.0659 | 1.2592 | 1.1874 | 0.91147 | 0.80068 | 0.72135 | 0.70027 | 0.69002
43602.5897 | 1.0596 | 1.2564 | 1.186 | 0.91088 | 0.79905 | 0.72061 | 0.70218 | 0.68987
43602.5897 | 1.0644 | 1.2597 | 1.1876 | 0.91168 | 0.80063 | 0.72165 | 0.70109 | 0.69076
43602.5899 | 1.0528 | 1.251 | 1.1818 | 0.90548 | 0.79672 | 0.71929 | 0.69899 | 0.68952
43602.5899 | 1.0537 | 1.2538 | 1.1828 | 0.90795 | 0.7969 | 0.71899 | 0.69878 | 0.68959
43602.5899 | 1.0526 | 1.2524 | 1.1821 | 0.90706 | 0.79645 | 0.71885 | 0.69832 | 0.68916
43602.5899 | 1.0507 | 1.2489 | 1.1804 | 0.9044 | 0.79477 | 0.71784 | 0.69706 | 0.68866
43602.5901 | 1.0494 | 1.2448 | 1.174 | 0.90211 | 0.79286 | 0.71615 | 0.69494 | 0.68828
43602.5901 | 1.0418 | 1.2426 | 1.1748 | 0.90096 | 0.79278 | 0.71605 | 0.69684 | 0.68793
43602.5901 | 1.046 | 1.2421 | 1.1736 | 0.9004 | 0.79154 | 0.71568 | 0.69539 | 0.68824
43602.59 | 1.0448 | 1.2426 | 1.1744 | 0.90101 | 0.79266 | 0.71603 | 0.69569 | 0.68794
43602.5902 | 1.0539 | 1.2513 | 1.1797 | 0.90616 | 0.79543 | 0.71715 | 0.69683 | 0.68799
43602.5903 | 1.0568 | 1.2524 | 1.1801 | 0.90732 | 0.79814 | 0.71917 | 0.69781 | 0.68885
43602.5903 | 1.0569 | 1.2519 | 1.1797 | 0.9063 | 0.79556 | 0.71767 | 0.69754 | 0.68842
43602.5902 | 1.0522 | 1.2533 | 1.1835 | 0.90873 | 0.80049 | 0.72108 | 0.70348 | 0.69017
43602.5904 | 1.0637 | 1.2582 | 1.1865 | 0.91222 | 0.80025 | 0.72152 | 0.70062 | 0.68995
43602.5904 | 1.0685 | 1.2585 | 1.1851 | 0.91294 | 0.80222 | 0.72271 | 0.70163 | 0.69073
43602.5904 | 1.0556 | 1.2576 | 1.1861 | 0.91231 | 0.80129 | 0.72246 | 0.70127 | 0.69
43602.5904 | 1.0527 | 1.2505 | 1.1802 | 0.90685 | 0.79877 | 0.72057 | 0.69921 | 0.68994
43602.5906 | 1.0579 | 1.2558 | 1.184 | 0.91015 | 0.79825 | 0.7204 | 0.70062 | 0.69049
43602.5906 | 1.0594 | 1.2558 | 1.1841 | 0.90954 | 0.80059 | 0.72201 | 0.70425 | 0.69064
43602.5906 | 1.0594 | 1.2568 | 1.1844 | 0.91046 | 0.79978 | 0.72166 | 0.70095 | 0.6907
43602.5906 | 1.0612 | 1.2618 | 1.1917 | 0.91464 | 0.80401 | 0.72485 | 0.70489 | 0.69159
43602.5908 | 1.0694 | 1.2644 | 1.1923 | 0.91506 | 0.80463 | 0.72478 | 0.70379 | 0.69189
43602.5908 | 1.0701 | 1.2646 | 1.192 | 0.91574 | 0.80458 | 0.72474 | 0.70319 | 0.69179
43602.5908 | 1.0652 | 1.2642 | 1.1924 | 0.91496 | 0.80455 | 0.72524 | 0.70365 | 0.69188
43602.5908 | 1.0655 | 1.2659 | 1.1944 | 0.91646 | 0.80535 | 0.72547 | 0.70396 | 0.69268
43602.591 | 1.0635 | 1.2612 | 1.1907 | 0.91208 | 0.8033 | 0.72449 | 0.70338 | 0.69238
43602.591 | 1.0633 | 1.2622 | 1.1909 | 0.91259 | 0.80297 | 0.72447 | 0.70291 | 0.69263
43602.591 | 1.0576 | 1.2612 | 1.1907 | 0.91171 | 0.80261 | 0.7242 | 0.70664 | 0.69208
43602.591 | 1.0527 | 1.2555 | 1.1866 | 0.90944 | 0.8008 | 0.72276 | 0.70469 | 0.69218
43602.5912 | 1.0429 | 1.2451 | 1.1779 | 0.90249 | 0.79605 | 0.71924 | 0.69859 | 0.69117
43602.5912 | 1.0459 | 1.2449 | 1.1779 | 0.9023 | 0.79531 | 0.71933 | 0.69908 | 0.69092
43602.5912 | 1.045 | 1.2455 | 1.1782 | 0.90267 | 0.79529 | 0.71887 | 0.69826 | 0.69088
43602.5912 | 1.0465 | 1.2413 | 1.1738 | 0.90103 | 0.79278 | 0.71727 | 0.70077 | 0.69024
43602.5914 | 1.0488 | 1.2436 | 1.1746 | 0.90336 | 0.79429 | 0.7185 | 0.70002 | 0.69052
43602.5914 | 1.0449 | 1.2475 | 1.1772 | 0.90521 | 0.79604 | 0.71937 | 0.70177 | 0.69075
43602.5914 | 1.051 | 1.2466 | 1.1762 | 0.90482 | 0.79612 | 0.71945 | 0.69909 | 0.69065
43602.5914 | 1.0533 | 1.2513 | 1.1807 | 0.90923 | 0.79909 | 0.72143 | 0.70114 | 0.69135
43602.5916 | 1.0572 | 1.255 | 1.1832 | 0.91114 | 0.80033 | 0.72262 | 0.70246 | 0.69147
43602.5916 | 1.0597 | 1.2557 | 1.1832 | 0.91146 | 0.80148 | 0.72357 | 0.70298 | 0.69223
43602.5916 | 1.0669 | 1.2582 | 1.184 | 0.91486 | 0.80245 | 0.72359 | 0.70238 | 0.69176
43602.5915 | 1.0611 | 1.2535 | 1.1802 | 0.91179 | 0.80109 | 0.72261 | 0.70295 | 0.69181
43602.5917 | 1.055 | 1.2485 | 1.1782 | 0.90876 | 0.80095 | 0.72306 | 0.70258 | 0.69245
43602.5917 | 1.0596 | 1.2507 | 1.1793 | 0.90986 | 0.80002 | 0.72218 | 0.7022 | 0.69197
43602.5918 | 1.0564 | 1.2512 | 1.1795 | 0.91 | 0.80078 | 0.72273 | 0.70228 | 0.69197
43602.5917 | 1.0628 | 1.2545 | 1.1806 | 0.91148 | 0.801 | 0.72273 | 0.7022 | 0.69165
43602.5919 | 1.0676 | 1.2598 | 1.1866 | 0.91645 | 0.80561 | 0.72622 | 0.70866 | 0.6937
43602.5919 | 1.067 | 1.2599 | 1.1871 | 0.9166 | 0.8056 | 0.72638 | 0.70583 | 0.69308
43602.592 | 1.0694 | 1.2638 | 1.189 | 0.9188 | 0.8083 | 0.72789 | 0.70626 | 0.69387
43602.5919 | 1.0589 | 1.2569 | 1.1871 | 0.91485 | 0.80541 | 0.72645 | 0.70548 | 0.69325
43602.5921 | 1.0654 | 1.2628 | 1.19 | 0.91715 | 0.80716 | 0.72742 | 0.7065 | 0.69416
43602.5921 | 1.0707 | 1.2648 | 1.1912 | 0.91819 | 0.80729 | 0.7279 | 0.70805 | 0.6942
43602.5921 | 1.0695 | 1.2638 | 1.1921 | 0.91847 | 0.80832 | 0.72842 | 0.70747 | 0.69469
43602.5921 | 1.0814 | 1.2779 | 1.2034 | 0.92481 | 0.81293 | 0.73172 | 0.71041 | 0.69516
43602.5923 | 1.0937 | 1.294 | 1.2189 | 0.93573 | 0.82262 | 0.73925 | 0.71657 | 0.69801
43602.5923 | 1.096 | 1.2968 | 1.2208 | 0.93632 | 0.82281 | 0.73939 | 0.71615 | 0.6977
43602.5923 | 1.1008 | 1.2964 | 1.2216 | 0.9377 | 0.82452 | 0.74056 | 0.71684 | 0.69812
43602.5923 | 1.0916 | 1.2953 | 1.2223 | 0.93351 | 0.82095 | 0.73902 | 0.71612 | 0.6976
43602.5925 | 1.0784 | 1.2837 | 1.2166 | 0.92484 | 0.81656 | 0.7365 | 0.718 | 0.69818
43602.5925 | 1.0767 | 1.2831 | 1.2168 | 0.92477 | 0.81527 | 0.73574 | 0.71382 | 0.69788
43602.5925 | 1.0773 | 1.2868 | 1.2177 | 0.92693 | 0.81636 | 0.73598 | 0.71379 | 0.69799
43602.5925 | 1.0703 | 1.2802 | 1.2139 | 0.92199 | 0.81238 | 0.73296 | 0.71484 | 0.69729
43602.5927 | 1.0656 | 1.2748 | 1.2116 | 0.91659 | 0.80999 | 0.73119 | 0.70849 | 0.69677
43602.5927 | 1.0647 | 1.2755 | 1.2117 | 0.91666 | 0.80958 | 0.73107 | 0.70917 | 0.69694
43602.5927 | 1.0613 | 1.2745 | 1.2118 | 0.91754 | 0.80984 | 0.73108 | 0.70855 | 0.69695
43602.5927 | 1.0661 | 1.2764 | 1.2116 | 0.91693 | 0.80885 | 0.72957 | 0.70996 | 0.69588
43602.5929 | 1.0661 | 1.2769 | 1.2123 | 0.91719 | 0.80752 | 0.72856 | 0.70904 | 0.69551
43602.5929 | 1.0637 | 1.2764 | 1.2133 | 0.91719 | 0.80884 | 0.72913 | 0.70807 | 0.69577
43602.5929 | 1.0634 | 1.2774 | 1.2136 | 0.91809 | 0.80946 | 0.72974 | 0.70783 | 0.69547
43602.5929 | 1.0768 | 1.2892 | 1.2219 | 0.92475 | 0.81364 | 0.73314 | 0.71027 | 0.69628
43602.5931 | 1.0923 | 1.3013 | 1.2299 | 0.93432 | 0.82224 | 0.73859 | 0.71478 | 0.69764
43602.5931 | 1.0983 | 1.3015 | 1.2298 | 0.93403 | 0.82076 | 0.73769 | 0.71362 | 0.697
43602.5931 | 1.0995 | 1.303 | 1.2312 | 0.93554 | 0.82283 | 0.73881 | 0.71439 | 0.69786
43602.5931 | 1.0995 | 1.306 | 1.2314 | 0.93847 | 0.82419 | 0.74051 | 0.71934 | 0.69823
43602.5933 | 1.0978 | 1.2998 | 1.2267 | 0.93542 | 0.82407 | 0.74034 | 0.71711 | 0.69838
43602.5933 | 1.0949 | 1.2977 | 1.2253 | 0.93545 | 0.82297 | 0.73916 | 0.7162 | 0.69795
43602.5933 | 1.0934 | 1.2972 | 1.2244 | 0.93416 | 0.82185 | 0.73903 | 0.71635 | 0.69787
43602.5932 | 1.0904 | 1.2892 | 1.2167 | 0.93027 | 0.81855 | 0.7364 | 0.71361 | 0.69729
43602.5934 | 1.081 | 1.281 | 1.2091 | 0.92554 | 0.81421 | 0.73294 | 0.71261 | 0.69548
43602.5935 | 1.0821 | 1.283 | 1.2095 | 0.92606 | 0.81529 | 0.73392 | 0.71325 | 0.69592
43602.5935 | 1.0809 | 1.2809 | 1.2083 | 0.92483 | 0.81443 | 0.73339 | 0.71105 | 0.69591
43602.5934 | 1.0849 | 1.2821 | 1.2078 | 0.92708 | 0.81525 | 0.73354 | 0.71161 | 0.69554
43602.5936 | 1.0889 | 1.2799 | 1.2061 | 0.92726 | 0.81605 | 0.7339 | 0.71609 | 0.69573
43602.5936 | 1.0905 | 1.2829 | 1.2071 | 0.92922 | 0.81591 | 0.73352 | 0.71213 | 0.69502
43602.5937 | 1.0885 | 1.2818 | 1.2061 | 0.92768 | 0.81651 | 0.73388 | 0.7124 | 0.69544
43602.5936 | 1.0831 | 1.2785 | 1.2033 | 0.92648 | 0.81621 | 0.73423 | 0.71513 | 0.69547
43602.5938 | 1.0893 | 1.2766 | 1.1998 | 0.92719 | 0.81363 | 0.73156 | 0.7107 | 0.69448
43602.5938 | 1.0848 | 1.2715 | 1.197 | 0.92437 | 0.81379 | 0.73189 | 0.71071 | 0.69456
43602.5938 | 1.077 | 1.2727 | 1.198 | 0.92485 | 0.81266 | 0.73119 | 0.71002 | 0.69427
43602.5938 | 1.0856 | 1.2741 | 1.1967 | 0.92547 | 0.81318 | 0.73189 | 0.71115 | 0.69435
43602.594 | 1.0868 | 1.2801 | 1.2015 | 0.93 | 0.81554 | 0.73343 | 0.71153 | 0.69491
43602.594 | 1.0849 | 1.2719 | 1.1959 | 0.9244 | 0.81572 | 0.73341 | 0.71167 | 0.69454
43602.594 | 1.0899 | 1.2759 | 1.1984 | 0.92732 | 0.81437 | 0.73274 | 0.71082 | 0.69438
43602.594 | 1.0899 | 1.2766 | 1.1995 | 0.92846 | 0.81737 | 0.73469 | 0.71704 | 0.69471
43602.5942 | 1.1054 | 1.2815 | 1.2032 | 0.93323 | 0.81725 | 0.73511 | 0.71468 | 0.69464
43602.5942 | 1.0961 | 1.2753 | 1.1986 | 0.9278 | 0.81705 | 0.73483 | 0.71584 | 0.69458
43602.5942 | 1.0919 | 1.278 | 1.2 | 0.92983 | 0.8178 | 0.73506 | 0.71455 | 0.69533
43602.5942 | 1.0847 | 1.2717 | 1.1954 | 0.92609 | 0.81514 | 0.73335 | 0.71305 | 0.69475
43602.5944 | 1.0904 | 1.2691 | 1.1912 | 0.92443 | 0.81314 | 0.73153 | 0.71012 | 0.69517
43602.5944 | 1.0875 | 1.2709 | 1.1931 | 0.92688 | 0.81373 | 0.73206 | 0.71103 | 0.69487
43602.5944 | 1.0847 | 1.2663 | 1.1888 | 0.92297 | 0.81399 | 0.73254 | 0.71009 | 0.69504
43602.5944 | 1.0785 | 1.2615 | 1.1845 | 0.91987 | 0.80928 | 0.72888 | 0.70879 | 0.69418
43602.5946 | 1.0858 | 1.2638 | 1.1863 | 0.92251 | 0.81251 | 0.73061 | 0.7102 | 0.69437
43602.5946 | 1.0918 | 1.2664 | 1.1884 | 0.92527 | 0.81204 | 0.73026 | 0.70868 | 0.69388
43602.5946 | 1.091 | 1.2648 | 1.1862 | 0.92294 | 0.81249 | 0.73066 | 0.71313 | 0.69446
43602.5946 | 1.0904 | 1.2673 | 1.1885 | 0.92585 | 0.81455 | 0.73243 | 0.71155 | 0.695
43602.5948 | 1.0749 | 1.257 | 1.1795 | 0.9191 | 0.80795 | 0.72773 | 0.71038 | 0.69421
43602.5948 | 1.0771 | 1.255 | 1.1777 | 0.9181 | 0.80773 | 0.72758 | 0.70853 | 0.69432
43602.5948 | 1.0736 | 1.2521 | 1.1748 | 0.91553 | 0.80715 | 0.72725 | 0.70735 | 0.69408
43602.5948 | 1.0615 | 1.2422 | 1.1667 | 0.90996 | 0.80153 | 0.72324 | 0.70633 | 0.6934
43602.595 | 1.0517 | 1.2351 | 1.1592 | 0.90603 | 0.79576 | 0.71927 | 0.7005 | 0.69219
43602.595 | 1.053 | 1.2328 | 1.1579 | 0.9048 | 0.79734 | 0.71996 | 0.70137 | 0.69319
43602.595 | 1.0521 | 1.2345 | 1.1585 | 0.9061 | 0.79684 | 0.71986 | 0.70103 | 0.69271
43602.595 | 1.0566 | 1.2261 | 1.1511 | 0.90257 | 0.79343 | 0.71671 | 0.69813 | 0.69178
43602.5952 | 1.049 | 1.2258 | 1.1494 | 0.9019 | 0.79254 | 0.71593 | 0.69732 | 0.69087
43602.5952 | 1.0553 | 1.232 | 1.1539 | 0.90681 | 0.79693 | 0.71933 | 0.69935 | 0.69237
43602.5952 | 1.051 | 1.226 | 1.1496 | 0.90213 | 0.79342 | 0.71693 | 0.70011 | 0.69102
43602.5951 | 1.0717 | 1.2395 | 1.1593 | 0.91079 | 0.79979 | 0.7215 | 0.7026 | 0.69197
43602.5953 | 1.0745 | 1.2371 | 1.1577 | 0.90994 | 0.79997 | 0.72133 | 0.70292 | 0.69228
43602.5954 | 1.0727 | 1.2329 | 1.1557 | 0.90864 | 0.80131 | 0.72253 | 0.7035 | 0.69276
43602.5954 | 1.0598 | 1.2334 | 1.1556 | 0.90822 | 0.79971 | 0.72146 | 0.7028 | 0.69261
43602.5953 | 1.0551 | 1.2238 | 1.1468 | 0.90173 | 0.79672 | 0.71922 | 0.70337 | 0.69286
43602.5955 | 1.0449 | 1.2124 | 1.1367 | 0.89638 | 0.78754 | 0.71248 | 0.69537 | 0.69083
43602.5956 | 1.0265 | 1.2052 | 1.1313 | 0.89002 | 0.78704 | 0.7117 | 0.69472 | 0.69067
43602.5956 | 1.0346 | 1.2042 | 1.1306 | 0.88998 | 0.78476 | 0.71022 | 0.6932 | 0.69056
43602.5955 | 1.0207 | 1.1983 | 1.1245 | 0.88607 | 0.78153 | 0.70766 | 0.69113 | 0.68964
43602.5957 | 1.0227 | 1.1961 | 1.1216 | 0.88487 | 0.78036 | 0.7067 | 0.68953 | 0.68888
43602.5957 | 1.0274 | 1.1959 | 1.1215 | 0.88553 | 0.7805 | 0.70684 | 0.68929 | 0.68924
43602.5958 | 1.0209 | 1.1932 | 1.1198 | 0.88331 | 0.77751 | 0.70459 | 0.69097 | 0.68825
43602.5957 | 1.0237 | 1.1886 | 1.115 | 0.88181 | 0.77782 | 0.70489 | 0.68768 | 0.68837
43602.5959 | 1.0114 | 1.1789 | 1.1061 | 0.87583 | 0.7735 | 0.70183 | 0.68568 | 0.68773
43602.5959 | 1.0195 | 1.1822 | 1.1093 | 0.87975 | 0.77402 | 0.70181 | 0.68422 | 0.68782
43602.5959 | 1.022 | 1.1806 | 1.1063 | 0.87684 | 0.77222 | 0.70093 | 0.68642 | 0.68685
43602.5959 | 1.0166 | 1.1752 | 1.0997 | 0.87382 | 0.77091 | 0.69963 | 0.68294 | 0.68656
43602.5961 | 1.0113 | 1.1667 | 1.0922 | 0.86809 | 0.76595 | 0.69567 | 0.68075 | 0.68506
43602.5961 | 1.0096 | 1.1654 | 1.0915 | 0.86778 | 0.76695 | 0.69635 | 0.68049 | 0.68545
43602.5961 | 0.99879 | 1.1655 | 1.0922 | 0.86813 | 0.76364 | 0.6939 | 0.67903 | 0.68441
43602.5961 | 1.0027 | 1.1624 | 1.0888 | 0.86691 | 0.76238 | 0.69277 | 0.67792 | 0.68379
43602.5963 | 1.0233 | 1.1676 | 1.0915 | 0.8702 | 0.76506 | 0.69481 | 0.67886 | 0.68412
43602.5963 | 1.0193 | 1.1691 | 1.0931 | 0.8713 | 0.7666 | 0.69586 | 0.6799 | 0.68463
43602.5963 | 1.0144 | 1.165 | 1.0905 | 0.86923 | 0.76699 | 0.69636 | 0.68051 | 0.6846
43602.5963 | 1.02 | 1.1705 | 1.0933 | 0.87202 | 0.76823 | 0.69757 | 0.68348 | 0.68551
43602.5965 | 1.0244 | 1.1685 | 1.0903 | 0.87052 | 0.76631 | 0.69588 | 0.67997 | 0.68525
43602.5965 | 0.9963 | 1.1593 | 1.0857 | 0.8662 | 0.76597 | 0.69561 | 0.68321 | 0.68492
43602.5965 | 1.0028 | 1.1599 | 1.0851 | 0.86607 | 0.76308 | 0.69429 | 0.67928 | 0.6848
43602.5965 | 1.0066 | 1.1535 | 1.0786 | 0.8621 | 0.75887 | 0.69051 | 0.67532 | 0.68394
43602.5967 | 0.98617 | 1.1477 | 1.0745 | 0.85852 | 0.75821 | 0.69001 | 0.67641 | 0.68395
43602.5967 | 0.98308 | 1.1455 | 1.0731 | 0.85723 | 0.75756 | 0.69005 | 0.67541 | 0.68399
43602.5967 | 0.99855 | 1.1522 | 1.0775 | 0.8611 | 0.75762 | 0.6895 | 0.67476 | 0.6838
43602.5967 | 0.98854 | 1.1567 | 1.0839 | 0.86457 | 0.76323 | 0.69434 | 0.67934 | 0.68519
43602.5969 | 1.0052 | 1.1634 | 1.0888 | 0.86784 | 0.76536 | 0.69581 | 0.68135 | 0.68656
43602.5969 | 0.99215 | 1.1581 | 1.0874 | 0.86606 | 0.76176 | 0.69339 | 0.67874 | 0.68519
43602.5969 | 0.98796 | 1.1566 | 1.0857 | 0.86476 | 0.76203 | 0.69383 | 0.6784 | 0.68564
43602.5969 | 0.96988 | 1.1468 | 1.0787 | 0.8566 | 0.75659 | 0.68983 | 0.67688 | 0.68527
43602.5971 | 0.95354 | 1.1387 | 1.0721 | 0.85046 | 0.75214 | 0.68683 | 0.6726 | 0.68528
43602.5971 | 0.95858 | 1.1372 | 1.0704 | 0.84947 | 0.75053 | 0.68571 | 0.67665 | 0.68509
43602.5971 | 0.95953 | 1.1389 | 1.0723 | 0.85234 | 0.75184 | 0.68576 | 0.6731 | 0.68566
43602.5971 | 0.94463 | 1.1295 | 1.0655 | 0.84533 | 0.74626 | 0.68244 | 0.66961 | 0.68453
43602.5973 | 0.94085 | 1.1242 | 1.0605 | 0.84236 | 0.74345 | 0.67953 | 0.66689 | 0.68336
43602.5973 | 0.93371 | 1.1213 | 1.0617 | 0.84155 | 0.74373 | 0.67949 | 0.66668 | 0.68294
43602.5973 | 0.93693 | 1.1227 | 1.0605 | 0.84049 | 0.74263 | 0.67915 | 0.66658 | 0.68279
43602.5972 | 0.93532 | 1.1191 | 1.0578 | 0.83891 | 0.74123 | 0.67748 | 0.66439 | 0.68222
43602.5974 | 0.94291 | 1.126 | 1.0607 | 0.84265 | 0.74279 | 0.67793 | 0.665 | 0.68189
43602.5975 | 0.93781 | 1.1195 | 1.0576 | 0.83701 | 0.73992 | 0.67598 | 0.6633 | 0.68045
43602.5975 | 0.93926 | 1.1232 | 1.0601 | 0.84088 | 0.73999 | 0.67574 | 0.66354 | 0.68049
43602.5974 | 0.95032 | 1.1302 | 1.0628 | 0.84524 | 0.7419 | 0.67696 | 0.66614 | 0.68065
43602.5976 | 0.94652 | 1.1307 | 1.0638 | 0.8463 | 0.74374 | 0.67879 | 0.66582 | 0.6809
43602.5977 | 0.94898 | 1.1267 | 1.0599 | 0.84149 | 0.74293 | 0.67779 | 0.66465 | 0.68022
43602.5977 | 0.94522 | 1.1269 | 1.0613 | 0.84266 | 0.74146 | 0.67696 | 0.66575 | 0.67991
43602.5976 | 0.95325 | 1.1291 | 1.0617 | 0.84392 | 0.74331 | 0.67824 | 0.66424 | 0.68024
43602.5978 | 0.95239 | 1.1283 | 1.0608 | 0.84382 | 0.74201 | 0.67728 | 0.66445 | 0.68034
43602.5978 | 0.94356 | 1.1252 | 1.0601 | 0.84205 | 0.74227 | 0.67724 | 0.66432 | 0.68023
43602.5979 | 0.93788 | 1.1204 | 1.0572 | 0.83841 | 0.74038 | 0.67667 | 0.66219 | 0.68024
43602.5978 | 0.93151 | 1.1146 | 1.0521 | 0.83615 | 0.73788 | 0.67472 | 0.66194 | 0.68042
43602.598 | 0.91812 | 1.1039 | 1.0454 | 0.83056 | 0.73513 | 0.67286 | 0.66011 | 0.68034
43602.598 | 0.92529 | 1.1047 | 1.0439 | 0.83083 | 0.73293 | 0.67173 | 0.65856 | 0.67981
43602.598 | 0.92869 | 1.1061 | 1.0433 | 0.83104 | 0.733 | 0.67154 | 0.66033 | 0.67983
43602.598 | 0.91867 | 1.1027 | 1.0421 | 0.8311 | 0.73114 | 0.67048 | 0.65768 | 0.67988
43602.5982 | 0.93423 | 1.1068 | 1.0431 | 0.83173 | 0.73157 | 0.67017 | 0.65815 | 0.67883
43602.5982 | 0.9297 | 1.1083 | 1.0459 | 0.83218 | 0.73596 | 0.67284 | 0.65984 | 0.68038
43602.5982 | 0.92308 | 1.1039 | 1.0422 | 0.83008 | 0.7329 | 0.67121 | 0.65962 | 0.67926
43602.5982 | 0.92539 | 1.1045 | 1.0412 | 0.83013 | 0.73246 | 0.67055 | 0.65749 | 0.67867
43602.5984 | 0.93599 | 1.108 | 1.0426 | 0.8335 | 0.73271 | 0.67117 | 0.65877 | 0.6788
43602.5984 | 0.93294 | 1.1078 | 1.0422 | 0.83264 | 0.73506 | 0.67232 | 0.66067 | 0.67939
43602.5984 | 0.92706 | 1.1047 | 1.0409 | 0.83111 | 0.73357 | 0.67135 | 0.65842 | 0.67886
43602.5984 | 0.9253 | 1.0992 | 1.0355 | 0.82881 | 0.7317 | 0.66994 | 0.65768 | 0.67936
43602.5986 | 0.91913 | 1.0934 | 1.0296 | 0.82668 | 0.72758 | 0.66757 | 0.65702 | 0.67902
43602.5986 | 0.91769 | 1.0926 | 1.029 | 0.82497 | 0.7308 | 0.66936 | 0.65823 | 0.67998
43602.5986 | 0.9166 | 1.0887 | 1.026 | 0.82187 | 0.726 | 0.66638 | 0.65493 | 0.67826
43602.5986 | 0.91255 | 1.0869 | 1.0234 | 0.82246 | 0.7263 | 0.666 | 0.65403 | 0.67874
43602.5988 | 0.91618 | 1.083 | 1.0185 | 0.82019 | 0.72284 | 0.66333 | 0.65245 | 0.67754
43602.5988 | 0.91175 | 1.0829 | 1.0193 | 0.82001 | 0.72561 | 0.665 | 0.65439 | 0.67827
43602.5988 | 0.92319 | 1.0883 | 1.0217 | 0.82411 | 0.72454 | 0.6643 | 0.65272 | 0.67766
43602.5988 | 0.92498 | 1.0906 | 1.0234 | 0.82571 | 0.72704 | 0.66655 | 0.65516 | 0.67844
43602.599 | 0.93887 | 1.0968 | 1.0275 | 0.82886 | 0.72841 | 0.66782 | 0.65646 | 0.67865
43602.599 | 0.93823 | 1.1008 | 1.0314 | 0.83198 | 0.73467 | 0.67202 | 0.66041 | 0.68073
43602.599 | 0.9425 | 1.0971 | 1.0286 | 0.82989 | 0.73348 | 0.67118 | 0.65938 | 0.68024
43602.599 | 0.92868 | 1.0946 | 1.0268 | 0.82814 | 0.73273 | 0.67084 | 0.65952 | 0.68066
43602.5992 | 0.91986 | 1.0837 | 1.0183 | 0.82312 | 0.72635 | 0.66707 | 0.65617 | 0.68065
43602.5992 | 0.90995 | 1.0797 | 1.0168 | 0.81998 | 0.72684 | 0.66732 | 0.6568 | 0.68098
43602.5992 | 0.90755 | 1.0783 | 1.0154 | 0.81941 | 0.72467 | 0.66593 | 0.6556 | 0.68052
43602.5992 | 0.90017 | 1.0705 | 1.0083 | 0.81542 | 0.72058 | 0.66377 | 0.65341 | 0.68054
43602.5994 | 0.88431 | 1.0611 | 1.0039 | 0.81076 | 0.71809 | 0.66177 | 0.65262 | 0.67997
43602.5994 | 0.89142 | 1.0627 | 1.0041 | 0.81121 | 0.71782 | 0.66138 | 0.65191 | 0.67998
43602.5994 | 0.89645 | 1.0676 | 1.0062 | 0.81499 | 0.71903 | 0.66202 | 0.65192 | 0.68034
43602.5994 | 0.89102 | 1.0652 | 1.0054 | 0.81334 | 0.71852 | 0.6615 | 0.65175 | 0.67996
43602.5996 | 0.90246 | 1.0741 | 1.0121 | 0.81849 | 0.72378 | 0.66441 | 0.65363 | 0.68013
43602.5996 | 0.91005 | 1.0748 | 1.0109 | 0.81811 | 0.72325 | 0.66401 | 0.65394 | 0.67983
43602.5996 | 0.90545 | 1.0732 | 1.0111 | 0.81716 | 0.72371 | 0.66436 | 0.65668 | 0.68023
43602.5995 | 0.92187 | 1.085 | 1.0176 | 0.82539 | 0.72809 | 0.66798 | 0.65778 | 0.68195
43602.5998 | 0.91298 | 1.0819 | 1.017 | 0.8226 | 0.7291 | 0.66889 | 0.65797 | 0.68224
43602.5998 | 0.9092 | 1.0813 | 1.0174 | 0.8229 | 0.72756 | 0.66846 | 0.65708 | 0.68178
43602.5998 | 0.91282 | 1.0816 | 1.0176 | 0.82302 | 0.72825 | 0.66854 | 0.66274 | 0.68216
43602.5997 | 0.90583 | 1.0798 | 1.0175 | 0.82196 | 0.72911 | 0.66943 | 0.6582 | 0.6833
43602.5999 | 0.89287 | 1.0704 | 1.0134 | 0.81788 | 0.72591 | 0.66786 | 0.65711 | 0.68334
43602.6 | 0.89571 | 1.0709 | 1.013 | 0.81797 | 0.72451 | 0.66699 | 0.65656 | 0.68317
43602.6 | 0.90396 | 1.0747 | 1.0133 | 0.82019 | 0.72545 | 0.66765 | 0.65672 | 0.68369
43602.5999 | 0.88365 | 1.0631 | 1.0089 | 0.81308 | 0.72179 | 0.66561 | 0.65468 | 0.68304
43602.6001 | 0.89166 | 1.072 | 1.0132 | 0.81946 | 0.7249 | 0.66778 | 0.65703 | 0.68431
43602.6001 | 0.88171 | 1.064 | 1.0116 | 0.81445 | 0.72351 | 0.66683 | 0.65927 | 0.68343
43602.6002 | 0.87911 | 1.0632 | 1.011 | 0.81359 | 0.72091 | 0.66538 | 0.6552 | 0.68291
43602.6001 | 0.88328 | 1.0644 | 1.0114 | 0.81466 | 0.72187 | 0.66541 | 0.65452 | 0.68313
43602.6003 | 0.88014 | 1.0649 | 1.0114 | 0.81547 | 0.72171 | 0.6648 | 0.65771 | 0.68246
43602.6003 | 0.88113 | 1.0638 | 1.0099 | 0.81388 | 0.7217 | 0.66497 | 0.65456 | 0.68244
43602.6004 | 0.88422 | 1.0629 | 1.0095 | 0.81297 | 0.72013 | 0.66398 | 0.6535 | 0.68163
43602.6003 | 0.89028 | 1.0691 | 1.0125 | 0.81605 | 0.72234 | 0.66469 | 0.65539 | 0.68155
43602.6005 | 0.89416 | 1.07 | 1.0125 | 0.81674 | 0.7219 | 0.66456 | 0.65396 | 0.68117
43602.6005 | 0.89176 | 1.0711 | 1.0135 | 0.81751 | 0.72238 | 0.66497 | 0.65334 | 0.68113
43602.6005 | 0.89427 | 1.0721 | 1.0137 | 0.81764 | 0.72226 | 0.66481 | 0.65445 | 0.68097
43602.6005 | 0.89752 | 1.0747 | 1.0145 | 0.81989 | 0.72392 | 0.66568 | 0.6544 | 0.68122
43602.6007 | 0.90891 | 1.0782 | 1.0152 | 0.82092 | 0.72607 | 0.66707 | 0.65622 | 0.68117
43602.6007 | 0.90393 | 1.0792 | 1.0169 | 0.82175 | 0.72529 | 0.6666 | 0.65565 | 0.68089
43602.6007 | 0.91394 | 1.0827 | 1.0183 | 0.824 | 0.72705 | 0.66766 | 0.65692 | 0.68164
43602.6007 | 0.9223 | 1.0843 | 1.0192 | 0.82491 | 0.72906 | 0.66921 | 0.66123 | 0.68176
43602.6009 | 0.91263 | 1.0813 | 1.0175 | 0.82258 | 0.72675 | 0.66772 | 0.65696 | 0.68058
43602.6009 | 0.91209 | 1.0841 | 1.0192 | 0.82525 | 0.7283 | 0.6686 | 0.65745 | 0.68126
43602.6009 | 0.9166 | 1.0838 | 1.019 | 0.82495 | 0.72869 | 0.66883 | 0.65744 | 0.6812
43602.6009 | 0.92638 | 1.0937 | 1.0258 | 0.83025 | 0.732 | 0.67159 | 0.66418 | 0.68205
43602.6011 | 0.91632 | 1.086 | 1.0208 | 0.82568 | 0.72807 | 0.66874 | 0.66168 | 0.68101
43602.6011 | 0.92233 | 1.0893 | 1.0229 | 0.82787 | 0.73006 | 0.67002 | 0.65951 | 0.68152
43602.6011 | 0.93659 | 1.0959 | 1.0273 | 0.83264 | 0.73348 | 0.67213 | 0.66112 | 0.68241
43602.6011 | 0.93765 | 1.0949 | 1.0258 | 0.83077 | 0.73362 | 0.6723 | 0.66164 | 0.68245
43602.6013 | 0.92833 | 1.0909 | 1.0241 | 0.82919 | 0.73225 | 0.67156 | 0.66064 | 0.68205
43602.6013 | 0.9149 | 1.0854 | 1.0221 | 0.82553 | 0.73049 | 0.67025 | 0.65866 | 0.68156
43602.6013 | 0.92165 | 1.0897 | 1.0244 | 0.82893 | 0.73042 | 0.67031 | 0.66148 | 0.68147
43602.6013 | 0.92062 | 1.0895 | 1.0259 | 0.82846 | 0.73139 | 0.67093 | 0.66062 | 0.68199
43602.6015 | 0.92989 | 1.0952 | 1.0296 | 0.83145 | 0.73522 | 0.67366 | 0.66536 | 0.68242
43602.6015 | 0.92324 | 1.0935 | 1.0291 | 0.83064 | 0.73465 | 0.67295 | 0.66324 | 0.68198
43602.6015 | 0.91636 | 1.0899 | 1.0282 | 0.82929 | 0.73218 | 0.67199 | 0.66181 | 0.68204
43602.6015 | 0.92387 | 1.0919 | 1.0268 | 0.82985 | 0.73174 | 0.6716 | 0.66073 | 0.68223
43602.6017 | 0.93031 | 1.0967 | 1.0304 | 0.832 | 0.7316 | 0.6713 | 0.66132 | 0.68237
43602.6017 | 0.93156 | 1.0976 | 1.0312 | 0.83266 | 0.73657 | 0.67438 | 0.66237 | 0.68364
43602.6017 | 0.91004 | 1.0877 | 1.028 | 0.82599 | 0.73176 | 0.6716 | 0.6601 | 0.682
43602.6017 | 0.92552 | 1.0972 | 1.0326 | 0.83254 | 0.73502 | 0.6736 | 0.66197 | 0.68307
43602.6019 | 0.92181 | 1.0982 | 1.0342 | 0.83449 | 0.73467 | 0.67377 | 0.66217 | 0.68337
43602.6019 | 0.91989 | 1.0943 | 1.0326 | 0.83127 | 0.73605 | 0.67468 | 0.66287 | 0.68359
43602.6019 | 0.92099 | 1.0949 | 1.032 | 0.83115 | 0.73334 | 0.67294 | 0.66303 | 0.68278
43602.6019 | 0.92694 | 1.0976 | 1.0319 | 0.83285 | 0.73344 | 0.67263 | 0.665 | 0.68306
43602.6021 | 0.92034 | 1.0945 | 1.0292 | 0.82962 | 0.73167 | 0.67124 | 0.66017 | 0.6829
43602.6021 | 0.9163 | 1.095 | 1.0306 | 0.8303 | 0.73435 | 0.67282 | 0.6647 | 0.68353
43602.6021 | 0.9042 | 1.0877 | 1.029 | 0.82603 | 0.73199 | 0.67192 | 0.66137 | 0.68296
43602.6021 | 0.91046 | 1.087 | 1.0257 | 0.82663 | 0.72996 | 0.67038 | 0.66107 | 0.68292
43602.6023 | 0.9021 | 1.0838 | 1.0242 | 0.82391 | 0.72962 | 0.67002 | 0.6591 | 0.68273
43602.6023 | 0.90698 | 1.083 | 1.0228 | 0.82221 | 0.72762 | 0.66889 | 0.66112 | 0.68178
43602.6023 | 0.91513 | 1.0892 | 1.0253 | 0.82656 | 0.72796 | 0.66888 | 0.65813 | 0.68168
43602.6023 | 0.91662 | 1.0908 | 1.0266 | 0.82803 | 0.72938 | 0.66997 | 0.65851 | 0.68199
43602.6025 | 0.91664 | 1.0913 | 1.0283 | 0.82803 | 0.73036 | 0.67062 | 0.65912 | 0.68203
43602.6025 | 0.92014 | 1.0946 | 1.0288 | 0.83054 | 0.73299 | 0.67213 | 0.66237 | 0.68275
43602.6025 | 0.9084 | 1.0866 | 1.0263 | 0.82493 | 0.73067 | 0.6709 | 0.66067 | 0.68185
43602.6024 | 0.91813 | 1.0885 | 1.0237 | 0.82623 | 0.73044 | 0.67057 | 0.65892 | 0.68207
43602.6027 | 0.90493 | 1.0805 | 1.0206 | 0.82419 | 0.72675 | 0.66837 | 0.65711 | 0.68152
43602.6027 | 0.90789 | 1.0818 | 1.0204 | 0.82435 | 0.72808 | 0.66896 | 0.65737 | 0.68172
43602.6027 | 0.9066 | 1.0795 | 1.0184 | 0.82236 | 0.72793 | 0.66888 | 0.65859 | 0.68166
43602.6026 | 0.89369 | 1.0711 | 1.0124 | 0.81855 | 0.72308 | 0.66551 | 0.65372 | 0.68042
43602.6028 | 0.90023 | 1.0728 | 1.0102 | 0.81897 | 0.72451 | 0.66559 | 0.65384 | 0.6803
43602.6029 | 0.90984 | 1.0738 | 1.0096 | 0.81907 | 0.72358 | 0.66533 | 0.65463 | 0.68014
43602.6029 | 0.89773 | 1.0699 | 1.0085 | 0.81668 | 0.72388 | 0.66519 | 0.65701 | 0.68019
43602.6028 | 0.9031 | 1.071 | 1.0087 | 0.81824 | 0.72638 | 0.66665 | 0.65572 | 0.68065
43602.603 | 0.91439 | 1.0697 | 1.0048 | 0.81664 | 0.72225 | 0.66396 | 0.6567 | 0.6787
43602.603 | 0.91608 | 1.0707 | 1.005 | 0.81713 | 0.72152 | 0.66299 | 0.65332 | 0.67849
43602.6031 | 0.91484 | 1.0726 | 1.0074 | 0.81924 | 0.72331 | 0.66453 | 0.65417 | 0.67899
43602.603 | 0.91416 | 1.0732 | 1.0071 | 0.81932 | 0.72267 | 0.6645 | 0.65389 | 0.67874
43602.6032 | 0.92011 | 1.0713 | 1.0047 | 0.81754 | 0.72356 | 0.66425 | 0.65512 | 0.67814
43602.6032 | 0.90769 | 1.0693 | 1.0046 | 0.81784 | 0.72225 | 0.66375 | 0.65333 | 0.67817
43602.6033 | 0.93285 | 1.0772 | 1.0083 | 0.82097 | 0.72517 | 0.66619 | 0.65501 | 0.67897
43602.6032 | 0.94639 | 1.0796 | 1.0086 | 0.82203 | 0.72377 | 0.6648 | 0.65351 | 0.67878
43602.6034 | 0.91516 | 1.0663 | 0.99933 | 0.81521 | 0.72168 | 0.66333 | 0.65503 | 0.67811
43602.6034 | 0.91927 | 1.067 | 0.99998 | 0.81575 | 0.72009 | 0.66199 | 0.6519 | 0.67788
43602.6035 | 0.91366 | 1.0678 | 1.0012 | 0.81666 | 0.72358 | 0.6646 | 0.65396 | 0.67858
43602.6034 | 0.93183 | 1.0661 | 0.99705 | 0.81448 | 0.72083 | 0.66224 | 0.65178 | 0.67772
43602.6036 | 0.91463 | 1.0616 | 0.99491 | 0.81273 | 0.72181 | 0.66289 | 0.65401 | 0.67767
43602.6036 | 0.91767 | 1.0648 | 0.99685 | 0.81422 | 0.71816 | 0.6603 | 0.65065 | 0.67666
43602.6036 | 0.93305 | 1.0681 | 0.99787 | 0.81513 | 0.7204 | 0.66203 | 0.65198 | 0.67723
43602.6036 | 0.93539 | 1.0738 | 1.0042 | 0.819 | 0.72516 | 0.66579 | 0.65458 | 0.67771
43602.6038 | 0.95838 | 1.0887 | 1.0148 | 0.82658 | 0.73056 | 0.66972 | 0.65786 | 0.67877
43602.6038 | 0.94547 | 1.0829 | 1.0121 | 0.82405 | 0.72897 | 0.66898 | 0.65912 | 0.67859
43602.6038 | 0.95763 | 1.0871 | 1.0142 | 0.82633 | 0.73171 | 0.67093 | 0.65967 | 0.67971
43602.604 | 0.92425 | 1.0729 | 1.0056 | 0.81996 | 0.72581 | 0.6669 | 0.65633 | 0.67979
43602.604 | 0.93031 | 1.0737 | 1.0059 | 0.82044 | 0.72754 | 0.66834 | 0.65784 | 0.68077
43602.604 | 0.91601 | 1.068 | 1.0024 | 0.81724 | 0.72475 | 0.66631 | 0.65586 | 0.68015
43602.604 | 0.89944 | 1.0612 | 0.99825 | 0.81389 | 0.72286 | 0.665 | 0.65512 | 0.68045
43602.6042 | 0.90216 | 1.0611 | 0.99759 | 0.81553 | 0.72155 | 0.66403 | 0.65422 | 0.68065
43602.6042 | 0.89376 | 1.0561 | 0.99309 | 0.81139 | 0.72002 | 0.66302 | 0.65326 | 0.68023
43602.6042 | 0.90814 | 1.061 | 0.99612 | 0.81484 | 0.71982 | 0.66278 | 0.65772 | 0.68048
43602.6042 | 0.90867 | 1.0607 | 0.99624 | 0.81563 | 0.72328 | 0.66478 | 0.65562 | 0.68153
43602.6044 | 0.88064 | 1.0452 | 0.98638 | 0.807 | 0.71556 | 0.65931 | 0.65447 | 0.67948
43602.6044 | 0.88541 | 1.0464 | 0.98624 | 0.80701 | 0.71469 | 0.65877 | 0.65145 | 0.67936
43602.6044 | 0.88763 | 1.0489 | 0.98763 | 0.80865 | 0.7151 | 0.65918 | 0.65066 | 0.67938
43602.6044 | 0.86972 | 1.0408 | 0.98347 | 0.80342 | 0.71226 | 0.65695 | 0.64784 | 0.6779
43602.6046 | 0.90258 | 1.0503 | 0.98577 | 0.80806 | 0.71543 | 0.659 | 0.64947 | 0.67884
43602.6046 | 0.88511 | 1.0441 | 0.98236 | 0.80453 | 0.71316 | 0.65731 | 0.65163 | 0.67797
43602.6046 | 0.90043 | 1.051 | 0.98704 | 0.80895 | 0.71478 | 0.65871 | 0.65103 | 0.67877
43602.6045 | 0.89598 | 1.0516 | 0.98616 | 0.80849 | 0.71634 | 0.65987 | 0.65077 | 0.67912
43602.6048 | 0.89466 | 1.046 | 0.98231 | 0.80586 | 0.71541 | 0.65949 | 0.65056 | 0.679
43602.6048 | 0.87955 | 1.042 | 0.98261 | 0.80476 | 0.7134 | 0.65809 | 0.6516 | 0.67899
43602.6048 | 0.90375 | 1.0491 | 0.98389 | 0.80762 | 0.71544 | 0.65964 | 0.65053 | 0.67968
43602.6047 | 0.89212 | 1.0471 | 0.98348 | 0.80769 | 0.71577 | 0.66005 | 0.65098 | 0.68005
43602.605 | 0.88588 | 1.0425 | 0.98061 | 0.80575 | 0.71466 | 0.65918 | 0.65004 | 0.67999
43602.605 | 0.90417 | 1.0464 | 0.98281 | 0.80754 | 0.71493 | 0.65914 | 0.65039 | 0.68022
43602.6049 | 0.88146 | 1.0388 | 0.97845 | 0.80345 | 0.71431 | 0.65874 | 0.64949 | 0.68009
43602.6051 | 0.88657 | 1.037 | 0.9748 | 0.80213 | 0.71248 | 0.65728 | 0.64926 | 0.68021
43602.6051 | 0.88416 | 1.0353 | 0.97451 | 0.80196 | 0.71212 | 0.65717 | 0.64926 | 0.68016
43602.6051 | 0.86146 | 1.0251 | 0.96917 | 0.79644 | 0.70907 | 0.65541 | 0.64698 | 0.68013
43602.6053 | 0.86923 | 1.026 | 0.96752 | 0.79687 | 0.70482 | 0.65258 | 0.64562 | 0.67924
43602.6053 | 0.88493 | 1.0304 | 0.96959 | 0.79955 | 0.70981 | 0.65531 | 0.64758 | 0.68086
43602.6053 | 0.86347 | 1.0217 | 0.96513 | 0.79526 | 0.70747 | 0.65347 | 0.64551 | 0.67934
43602.6053 | 0.87337 | 1.0245 | 0.96524 | 0.79609 | 0.7054 | 0.65241 | 0.64545 | 0.67953
43602.6055 | 0.87073 | 1.0251 | 0.96613 | 0.79629 | 0.70791 | 0.65382 | 0.6466 | 0.67961
43602.6055 | 0.87933 | 1.0259 | 0.96621 | 0.79715 | 0.70728 | 0.65351 | 0.64572 | 0.67941
43602.6055 | 0.87169 | 1.0232 | 0.96577 | 0.79644 | 0.70696 | 0.65308 | 0.64544 | 0.67919
43602.6054 | 0.87322 | 1.0243 | 0.96508 | 0.79586 | 0.70698 | 0.65355 | 0.64589 | 0.67947
43602.6057 | 0.87298 | 1.0232 | 0.96376 | 0.79546 | 0.70589 | 0.65281 | 0.6459 | 0.67956
43602.6057 | 0.8829 | 1.0256 | 0.96556 | 0.7969 | 0.70693 | 0.6536 | 0.64622 | 0.67993
43602.6057 | 0.87075 | 1.0235 | 0.9642 | 0.79619 | 0.70805 | 0.65402 | 0.64714 | 0.68021
43602.6056 | 0.86891 | 1.0219 | 0.96299 | 0.79485 | 0.70666 | 0.65338 | 0.64646 | 0.68025
43602.6058 | 0.87042 | 1.0197 | 0.96111 | 0.79424 | 0.70632 | 0.65324 | 0.64498 | 0.68056
43602.6059 | 0.85404 | 1.0132 | 0.95845 | 0.79155 | 0.70449 | 0.65218 | 0.64691 | 0.68015
43602.6059 | 0.8611 | 1.0148 | 0.95777 | 0.79162 | 0.70362 | 0.65162 | 0.64779 | 0.68052
43602.6058 | 0.85377 | 1.0113 | 0.95569 | 0.78969 | 0.70481 | 0.65226 | 0.64479 | 0.68046
43602.606 | 0.8452 | 1.005 | 0.95207 | 0.78772 | 0.70168 | 0.65012 | 0.64306 | 0.68034
43602.6061 | 0.85434 | 1.0084 | 0.95281 | 0.789 | 0.70213 | 0.6505 | 0.64287 | 0.68069
43602.6061 | 0.86186 | 1.009 | 0.95223 | 0.78862 | 0.7022 | 0.65048 | 0.64293 | 0.68057
43602.606 | 0.85539 | 1.0062 | 0.95056 | 0.78779 | 0.70303 | 0.65029 | 0.6448 | 0.68068
43602.6062 | 0.84931 | 1.0005 | 0.94597 | 0.78431 | 0.6982 | 0.64748 | 0.64586 | 0.6789
43602.6063 | 0.86084 | 1.0043 | 0.94777 | 0.7859 | 0.6986 | 0.64757 | 0.64321 | 0.6792
43602.6063 | 0.85776 | 1.0035 | 0.94828 | 0.78682 | 0.70031 | 0.64833 | 0.64303 | 0.67966
43602.6062 | 0.89285 | 1.0156 | 0.9543 | 0.79044 | 0.70413 | 0.65101 | 0.64565 | 0.68058
43602.6064 | 0.86667 | 1.0112 | 0.95243 | 0.78873 | 0.70339 | 0.65051 | 0.64415 | 0.67907
43602.6065 | 0.88463 | 1.0152 | 0.9545 | 0.79078 | 0.7026 | 0.64994 | 0.64394 | 0.67901
43602.6065 | 0.87146 | 1.0136 | 0.95386 | 0.79021 | 0.70322 | 0.65059 | 0.647 | 0.67926
43602.6064 | 0.88487 | 1.0234 | 0.96242 | 0.79634 | 0.70841 | 0.65443 | 0.64843 | 0.68066
43602.6066 | 0.86764 | 1.021 | 0.96171 | 0.79534 | 0.70927 | 0.65577 | 0.65495 | 0.68266
43602.6066 | 0.86423 | 1.0185 | 0.96024 | 0.79425 | 0.70747 | 0.65496 | 0.64907 | 0.68247
43602.6067 | 0.86754 | 1.018 | 0.96011 | 0.79374 | 0.70679 | 0.65468 | 0.64868 | 0.68247
43602.6066 | 0.86129 | 1.0129 | 0.95649 | 0.7926 | 0.70616 | 0.65416 | 0.64814 | 0.68395
43602.6068 | 0.82734 | 0.99506 | 0.94834 | 0.78555 | 0.7011 | 0.65102 | 0.64584 | 0.68423
43602.6068 | 0.83282 | 0.99789 | 0.94954 | 0.78752 | 0.70136 | 0.65133 | 0.64592 | 0.68439
43602.6069 | 0.83782 | 0.99863 | 0.94924 | 0.78718 | 0.70238 | 0.65154 | 0.64578 | 0.68463
43602.6068 | 0.83199 | 0.99284 | 0.94485 | 0.78431 | 0.69886 | 0.64931 | 0.64331 | 0.68382
43602.607 | 0.81874 | 0.98621 | 0.94236 | 0.78199 | 0.69649 | 0.64744 | 0.64156 | 0.6831
43602.607 | 0.81777 | 0.98623 | 0.94229 | 0.78192 | 0.69669 | 0.6472 | 0.64031 | 0.68307
43602.607 | 0.81832 | 0.98573 | 0.94214 | 0.78037 | 0.6961 | 0.6467 | 0.64203 | 0.68204
43602.6072 | 0.84774 | 1.0051 | 0.95382 | 0.78837 | 0.70039 | 0.64906 | 0.64204 | 0.68159
43602.6072 | 0.844 | 1.0074 | 0.95679 | 0.78953 | 0.70205 | 0.64949 | 0.64462 | 0.68151
43602.6072 | 0.84882 | 1.0118 | 0.95949 | 0.79145 | 0.7022 | 0.64986 | 0.644 | 0.68132
43602.6072 | 0.88437 | 1.0391 | 0.97812 | 0.80388 | 0.71333 | 0.65774 | 0.64946 | 0.68204
43602.6074 | 0.87816 | 1.04 | 0.98108 | 0.80481 | 0.71687 | 0.66113 | 0.65424 | 0.68316
43602.6074 | 0.888 | 1.0452 | 0.98428 | 0.8089 | 0.7157 | 0.66077 | 0.65176 | 0.68306
43602.6074 | 0.87612 | 1.0424 | 0.98356 | 0.80717 | 0.71801 | 0.66224 | 0.65309 | 0.68372
43602.6074 | 0.86453 | 1.0355 | 0.97904 | 0.80331 | 0.71449 | 0.66064 | 0.65186 | 0.68461
43602.6076 | 0.84955 | 1.02 | 0.96863 | 0.79788 | 0.7104 | 0.65848 | 0.65126 | 0.68592
43602.6076 | 0.84941 | 1.0203 | 0.96882 | 0.79799 | 0.71028 | 0.65827 | 0.65383 | 0.68613
43602.6076 | 0.84881 | 1.0183 | 0.968 | 0.79693 | 0.71098 | 0.65887 | 0.65122 | 0.68646
43602.6076 | 0.84532 | 1.0119 | 0.96215 | 0.79498 | 0.70834 | 0.65719 | 0.6509 | 0.68661
43602.6078 | 0.82299 | 0.99816 | 0.95569 | 0.78947 | 0.70453 | 0.65503 | 0.64828 | 0.68679
43602.6078 | 0.82192 | 0.99778 | 0.95578 | 0.78989 | 0.70463 | 0.65547 | 0.65243 | 0.68705
43602.6078 | 0.8283 | 1.0001 | 0.9561 | 0.79117 | 0.70452 | 0.65543 | 0.64956 | 0.6871
43602.6078 | 0.82335 | 0.99643 | 0.95415 | 0.79002 | 0.70415 | 0.65456 | 0.64763 | 0.68726
43602.608 | 0.8168 | 0.99274 | 0.95312 | 0.78856 | 0.70364 | 0.65479 | 0.648 | 0.68745
43602.608 | 0.82945 | 0.99611 | 0.95145 | 0.78779 | 0.70343 | 0.65439 | 0.64711 | 0.68713
43602.608 | 0.82177 | 0.99372 | 0.95245 | 0.7879 | 0.70206 | 0.65343 | 0.65189 | 0.68648
43602.608 | 0.824 | 0.99825 | 0.95592 | 0.78975 | 0.70283 | 0.65344 | 0.64726 | 0.68585
43602.6082 | 0.83475 | 1.0109 | 0.96696 | 0.79572 | 0.70686 | 0.65556 | 0.64899 | 0.68566
43602.6082 | 0.83954 | 1.0131 | 0.96752 | 0.79588 | 0.70725 | 0.65581 | 0.64853 | 0.68538
43602.6082 | 0.85296 | 1.0166 | 0.96774 | 0.79619 | 0.70714 | 0.65547 | 0.6475 | 0.68504
43602.6082 | 0.85389 | 1.0245 | 0.97635 | 0.80004 | 0.71032 | 0.65751 | 0.65361 | 0.68434
43602.6084 | 0.86094 | 1.0359 | 0.98505 | 0.80491 | 0.7146 | 0.66038 | 0.65113 | 0.68435
43602.6084 | 0.86026 | 1.037 | 0.9866 | 0.80539 | 0.71525 | 0.66087 | 0.65103 | 0.68461
43602.6084 | 0.86555 | 1.0377 | 0.98628 | 0.80539 | 0.71513 | 0.66086 | 0.65432 | 0.68437
43602.6084 | 0.86417 | 1.0406 | 0.98894 | 0.80712 | 0.71659 | 0.66194 | 0.65291 | 0.6845
43602.6086 | 0.88172 | 1.0529 | 0.9944 | 0.81306 | 0.72118 | 0.66485 | 0.65561 | 0.68546
43602.6086 | 0.86997 | 1.0472 | 0.99375 | 0.80967 | 0.72018 | 0.66436 | 0.65724 | 0.6852
43602.6086 | 0.87932 | 1.0529 | 0.99563 | 0.81308 | 0.71971 | 0.66435 | 0.65638 | 0.6853
43602.6086 | 0.87721 | 1.0495 | 0.99147 | 0.81123 | 0.72061 | 0.66537 | 0.6562 | 0.6867
43602.6088 | 0.87153 | 1.0446 | 0.98952 | 0.80949 | 0.71922 | 0.66482 | 0.65592 | 0.68707
43602.6088 | 0.87181 | 1.0453 | 0.99005 | 0.81022 | 0.71939 | 0.66494 | 0.65613 | 0.68679
43602.6088 | 0.86331 | 1.0431 | 0.9907 | 0.8098 | 0.72017 | 0.66523 | 0.65562 | 0.68708
43602.6088 | 0.86399 | 1.0413 | 0.98932 | 0.807 | 0.71917 | 0.66505 | 0.65548 | 0.68716
43602.609 | 0.86597 | 1.0404 | 0.98727 | 0.80746 | 0.71801 | 0.6642 | 0.65757 | 0.68749
43602.609 | 0.86645 | 1.0404 | 0.98801 | 0.80835 | 0.71855 | 0.66488 | 0.65915 | 0.68756
43602.609 | 0.87219 | 1.0432 | 0.98825 | 0.80866 | 0.71928 | 0.66539 | 0.6567 | 0.68795
43602.609 | 0.86138 | 1.0358 | 0.98461 | 0.80565 | 0.71724 | 0.66393 | 0.65551 | 0.68742
43602.6092 | 0.85574 | 1.0372 | 0.98665 | 0.80699 | 0.7166 | 0.66304 | 0.65431 | 0.68693
43602.6092 | 0.86952 | 1.0416 | 0.98658 | 0.80739 | 0.71751 | 0.66316 | 0.65833 | 0.68696
43602.6092 | 0.86566 | 1.0402 | 0.98652 | 0.8077 | 0.71757 | 0.66331 | 0.65545 | 0.68664
43602.6092 | 0.86516 | 1.0421 | 0.98826 | 0.80841 | 0.71772 | 0.6631 | 0.65492 | 0.6863
43602.6094 | 0.87846 | 1.0466 | 0.98939 | 0.80876 | 0.71798 | 0.66345 | 0.65518 | 0.68582
43602.6094 | 0.8767 | 1.0491 | 0.99109 | 0.81111 | 0.71897 | 0.66376 | 0.6552 | 0.68584
43602.6094 | 0.89264 | 1.0538 | 0.99176 | 0.81151 | 0.7201 | 0.66436 | 0.65559 | 0.68596
43602.6095 | 0.88831 | 1.053 | 0.99021 | 0.81128 | 0.71986 | 0.66455 | 0.65639 | 0.68528
43602.6095 | 0.90361 | 1.0565 | 0.99169 | 0.81288 | 0.72124 | 0.66534 | 0.65566 | 0.68579
43602.6095 | 0.89219 | 1.0539 | 0.99077 | 0.81186 | 0.72243 | 0.66568 | 0.65628 | 0.68573
43602.6095 | 0.89361 | 1.0538 | 0.99006 | 0.81226 | 0.72134 | 0.66537 | 0.66079 | 0.68598
43602.6097 | 0.89435 | 1.0523 | 0.98776 | 0.81157 | 0.72227 | 0.66661 | 0.65722 | 0.68649
43602.6097 | 0.88588 | 1.0491 | 0.98662 | 0.8103 | 0.72029 | 0.66548 | 0.65676 | 0.68605
43602.6097 | 0.89762 | 1.0525 | 0.98791 | 0.81196 | 0.72229 | 0.66662 | 0.65812 | 0.68725
43602.6097 | 0.90317 | 1.0545 | 0.98823 | 0.81315 | 0.72283 | 0.66714 | 0.6581 | 0.6877
43602.6099 | 0.88278 | 1.045 | 0.983 | 0.80963 | 0.72153 | 0.66656 | 0.65737 | 0.68854
43602.6099 | 0.88843 | 1.0428 | 0.98064 | 0.80803 | 0.72075 | 0.66605 | 0.65676 | 0.6881
43602.61 | 0.88613 | 1.0417 | 0.97973 | 0.80731 | 0.71902 | 0.66514 | 0.66042 | 0.68781
43602.6099 | 0.87909 | 1.0386 | 0.97763 | 0.80659 | 0.7174 | 0.664 | 0.65528 | 0.68786
43602.6101 | 0.86639 | 1.0284 | 0.97003 | 0.80003 | 0.71514 | 0.6622 | 0.65525 | 0.68761
43602.6101 | 0.8753 | 1.0341 | 0.97413 | 0.80414 | 0.71479 | 0.66182 | 0.65474 | 0.68761
43602.6101 | 0.87539 | 1.0345 | 0.97474 | 0.80524 | 0.71807 | 0.66403 | 0.65699 | 0.68863
43602.6103 | 0.87716 | 1.0348 | 0.97386 | 0.804 | 0.71853 | 0.66377 | 0.65825 | 0.68803
43602.6103 | 0.87469 | 1.0333 | 0.9732 | 0.80292 | 0.71574 | 0.6625 | 0.65446 | 0.68716
43602.6103 | 0.89207 | 1.0413 | 0.97783 | 0.80695 | 0.71862 | 0.66444 | 0.65618 | 0.68837
43602.6103 | 0.87442 | 1.0365 | 0.97552 | 0.80427 | 0.71713 | 0.66359 | 0.65453 | 0.68725
43602.6105 | 0.91478 | 1.0518 | 0.98532 | 0.81311 | 0.72239 | 0.66692 | 0.6584 | 0.68913
43602.6105 | 0.89859 | 1.0459 | 0.98146 | 0.80964 | 0.72309 | 0.66697 | 0.65782 | 0.68832
43602.6105 | 0.88165 | 1.0394 | 0.97847 | 0.80676 | 0.71968 | 0.66508 | 0.65861 | 0.68788
43602.6107 | 0.88751 | 1.0409 | 0.97858 | 0.80734 | 0.71984 | 0.66514 | 0.65753 | 0.68856
43602.6107 | 0.88893 | 1.0432 | 0.97947 | 0.80818 | 0.71988 | 0.66529 | 0.65695 | 0.68873
43602.6107 | 0.88487 | 1.0423 | 0.97996 | 0.80803 | 0.72106 | 0.66603 | 0.6576 | 0.6891
43602.6108 | 0.8713 | 1.0359 | 0.97613 | 0.80574 | 0.71805 | 0.66404 | 0.65532 | 0.68888
43602.6108 | 0.88508 | 1.0391 | 0.97708 | 0.80708 | 0.71908 | 0.66471 | 0.65589 | 0.68921
43602.6109 | 0.86806 | 1.0332 | 0.97477 | 0.80406 | 0.71784 | 0.66375 | 0.65616 | 0.68849
43602.6108 | 0.87623 | 1.0308 | 0.97132 | 0.80283 | 0.71607 | 0.66245 | 0.65537 | 0.68824
43602.611 | 0.86458 | 1.0296 | 0.97195 | 0.80324 | 0.71575 | 0.66212 | 0.65581 | 0.688
43602.611 | 0.88701 | 1.0337 | 0.97252 | 0.80465 | 0.71584 | 0.66209 | 0.65432 | 0.6883
43602.6111 | 0.86978 | 1.0318 | 0.97299 | 0.80427 | 0.71713 | 0.66298 | 0.65594 | 0.68881
43602.611 | 0.88867 | 1.039 | 0.97644 | 0.80703 | 0.72033 | 0.66477 | 0.65914 | 0.68975
43602.6112 | 0.87892 | 1.0323 | 0.97279 | 0.80391 | 0.71607 | 0.66244 | 0.6547 | 0.68766
43602.6112 | 0.88206 | 1.0334 | 0.97302 | 0.80395 | 0.71578 | 0.66204 | 0.65344 | 0.68754
43602.6113 | 0.88415 | 1.0341 | 0.97358 | 0.80513 | 0.71742 | 0.663 | 0.65557 | 0.68805
43602.6112 | 0.87367 | 1.033 | 0.97269 | 0.80412 | 0.71779 | 0.66311 | 0.65726 | 0.68784
43602.6114 | 0.87528 | 1.0328 | 0.97318 | 0.80349 | 0.71672 | 0.66249 | 0.65461 | 0.68729
43602.6114 | 0.89287 | 1.0372 | 0.97544 | 0.80521 | 0.71628 | 0.66259 | 0.657 | 0.68778
43602.6114 | 0.8872 | 1.0382 | 0.97598 | 0.8057 | 0.71828 | 0.66377 | 0.6579 | 0.68792
43602.6116 | 0.9133 | 1.0472 | 0.98177 | 0.81043 | 0.72064 | 0.66537 | 0.65994 | 0.68866
43602.6116 | 0.87457 | 1.0336 | 0.97392 | 0.80243 | 0.71903 | 0.6642 | 0.6566 | 0.68795
43602.6116 | 0.90607 | 1.0428 | 0.97737 | 0.80672 | 0.71621 | 0.66292 | 0.6549 | 0.6876
43602.6117 | 0.9096 | 1.0409 | 0.97778 | 0.80748 | 0.71814 | 0.66424 | 0.65564 | 0.68898
43602.6118 | 0.8764 | 1.0335 | 0.97346 | 0.80393 | 0.71784 | 0.66368 | 0.65522 | 0.68829
43602.6117 | 0.87885 | 1.0351 | 0.97386 | 0.80402 | 0.7161 | 0.66291 | 0.65485 | 0.6881
43602.6119 | 0.88372 | 1.0342 | 0.97388 | 0.80438 | 0.71607 | 0.66243 | 0.65406 | 0.68813
43602.6119 | 0.88342 | 1.0364 | 0.97412 | 0.80464 | 0.71721 | 0.66334 | 0.65445 | 0.68863
43602.6119 | 0.88423 | 1.0374 | 0.97611 | 0.8051 | 0.71767 | 0.66397 | 0.65808 | 0.68853
43602.6121 | 0.89211 | 1.044 | 0.98281 | 0.81043 | 0.72003 | 0.66583 | 0.65913 | 0.6892
43602.6121 | 0.89155 | 1.0449 | 0.98303 | 0.81038 | 0.72263 | 0.66736 | 0.65828 | 0.68972
43602.6121 | 0.90029 | 1.0451 | 0.98335 | 0.81025 | 0.72069 | 0.6661 | 0.65717 | 0.68881
43602.6121 | 0.88541 | 1.0458 | 0.98459 | 0.81109 | 0.72307 | 0.66784 | 0.65897 | 0.68975
43602.6123 | 0.887 | 1.0456 | 0.98432 | 0.81129 | 0.7212 | 0.66685 | 0.65881 | 0.68972
43602.6123 | 0.87561 | 1.0429 | 0.9837 | 0.80974 | 0.72235 | 0.66753 | 0.65891 | 0.69
43602.6123 | 0.88287 | 1.0446 | 0.98343 | 0.81025 | 0.72173 | 0.66705 | 0.65877 | 0.69018
43602.6124 | 0.87935 | 1.0404 | 0.97957 | 0.80825 | 0.71887 | 0.66548 | 0.65612 | 0.68955
43602.6124 | 0.87604 | 1.0379 | 0.97918 | 0.80684 | 0.71932 | 0.66562 | 0.65904 | 0.68951
43602.6124 | 0.87835 | 1.0403 | 0.98085 | 0.80825 | 0.71904 | 0.66551 | 0.65694 | 0.68937
43602.6126 | 0.87105 | 1.0355 | 0.97735 | 0.80662 | 0.718 | 0.66445 | 0.65878 | 0.68947
43602.6126 | 0.8803 | 1.0389 | 0.97879 | 0.80784 | 0.71845 | 0.6649 | 0.65797 | 0.68956
43602.6126 | 0.87723 | 1.0363 | 0.9777 | 0.80692 | 0.71932 | 0.66519 | 0.65739 | 0.68976
43602.6126 | 0.88569 | 1.0399 | 0.97898 | 0.80866 | 0.71928 | 0.66493 | 0.65675 | 0.68955
43602.6128 | 0.8883 | 1.0427 | 0.98124 | 0.80999 | 0.72051 | 0.6657 | 0.65733 | 0.6896
43602.6128 | 0.86924 | 1.0365 | 0.979 | 0.80648 | 0.71971 | 0.66525 | 0.65632 | 0.68914
43602.6128 | 0.87643 | 1.0374 | 0.97762 | 0.80637 | 0.71805 | 0.66411 | 0.65668 | 0.68904
43602.6128 | 0.88166 | 1.0425 | 0.98097 | 0.80893 | 0.72149 | 0.66615 | 0.65797 | 0.68973
43602.613 | 0.86683 | 1.0339 | 0.97692 | 0.805 | 0.71879 | 0.66418 | 0.65668 | 0.68881
43602.613 | 0.8726 | 1.0346 | 0.97639 | 0.80628 | 0.7172 | 0.66361 | 0.65608 | 0.68892
43602.613 | 0.87489 | 1.0344 | 0.97508 | 0.80485 | 0.71668 | 0.66326 | 0.65463 | 0.68875
43602.6131 | 0.87328 | 1.0359 | 0.97751 | 0.80698 | 0.71719 | 0.6634 | 0.65823 | 0.68883
43602.6132 | 0.88793 | 1.0417 | 0.97964 | 0.80969 | 0.72001 | 0.66521 | 0.65764 | 0.68965
43602.6132 | 0.8736 | 1.0354 | 0.97673 | 0.8067 | 0.72002 | 0.66502 | 0.65879 | 0.68947
43602.6131 | 0.86816 | 1.0304 | 0.97302 | 0.80333 | 0.7169 | 0.66274 | 0.65563 | 0.68873
43602.6133 | 0.86862 | 1.0302 | 0.97246 | 0.80364 | 0.71559 | 0.66206 | 0.65499 | 0.68861
43602.6134 | 0.88364 | 1.0342 | 0.97385 | 0.80575 | 0.71713 | 0.66306 | 0.6548 | 0.68909
43602.6133 | 0.8673 | 1.0288 | 0.97167 | 0.80293 | 0.71575 | 0.66223 | 0.65599 | 0.68824
43602.6135 | 0.87345 | 1.0314 | 0.97145 | 0.80325 | 0.71668 | 0.66256 | 0.65597 | 0.68861
43602.6135 | 0.88134 | 1.0339 | 0.97273 | 0.80506 | 0.71615 | 0.66221 | 0.65489 | 0.68856
43602.6135 | 0.90201 | 1.0386 | 0.97422 | 0.80611 | 0.71809 | 0.66361 | 0.6557 | 0.68898
43602.6137 | 0.8783 | 1.0348 | 0.97243 | 0.80476 | 0.71703 | 0.66297 | 0.65556 | 0.68836
43602.6137 | 0.87906 | 1.0322 | 0.96993 | 0.80251 | 0.71571 | 0.66203 | 0.65326 | 0.68802
43602.6137 | 0.90251 | 1.0403 | 0.97497 | 0.80681 | 0.71738 | 0.66332 | 0.65524 | 0.68868
43602.6138 | 0.892 | 1.0409 | 0.97586 | 0.80634 | 0.71945 | 0.66449 | 0.65624 | 0.68858
43602.6138 | 0.89001 | 1.0402 | 0.97589 | 0.80614 | 0.71841 | 0.66364 | 0.65528 | 0.68812
43602.6138 | 0.89625 | 1.0434 | 0.97836 | 0.80788 | 0.71877 | 0.66379 | 0.65557 | 0.68803
43602.614 | 0.89435 | 1.0435 | 0.97911 | 0.8085 | 0.71897 | 0.66415 | 0.65676 | 0.68761
43602.614 | 0.88945 | 1.0436 | 0.97922 | 0.80858 | 0.72091 | 0.66564 | 0.6582 | 0.68903
43602.614 | 0.89561 | 1.0444 | 0.97954 | 0.80896 | 0.71945 | 0.66462 | 0.65698 | 0.68852
43602.6141 | 0.88188 | 1.041 | 0.97819 | 0.8082 | 0.72036 | 0.66505 | 0.6577 | 0.68885
43602.6141 | 0.8996 | 1.0458 | 0.98068 | 0.80986 | 0.71973 | 0.66499 | 0.65717 | 0.68899
43602.6141 | 0.89798 | 1.0468 | 0.98193 | 0.81128 | 0.72129 | 0.66604 | 0.65897 | 0.68936
43602.6143 | 0.89289 | 1.0438 | 0.97956 | 0.80958 | 0.71982 | 0.66524 | 0.65863 | 0.68943
43602.6143 | 0.87458 | 1.0392 | 0.97792 | 0.80766 | 0.71992 | 0.66549 | 0.65982 | 0.68942
43602.6143 | 0.88979 | 1.042 | 0.97829 | 0.80841 | 0.71862 | 0.6648 | 0.65679 | 0.68935
43602.6145 | 0.87166 | 1.032 | 0.97218 | 0.8039 | 0.71589 | 0.66248 | 0.65728 | 0.68866
43602.6145 | 0.8734 | 1.0325 | 0.97228 | 0.80445 | 0.71626 | 0.66283 | 0.65559 | 0.68895
43602.6144 | 0.88197 | 1.0348 | 0.97331 | 0.805 | 0.71737 | 0.66318 | 0.65499 | 0.68937
43602.6146 | 0.88113 | 1.033 | 0.97105 | 0.803 | 0.7166 | 0.66256 | 0.65462 | 0.68892
43602.6146 | 0.86555 | 1.0273 | 0.96904 | 0.80065 | 0.714 | 0.66093 | 0.65247 | 0.68829
43602.6146 | 0.87965 | 1.035 | 0.97297 | 0.80463 | 0.71564 | 0.66214 | 0.65363 | 0.68853
43602.6148 | 0.88724 | 1.0414 | 0.97818 | 0.8077 | 0.71969 | 0.66479 | 0.6561 | 0.68842
43602.6148 | 0.88948 | 1.0425 | 0.97811 | 0.80778 | 0.71809 | 0.66339 | 0.65551 | 0.68814
43602.6148 | 0.89976 | 1.0475 | 0.98145 | 0.81025 | 0.72023 | 0.66512 | 0.65596 | 0.68859
43602.6148 | 0.90082 | 1.0473 | 0.9818 | 0.81015 | 0.72139 | 0.66622 | 0.65797 | 0.68927
43602.615 | 0.86962 | 1.0371 | 0.97699 | 0.80594 | 0.71866 | 0.66485 | 0.6586 | 0.68882
43602.615 | 0.88769 | 1.0423 | 0.97903 | 0.80823 | 0.71828 | 0.66485 | 0.65723 | 0.68941
43602.615 | 0.87884 | 1.0384 | 0.97713 | 0.80684 | 0.71938 | 0.66501 | 0.6571 | 0.68923
43602.6151 | 0.87813 | 1.0364 | 0.97431 | 0.8049 | 0.71774 | 0.66414 | 0.65631 | 0.68959
43602.6151 | 0.88528 | 1.0392 | 0.97677 | 0.80727 | 0.71681 | 0.66321 | 0.65556 | 0.6887
43602.6151 | 0.91486 | 1.0472 | 0.98094 | 0.81036 | 0.72039 | 0.66567 | 0.65607 | 0.68946
43602.6153 | 0.89053 | 1.0445 | 0.98097 | 0.8101 | 0.72133 | 0.66608 | 0.65801 | 0.68952
43602.6153 | 0.89321 | 1.0439 | 0.97993 | 0.80915 | 0.7195 | 0.66497 | 0.65721 | 0.68887
43602.6153 | 0.88348 | 1.0434 | 0.97974 | 0.80909 | 0.72071 | 0.66588 | 0.65734 | 0.68923
43602.6154 | 0.88839 | 1.0451 | 0.98065 | 0.80981 | 0.7199 | 0.66516 | 0.65752 | 0.6893
43602.6155 | 0.8901 | 1.0454 | 0.97968 | 0.80941 | 0.72081 | 0.66573 | 0.65776 | 0.68928
43602.6154 | 0.88502 | 1.0417 | 0.97888 | 0.80782 | 0.7193 | 0.66502 | 0.65721 | 0.68898
43602.6156 | 0.87241 | 1.0382 | 0.97867 | 0.80637 | 0.72007 | 0.66578 | 0.65693 | 0.68924
43602.6156 | 0.87673 | 1.0399 | 0.9787 | 0.80773 | 0.71754 | 0.66399 | 0.65545 | 0.68897
43602.6156 | 0.88185 | 1.0404 | 0.97808 | 0.80723 | 0.71968 | 0.6651 | 0.6565 | 0.68953
43602.6158 | 0.87588 | 1.0342 | 0.97285 | 0.80372 | 0.71593 | 0.66284 | 0.65818 | 0.68919
43602.6158 | 0.86989 | 1.0327 | 0.97233 | 0.80381 | 0.71534 | 0.66238 | 0.65454 | 0.68866
43602.6158 | 0.87646 | 1.0328 | 0.97159 | 0.80333 | 0.71518 | 0.66215 | 0.65458 | 0.68903
43602.6159 | 0.86466 | 1.0258 | 0.967 | 0.79974 | 0.71336 | 0.66083 | 0.65365 | 0.68854
43602.6159 | 0.85963 | 1.0245 | 0.96708 | 0.80035 | 0.71188 | 0.66007 | 0.652 | 0.68812
43602.6159 | 0.87655 | 1.0286 | 0.96789 | 0.80138 | 0.71374 | 0.6611 | 0.6537 | 0.68862
43602.6161 | 0.87849 | 1.0261 | 0.96605 | 0.7999 | 0.71198 | 0.65982 | 0.65188 | 0.68794
43602.6161 | 0.87505 | 1.0285 | 0.96649 | 0.80058 | 0.71452 | 0.66099 | 0.65253 | 0.68847
43602.6161 | 0.88748 | 1.0286 | 0.96531 | 0.80029 | 0.71256 | 0.65982 | 0.65469 | 0.68764
43602.6162 | 0.87677 | 1.0239 | 0.9617 | 0.79833 | 0.71035 | 0.6587 | 0.65066 | 0.68725
43602.6163 | 0.89519 | 1.0286 | 0.96467 | 0.80095 | 0.71191 | 0.65935 | 0.65141 | 0.68757
43602.6162 | 0.87157 | 1.022 | 0.96002 | 0.79644 | 0.71226 | 0.65947 | 0.65185 | 0.68713
43602.6164 | 0.87749 | 1.02 | 0.95764 | 0.79573 | 0.70918 | 0.65744 | 0.65085 | 0.68635
43602.6164 | 0.88071 | 1.0208 | 0.95779 | 0.79551 | 0.70799 | 0.65639 | 0.64974 | 0.68587
43602.6164 | 0.90766 | 1.0285 | 0.96222 | 0.79905 | 0.71095 | 0.65825 | 0.65263 | 0.6864
43602.6166 | 0.90179 | 1.0269 | 0.96151 | 0.79832 | 0.71093 | 0.65803 | 0.65414 | 0.68548
43602.6166 | 0.90741 | 1.0294 | 0.96236 | 0.79929 | 0.7126 | 0.65937 | 0.65163 | 0.68591
43602.6165 | 0.89681 | 1.0277 | 0.9624 | 0.79843 | 0.71208 | 0.65927 | 0.6522 | 0.68557
43602.6167 | 0.92672 | 1.0427 | 0.97291 | 0.80631 | 0.7161 | 0.66202 | 0.65416 | 0.6857
43602.6167 | 0.91286 | 1.0404 | 0.97223 | 0.80556 | 0.71738 | 0.66298 | 0.65483 | 0.68591
43602.6167 | 0.90355 | 1.0388 | 0.97113 | 0.80481 | 0.71765 | 0.6637 | 0.6551 | 0.68645
43602.6169 | 0.90506 | 1.0405 | 0.97386 | 0.80623 | 0.71863 | 0.66476 | 0.65614 | 0.6872
43602.6169 | 0.93676 | 1.0544 | 0.98332 | 0.81421 | 0.72307 | 0.66781 | 0.65852 | 0.68879
43602.6169 | 0.91568 | 1.0468 | 0.97765 | 0.80965 | 0.72112 | 0.66631 | 0.65748 | 0.68846
43602.617 | 0.89403 | 1.0406 | 0.97602 | 0.80877 | 0.7198 | 0.66614 | 0.65802 | 0.6897
43602.617 | 0.87998 | 1.0381 | 0.97443 | 0.80801 | 0.71943 | 0.66621 | 0.65812 | 0.68975
43602.617 | 0.88947 | 1.0398 | 0.97545 | 0.80878 | 0.71995 | 0.66655 | 0.65858 | 0.69031
43602.6172 | 0.8818 | 1.0368 | 0.97497 | 0.80856 | 0.72114 | 0.66761 | 0.65985 | 0.69202
43602.6172 | 0.86787 | 1.032 | 0.97356 | 0.80685 | 0.71879 | 0.66623 | 0.65837 | 0.69127
43602.6172 | 0.86781 | 1.0322 | 0.97352 | 0.80731 | 0.71947 | 0.66668 | 0.65914 | 0.69197
43602.6174 | 0.86682 | 1.0249 | 0.96732 | 0.80409 | 0.71548 | 0.66343 | 0.65606 | 0.69147
43602.6174 | 0.86243 | 1.0245 | 0.96835 | 0.80454 | 0.71621 | 0.66403 | 0.65912 | 0.69189
43602.6173 | 0.86055 | 1.0237 | 0.96763 | 0.8035 | 0.71447 | 0.66273 | 0.65535 | 0.6913
43602.6175 | 0.86512 | 1.0242 | 0.96783 | 0.80239 | 0.71296 | 0.66128 | 0.65307 | 0.69002
43602.6175 | 0.87986 | 1.027 | 0.96832 | 0.80308 | 0.71541 | 0.66259 | 0.65819 | 0.69074
43602.6175 | 0.86442 | 1.0276 | 0.97015 | 0.80273 | 0.71454 | 0.66234 | 0.65562 | 0.68956
43602.6177 | 0.88219 | 1.0475 | 0.98541 | 0.81268 | 0.72242 | 0.66774 | 0.65852 | 0.69016
43602.6177 | 0.8946 | 1.053 | 0.9888 | 0.81537 | 0.72299 | 0.6683 | 0.66008 | 0.69027
43602.6177 | 0.90429 | 1.0591 | 0.99281 | 0.81808 | 0.73022 | 0.67313 | 0.66388 | 0.69196
43602.6178 | 0.90583 | 1.0637 | 0.99667 | 0.82106 | 0.73124 | 0.67523 | 0.66634 | 0.69328
43602.6178 | 0.89585 | 1.0604 | 0.99613 | 0.82031 | 0.72987 | 0.67439 | 0.66892 | 0.69273
43602.6178 | 0.87896 | 1.0525 | 0.99287 | 0.81792 | 0.72941 | 0.67431 | 0.66557 | 0.69357
43602.618 | 0.85698 | 1.0342 | 0.98189 | 0.8098 | 0.72243 | 0.6704 | 0.66283 | 0.6943
43602.618 | 0.85676 | 1.0358 | 0.98283 | 0.811 | 0.72284 | 0.67103 | 0.66282 | 0.69469
43602.618 | 0.86314 | 1.0345 | 0.97989 | 0.81051 | 0.7225 | 0.67046 | 0.66392 | 0.69507
43602.6181 | 0.85309 | 1.0295 | 0.97906 | 0.80988 | 0.72023 | 0.66891 | 0.66078 | 0.69455
43602.6182 | 0.86 | 1.033 | 0.98013 | 0.81084 | 0.72161 | 0.66939 | 0.66061 | 0.69489
43602.6181 | 0.84892 | 1.029 | 0.98008 | 0.80855 | 0.7205 | 0.66839 | 0.66102 | 0.69342
43602.6183 | 0.85287 | 1.0361 | 0.98704 | 0.81202 | 0.72064 | 0.66815 | 0.66045 | 0.69258
43602.6183 | 0.85657 | 1.0377 | 0.98875 | 0.81239 | 0.72151 | 0.66868 | 0.66057 | 0.69268
43602.6183 | 0.86538 | 1.0448 | 0.99298 | 0.81516 | 0.72396 | 0.67003 | 0.66095 | 0.69269
43602.6185 | 0.871 | 1.0532 | 0.99942 | 0.81833 | 0.72669 | 0.67141 | 0.66221 | 0.69138
43602.6185 | 0.86274 | 1.0497 | 0.99854 | 0.81633 | 0.72518 | 0.67057 | 0.66432 | 0.6912
43602.6185 | 0.87628 | 1.0563 | 1.0017 | 0.8183 | 0.72588 | 0.67117 | 0.66234 | 0.69085
43602.6186 | 0.88274 | 1.0635 | 1.0065 | 0.82201 | 0.72883 | 0.67313 | 0.66402 | 0.69146
43602.6186 | 0.88189 | 1.0655 | 1.0083 | 0.82391 | 0.72997 | 0.67367 | 0.66546 | 0.6918
43602.6186 | 0.88387 | 1.065 | 1.0068 | 0.82319 | 0.73075 | 0.67417 | 0.66461 | 0.69186
43602.6188 | 0.88665 | 1.0669 | 1.0082 | 0.82337 | 0.73036 | 0.6739 | 0.66539 | 0.69174
43602.6188 | 0.89649 | 1.0678 | 1.0072 | 0.82384 | 0.73125 | 0.67431 | 0.66522 | 0.69192
43602.6188 | 0.88386 | 1.0643 | 1.0075 | 0.82288 | 0.73069 | 0.67418 | 0.66529 | 0.69169
43602.6189 | 0.89701 | 1.0714 | 1.0085 | 0.82539 | 0.73215 | 0.67523 | 0.66548 | 0.6924
43602.619 | 0.89733 | 1.0714 | 1.0082 | 0.82621 | 0.73281 | 0.67528 | 0.66662 | 0.69239
43602.6189 | 0.88567 | 1.0653 | 1.0062 | 0.82297 | 0.73103 | 0.67478 | 0.66463 | 0.69213
43602.6191 | 0.89705 | 1.0691 | 1.0069 | 0.82511 | 0.7321 | 0.67543 | 0.66707 | 0.69272
43602.6191 | 0.89271 | 1.0693 | 1.0078 | 0.82496 | 0.73265 | 0.67557 | 0.66577 | 0.69285
43602.6191 | 0.89496 | 1.0686 | 1.0065 | 0.82423 | 0.73285 | 0.67541 | 0.66695 | 0.69258
43602.6193 | 0.89443 | 1.0672 | 1.005 | 0.82373 | 0.73199 | 0.67523 | 0.67018 | 0.69257
43602.6193 | 0.89492 | 1.068 | 1.0039 | 0.82317 | 0.7309 | 0.67463 | 0.66593 | 0.69267
43602.6193 | 0.8983 | 1.0689 | 1.0043 | 0.82414 | 0.73121 | 0.67479 | 0.66463 | 0.69233
43602.6194 | 0.89771 | 1.0687 | 1.005 | 0.82401 | 0.73262 | 0.67521 | 0.66512 | 0.6927
43602.6194 | 0.89984 | 1.0706 | 1.0071 | 0.82505 | 0.73201 | 0.67519 | 0.66478 | 0.69239
43602.6194 | 0.91034 | 1.0779 | 1.0112 | 0.82889 | 0.73684 | 0.67827 | 0.66881 | 0.69421
43602.6196 | 0.90095 | 1.0774 | 1.0131 | 0.82901 | 0.73557 | 0.67802 | 0.66783 | 0.69315
43602.6196 | 0.90998 | 1.0787 | 1.0133 | 0.82918 | 0.73618 | 0.6782 | 0.66783 | 0.69302
43602.6196 | 0.92427 | 1.0847 | 1.0156 | 0.83138 | 0.73715 | 0.67915 | 0.66958 | 0.69365
43602.6197 | 0.91104 | 1.0776 | 1.0121 | 0.8284 | 0.73606 | 0.6786 | 0.66809 | 0.69359
43602.6198 | 0.91202 | 1.079 | 1.0124 | 0.82973 | 0.73655 | 0.67866 | 0.67068 | 0.69357
43602.6197 | 0.90064 | 1.0745 | 1.0099 | 0.82752 | 0.73709 | 0.67926 | 0.66922 | 0.69393
43602.6199 | 0.89691 | 1.0695 | 1.0076 | 0.82509 | 0.73726 | 0.67937 | 0.67017 | 0.69455
43602.6199 | 0.89343 | 1.0675 | 1.0054 | 0.8234 | 0.73283 | 0.67694 | 0.66774 | 0.69351
43602.6199 | 0.89467 | 1.0676 | 1.0047 | 0.82382 | 0.73244 | 0.67668 | 0.66685 | 0.69381
43602.6201 | 0.89087 | 1.0673 | 1.0056 | 0.82452 | 0.73326 | 0.6768 | 0.66725 | 0.69331
43602.6201 | 0.8964 | 1.0684 | 1.0051 | 0.82427 | 0.73399 | 0.67709 | 0.66808 | 0.69395
43602.6201 | 0.90441 | 1.0698 | 1.0045 | 0.8242 | 0.73385 | 0.67695 | 0.66673 | 0.69367
43602.6202 | 0.90607 | 1.0713 | 1.0059 | 0.82518 | 0.73329 | 0.67681 | 0.66739 | 0.69374
43602.6202 | 0.90148 | 1.0709 | 1.0068 | 0.82663 | 0.73512 | 0.67793 | 0.66837 | 0.69427
43602.6202 | 0.90981 | 1.0716 | 1.0054 | 0.82576 | 0.73281 | 0.67642 | 0.66723 | 0.69327
43602.6204 | 0.90197 | 1.0652 | 1.0014 | 0.82221 | 0.73401 | 0.67685 | 0.66801 | 0.6937
43602.6204 | 0.8976 | 1.0636 | 0.99968 | 0.82169 | 0.73143 | 0.67527 | 0.66881 | 0.693
43602.6204 | 0.9035 | 1.0641 | 0.99847 | 0.82149 | 0.73052 | 0.67449 | 0.66519 | 0.69302
43602.6205 | 0.90524 | 1.0643 | 0.99773 | 0.82111 | 0.73038 | 0.67449 | 0.6659 | 0.69269
43602.6206 | 0.90783 | 1.0658 | 0.9989 | 0.82205 | 0.73172 | 0.67531 | 0.66594 | 0.69298
43602.6205 | 0.915 | 1.069 | 1.0008 | 0.824 | 0.73315 | 0.67678 | 0.66746 | 0.69333
43602.6207 | 0.93284 | 1.077 | 1.0062 | 0.82783 | 0.7349 | 0.67745 | 0.66758 | 0.69316
43602.6207 | 0.90738 | 1.0687 | 1.0012 | 0.82372 | 0.73694 | 0.67913 | 0.66851 | 0.69357
43602.6207 | 0.91463 | 1.0701 | 1.001 | 0.82419 | 0.73141 | 0.67545 | 0.66575 | 0.69226
43602.6209 | 0.91406 | 1.0708 | 1.0013 | 0.82468 | 0.73278 | 0.67653 | 0.66687 | 0.69272
43602.6209 | 0.92421 | 1.0715 | 1.001 | 0.82409 | 0.73342 | 0.67698 | 0.66724 | 0.69281
43602.6209 | 0.90872 | 1.0675 | 1.0008 | 0.82318 | 0.73454 | 0.6778 | 0.66718 | 0.6927
43602.621 | 0.92285 | 1.0709 | 1.0028 | 0.82521 | 0.73306 | 0.67677 | 0.66641 | 0.6928
43602.621 | 0.91538 | 1.0703 | 1.0029 | 0.82546 | 0.73538 | 0.67844 | 0.6715 | 0.6936
43602.621 | 0.92291 | 1.0711 | 1.0025 | 0.82527 | 0.73404 | 0.67763 | 0.66893 | 0.69305
43602.6212 | 0.92101 | 1.0753 | 1.0061 | 0.8283 | 0.73642 | 0.67912 | 0.66895 | 0.69371
43602.6212 | 0.90888 | 1.0714 | 1.0042 | 0.8254 | 0.73556 | 0.67898 | 0.66987 | 0.69387
43602.6212 | 0.92498 | 1.0768 | 1.0076 | 0.82912 | 0.73607 | 0.67914 | 0.67137 | 0.69375
43602.6214 | 0.9309 | 1.0845 | 1.014 | 0.83368 | 0.74094 | 0.68266 | 0.67543 | 0.69516
43602.6214 | 0.91959 | 1.0813 | 1.0118 | 0.83123 | 0.73987 | 0.68229 | 0.67231 | 0.69483
43602.6213 | 0.93354 | 1.0843 | 1.0141 | 0.833 | 0.73968 | 0.68203 | 0.67112 | 0.6949
43602.6215 | 0.90851 | 1.0799 | 1.013 | 0.83133 | 0.74049 | 0.6832 | 0.67318 | 0.69612
43602.6215 | 0.92099 | 1.0829 | 1.0139 | 0.83328 | 0.74124 | 0.68341 | 0.67295 | 0.69645
43602.6215 | 0.91973 | 1.0836 | 1.0159 | 0.8345 | 0.74274 | 0.6844 | 0.67455 | 0.69725
43602.6217 | 0.9048 | 1.076 | 1.0113 | 0.83151 | 0.73983 | 0.68309 | 0.67409 | 0.69772
43602.6217 | 0.90048 | 1.0741 | 1.0105 | 0.83038 | 0.74006 | 0.68312 | 0.6724 | 0.69767
43602.6217 | 0.90679 | 1.076 | 1.011 | 0.83143 | 0.73956 | 0.68261 | 0.67323 | 0.69746
43602.6218 | 0.89825 | 1.0731 | 1.0111 | 0.82989 | 0.73892 | 0.68193 | 0.67305 | 0.69731
43602.6218 | 0.8955 | 1.073 | 1.0118 | 0.83029 | 0.73892 | 0.68198 | 0.67229 | 0.69758
43602.6218 | 0.89941 | 1.0751 | 1.0127 | 0.83141 | 0.73958 | 0.68246 | 0.67263 | 0.69764
43602.622 | 0.89186 | 1.074 | 1.0139 | 0.83146 | 0.73991 | 0.68249 | 0.67361 | 0.697
43602.622 | 0.89739 | 1.0728 | 1.0116 | 0.83006 | 0.73817 | 0.68151 | 0.67198 | 0.69662
43602.622 | 0.89676 | 1.075 | 1.0143 | 0.83176 | 0.73909 | 0.68227 | 0.67226 | 0.69685
43602.6222 | 0.91638 | 1.0855 | 1.0196 | 0.83636 | 0.74145 | 0.68335 | 0.67665 | 0.69674
43602.6222 | 0.91407 | 1.0872 | 1.0217 | 0.83773 | 0.74346 | 0.68501 | 0.67495 | 0.69732
43602.6222 | 0.91377 | 1.0876 | 1.0227 | 0.8371 | 0.74357 | 0.68531 | 0.67513 | 0.69687
43602.6223 | 0.9329 | 1.0983 | 1.0309 | 0.84333 | 0.74565 | 0.68774 | 0.6781 | 0.69833
43602.6224 | 0.92327 | 1.0979 | 1.0311 | 0.84396 | 0.75189 | 0.69123 | 0.68044 | 0.70011
43602.6223 | 0.90163 | 1.0828 | 1.0237 | 0.83744 | 0.74518 | 0.68851 | 0.68135 | 0.70047
43602.6227 | 0.89898 | 1.077 | 1.0195 | 0.83385 | 0.74325 | 0.68707 | 0.6774 | 0.70028
43602.6227 | 0.89544 | 1.0752 | 1.0191 | 0.83462 | 0.74265 | 0.6864 | 0.67591 | 0.70002
43602.6227 | 0.89914 | 1.0771 | 1.0196 | 0.83476 | 0.74311 | 0.68679 | 0.67655 | 0.70009
43602.6229 | 0.89718 | 1.0788 | 1.0214 | 0.83566 | 0.74212 | 0.68525 | 0.67588 | 0.69926
43602.6229 | 0.885 | 1.0771 | 1.0243 | 0.83574 | 0.74306 | 0.6861 | 0.67889 | 0.69933
43602.6228 | 0.90368 | 1.0851 | 1.0262 | 0.83822 | 0.74476 | 0.68702 | 0.67655 | 0.69928
43602.623 | 0.91306 | 1.0974 | 1.0369 | 0.84329 | 0.74925 | 0.69007 | 0.68313 | 0.69897
43602.623 | 0.91958 | 1.0997 | 1.0376 | 0.84448 | 0.74996 | 0.6904 | 0.6799 | 0.69924
43602.623 | 0.91844 | 1.1005 | 1.04 | 0.84554 | 0.75044 | 0.69072 | 0.68085 | 0.69926
43602.6232 | 0.91607 | 1.101 | 1.0405 | 0.84664 | 0.75228 | 0.69248 | 0.6831 | 0.70005
43602.6232 | 0.92324 | 1.1052 | 1.0423 | 0.84779 | 0.7525 | 0.6928 | 0.68177 | 0.69992
43602.6232 | 0.91879 | 1.1025 | 1.041 | 0.84682 | 0.7527 | 0.693 | 0.68108 | 0.7004
43602.6233 | 0.91633 | 1.0993 | 1.0371 | 0.84526 | 0.75039 | 0.69183 | 0.68137 | 0.70017
43602.6233 | 0.91473 | 1.0988 | 1.0372 | 0.84529 | 0.75159 | 0.69215 | 0.68059 | 0.70057
43602.6233 | 0.91985 | 1.0992 | 1.0369 | 0.84463 | 0.75111 | 0.69199 | 0.68051 | 0.70024
43602.6235 | 0.91713 | 1.0952 | 1.0334 | 0.84246 | 0.74929 | 0.69121 | 0.68097 | 0.70034
43602.6235 | 0.91302 | 1.0936 | 1.0332 | 0.84282 | 0.74978 | 0.69155 | 0.68476 | 0.70059
43602.6235 | 0.91451 | 1.0937 | 1.0331 | 0.84229 | 0.74968 | 0.6915 | 0.68155 | 0.70043
43602.6237 | 0.912 | 1.0976 | 1.0378 | 0.84513 | 0.75111 | 0.69259 | 0.68214 | 0.70068
43602.6237 | 0.92258 | 1.101 | 1.0388 | 0.84686 | 0.75196 | 0.69316 | 0.68196 | 0.70105
43602.6236 | 0.92622 | 1.1033 | 1.0403 | 0.84747 | 0.75296 | 0.6938 | 0.68256 | 0.70088
43602.6238 | 0.92111 | 1.1025 | 1.0404 | 0.84778 | 0.7536 | 0.69457 | 0.68703 | 0.70139
43602.6238 | 0.92217 | 1.1021 | 1.04 | 0.84671 | 0.7538 | 0.69431 | 0.68346 | 0.70151
43602.6238 | 0.91569 | 1.0987 | 1.0378 | 0.84547 | 0.75221 | 0.69374 | 0.68296 | 0.70122
43602.624 | 0.91403 | 1.0926 | 1.0318 | 0.84152 | 0.75067 | 0.69228 | 0.68451 | 0.7014
43602.624 | 0.9036 | 1.0883 | 1.0303 | 0.84035 | 0.74874 | 0.69119 | 0.68123 | 0.70098
43602.624 | 0.90448 | 1.0874 | 1.029 | 0.83999 | 0.74848 | 0.69102 | 0.682 | 0.7009
43602.6241 | 0.89982 | 1.0834 | 1.0256 | 0.8383 | 0.74651 | 0.68944 | 0.67928 | 0.70082
43602.6242 | 0.90584 | 1.0858 | 1.0258 | 0.83902 | 0.7462 | 0.68919 | 0.68318 | 0.70066
43602.6241 | 0.90913 | 1.0854 | 1.0241 | 0.83908 | 0.7467 | 0.6891 | 0.68095 | 0.70057
43602.6243 | 0.90664 | 1.0831 | 1.0226 | 0.83693 | 0.74528 | 0.6881 | 0.67741 | 0.69999
43602.6243 | 0.90571 | 1.0841 | 1.023 | 0.83791 | 0.74565 | 0.68807 | 0.67911 | 0.69996
43602.6243 | 0.90247 | 1.0831 | 1.0224 | 0.83783 | 0.74503 | 0.68752 | 0.6777 | 0.69943
43602.6245 | 0.91223 | 1.0852 | 1.0225 | 0.83695 | 0.7446 | 0.68704 | 0.6768 | 0.69901
43602.6245 | 0.90084 | 1.0837 | 1.0231 | 0.83709 | 0.74435 | 0.68689 | 0.67629 | 0.6987
43602.6245 | 0.91756 | 1.0892 | 1.0253 | 0.83898 | 0.7471 | 0.68864 | 0.67821 | 0.69927
43602.6246 | 0.93236 | 1.1029 | 1.0351 | 0.84591 | 0.75138 | 0.69193 | 0.68146 | 0.69969
43602.6246 | 0.93247 | 1.1035 | 1.036 | 0.84625 | 0.75307 | 0.6928 | 0.68088 | 0.7
43602.6246 | 0.93909 | 1.1054 | 1.0369 | 0.84763 | 0.75199 | 0.69229 | 0.68139 | 0.69954
43602.6248 | 0.9186 | 1.096 | 1.0324 | 0.84225 | 0.74986 | 0.69152 | 0.68119 | 0.6996
43602.6248 | 0.92789 | 1.1014 | 1.0347 | 0.84556 | 0.75031 | 0.69185 | 0.68138 | 0.69986
43602.6248 | 0.92784 | 1.1026 | 1.0363 | 0.84627 | 0.75247 | 0.69308 | 0.68168 | 0.70025
43602.625 | 0.93042 | 1.1024 | 1.0358 | 0.84636 | 0.75138 | 0.69253 | 0.68115 | 0.70049
43602.625 | 0.91437 | 1.0951 | 1.0324 | 0.84286 | 0.75173 | 0.69255 | 0.68235 | 0.70069
43602.625 | 0.91888 | 1.0949 | 1.0315 | 0.84154 | 0.74901 | 0.69126 | 0.67982 | 0.70018
43602.6251 | 0.91327 | 1.093 | 1.0309 | 0.84188 | 0.74798 | 0.69037 | 0.6795 | 0.70008
43602.6251 | 0.90751 | 1.0912 | 1.031 | 0.84172 | 0.74887 | 0.69103 | 0.68035 | 0.70009
43602.6251 | 0.91413 | 1.0915 | 1.0297 | 0.84037 | 0.74871 | 0.69076 | 0.67972 | 0.70004
43602.6253 | 0.90876 | 1.0883 | 1.0268 | 0.83892 | 0.74722 | 0.68948 | 0.67791 | 0.69995
43602.6253 | 0.91636 | 1.0897 | 1.0269 | 0.83999 | 0.74689 | 0.68905 | 0.67844 | 0.69986
43602.6253 | 0.90062 | 1.0836 | 1.0249 | 0.83723 | 0.74554 | 0.68824 | 0.6785 | 0.69976
43602.6255 | 0.89495 | 1.0763 | 1.0185 | 0.83295 | 0.74163 | 0.68538 | 0.67614 | 0.69819
43602.6255 | 0.90566 | 1.0816 | 1.0207 | 0.83652 | 0.74223 | 0.68607 | 0.67569 | 0.69843
43602.6254 | 0.91392 | 1.0848 | 1.0208 | 0.83699 | 0.7435 | 0.68653 | 0.67575 | 0.69846
43602.6256 | 0.90124 | 1.078 | 1.0165 | 0.83339 | 0.7406 | 0.6839 | 0.6739 | 0.6971
43602.6256 | 0.90442 | 1.0792 | 1.0179 | 0.8341 | 0.74146 | 0.68445 | 0.67395 | 0.69751
43602.6256 | 0.90034 | 1.0789 | 1.0173 | 0.8329 | 0.74289 | 0.68484 | 0.67495 | 0.69701
43602.6258 | 0.91697 | 1.0888 | 1.024 | 0.83912 | 0.74658 | 0.68746 | 0.67656 | 0.69776
43602.6258 | 0.90241 | 1.0816 | 1.0203 | 0.83491 | 0.7433 | 0.68556 | 0.67541 | 0.69643
43602.6258 | 0.93014 | 1.0952 | 1.027 | 0.84145 | 0.74757 | 0.68826 | 0.67757 | 0.69772
43602.6259 | 0.91537 | 1.0851 | 1.0211 | 0.83559 | 0.74341 | 0.68561 | 0.67619 | 0.69648
43602.626 | 0.93206 | 1.0921 | 1.0245 | 0.83949 | 0.74482 | 0.68648 | 0.67543 | 0.6973
43602.6259 | 0.9062 | 1.0847 | 1.0221 | 0.83678 | 0.74509 | 0.68676 | 0.67881 | 0.69728
43602.6261 | 0.90742 | 1.0804 | 1.0163 | 0.83348 | 0.74191 | 0.68399 | 0.67471 | 0.69621
43602.6261 | 0.90255 | 1.0781 | 1.0154 | 0.83279 | 0.74148 | 0.68327 | 0.67316 | 0.69616
43602.6261 | 0.90313 | 1.0767 | 1.0142 | 0.83182 | 0.74111 | 0.68356 | 0.67383 | 0.69664
43602.6263 | 0.90968 | 1.0782 | 1.0141 | 0.83186 | 0.73966 | 0.6827 | 0.67106 | 0.69551
43602.6263 | 0.91116 | 1.0816 | 1.016 | 0.83444 | 0.7415 | 0.6839 | 0.67803 | 0.69634
43602.6263 | 0.92756 | 1.0857 | 1.0184 | 0.83628 | 0.74219 | 0.68428 | 0.67429 | 0.69602
43602.6264 | 0.92518 | 1.088 | 1.0201 | 0.83712 | 0.74308 | 0.6847 | 0.67518 | 0.69548
43602.6265 | 0.91727 | 1.086 | 1.0197 | 0.83662 | 0.74476 | 0.68591 | 0.67983 | 0.69596
43602.6264 | 0.92297 | 1.0861 | 1.0181 | 0.83613 | 0.74315 | 0.68482 | 0.6751 | 0.69579
43602.6266 | 0.90016 | 1.0729 | 1.0105 | 0.82954 | 0.73778 | 0.68105 | 0.67683 | 0.69483
43602.6266 | 0.9178 | 1.0812 | 1.0148 | 0.8344 | 0.74 | 0.68284 | 0.67363 | 0.69571
43602.6266 | 0.91437 | 1.0768 | 1.0107 | 0.83095 | 0.74036 | 0.68264 | 0.67337 | 0.69543
43602.6268 | 0.89797 | 1.0691 | 1.0069 | 0.82718 | 0.73988 | 0.68198 | 0.67239 | 0.6954
43602.6268 | 0.90487 | 1.0705 | 1.0071 | 0.82762 | 0.73531 | 0.67953 | 0.66963 | 0.69397
43602.6268 | 0.90725 | 1.0734 | 1.0083 | 0.82984 | 0.73972 | 0.68172 | 0.67293 | 0.69536
43602.6269 | 0.92309 | 1.078 | 1.0103 | 0.83174 | 0.74016 | 0.6819 | 0.67123 | 0.69501
43602.627 | 0.92059 | 1.0776 | 1.0094 | 0.83127 | 0.73916 | 0.6813 | 0.6754 | 0.69451
43602.6269 | 0.91812 | 1.0765 | 1.0092 | 0.83092 | 0.74004 | 0.6818 | 0.67257 | 0.69499
43602.6271 | 0.91592 | 1.0771 | 1.0095 | 0.83091 | 0.73953 | 0.68163 | 0.67272 | 0.69504
43602.6271 | 0.92295 | 1.0771 | 1.009 | 0.83059 | 0.73843 | 0.68073 | 0.67375 | 0.69401
43602.6271 | 0.92198 | 1.0761 | 1.0077 | 0.82953 | 0.73911 | 0.68119 | 0.67172 | 0.69439
43602.6273 | 0.9157 | 1.0784 | 1.0108 | 0.83194 | 0.741 | 0.68234 | 0.67367 | 0.69469
43602.6273 | 0.9351 | 1.0813 | 1.0116 | 0.83281 | 0.74087 | 0.68243 | 0.67189 | 0.69487
43602.6273 | 0.92194 | 1.0783 | 1.0104 | 0.83083 | 0.74009 | 0.68182 | 0.67178 | 0.69414
43602.6274 | 0.91528 | 1.0731 | 1.0057 | 0.82768 | 0.73762 | 0.68066 | 0.67265 | 0.69371
43602.6274 | 0.91977 | 1.0778 | 1.0102 | 0.83162 | 0.73773 | 0.68047 | 0.67243 | 0.69379
43602.6274 | 0.91365 | 1.0738 | 1.0065 | 0.82876 | 0.74122 | 0.68269 | 0.67353 | 0.69491
43602.6276 | 0.92676 | 1.0722 | 1.0041 | 0.82771 | 0.73603 | 0.67907 | 0.66909 | 0.69337
43602.6276 | 0.91512 | 1.0688 | 1.0027 | 0.82656 | 0.73794 | 0.6808 | 0.67096 | 0.69423
43602.6276 | 0.92146 | 1.07 | 1.002 | 0.82661 | 0.73285 | 0.67719 | 0.67001 | 0.69275
43602.6278 | 0.9267 | 1.0694 | 1 | 0.82605 | 0.73438 | 0.67813 | 0.66813 | 0.69297
43602.6278 | 0.9338 | 1.072 | 1.0017 | 0.82636 | 0.7344 | 0.67782 | 0.66825 | 0.69264
43602.6278 | 0.91778 | 1.0697 | 1.0025 | 0.82621 | 0.73753 | 0.68019 | 0.6699 | 0.69293
43602.6279 | 0.92695 | 1.0846 | 1.0136 | 0.8336 | 0.74086 | 0.68273 | 0.67464 | 0.69286
43602.6279 | 0.95562 | 1.0915 | 1.0167 | 0.83644 | 0.74298 | 0.68415 | 0.6734 | 0.69328
43602.6279 | 0.94899 | 1.0888 | 1.0164 | 0.83609 | 0.74196 | 0.68369 | 0.67271 | 0.6931
43602.6281 | 0.93328 | 1.0791 | 1.0107 | 0.83235 | 0.73963 | 0.6822 | 0.67105 | 0.69373
43602.6281 | 0.91928 | 1.0756 | 1.0096 | 0.83091 | 0.73911 | 0.68177 | 0.67396 | 0.69343
43602.6281 | 0.91349 | 1.0717 | 1.0055 | 0.82818 | 0.73958 | 0.682 | 0.67527 | 0.69442
43602.6283 | 0.9012 | 1.0599 | 0.99634 | 0.82215 | 0.73207 | 0.67666 | 0.66583 | 0.69333
43602.6283 | 0.91337 | 1.0634 | 0.99825 | 0.8245 | 0.73415 | 0.67788 | 0.66996 | 0.69428
43602.6282 | 0.88909 | 1.054 | 0.99307 | 0.81948 | 0.73072 | 0.67543 | 0.66592 | 0.6929
43602.6284 | 0.92106 | 1.0597 | 0.99349 | 0.82107 | 0.73037 | 0.6743 | 0.66529 | 0.69256
43602.6284 | 0.89543 | 1.0534 | 0.99056 | 0.8179 | 0.7316 | 0.67527 | 0.6649 | 0.69314
43602.6284 | 0.90491 | 1.0542 | 0.98925 | 0.81808 | 0.72937 | 0.67378 | 0.66548 | 0.69233
43602.6286 | 0.90923 | 1.0573 | 0.99127 | 0.81972 | 0.73069 | 0.67426 | 0.66528 | 0.69104
43602.6286 | 0.91816 | 1.0637 | 0.99582 | 0.82287 | 0.73161 | 0.67536 | 0.6657 | 0.69152
43602.6286 | 0.92242 | 1.0665 | 0.99683 | 0.82383 | 0.73283 | 0.67644 | 0.66709 | 0.69129
43602.6288 | 0.95494 | 1.0826 | 1.0102 | 0.83365 | 0.7373 | 0.68012 | 0.67016 | 0.69245
43602.6288 | 0.92714 | 1.0735 | 1.0047 | 0.82926 | 0.73827 | 0.68057 | 0.66953 | 0.69233
43602.6287 | 0.91623 | 1.0682 | 1.0006 | 0.82622 | 0.73672 | 0.67989 | 0.67027 | 0.69299
43602.6289 | 0.91382 | 1.0645 | 0.99804 | 0.825 | 0.73331 | 0.67809 | 0.66956 | 0.69377
43602.6289 | 0.91048 | 1.0643 | 0.99933 | 0.82586 | 0.73566 | 0.67948 | 0.67083 | 0.69496
43602.6289 | 0.89504 | 1.0546 | 0.99234 | 0.82077 | 0.73299 | 0.67782 | 0.66973 | 0.6946
43602.6291 | 0.88676 | 1.0453 | 0.98608 | 0.81696 | 0.7288 | 0.67464 | 0.66637 | 0.69488
43602.6291 | 0.88455 | 1.0441 | 0.98499 | 0.81598 | 0.72679 | 0.6735 | 0.66443 | 0.6938
43602.6291 | 0.87243 | 1.0408 | 0.98444 | 0.81523 | 0.72672 | 0.67297 | 0.66561 | 0.69409
43602.6292 | 0.87953 | 1.0418 | 0.98416 | 0.81513 | 0.72559 | 0.67201 | 0.66421 | 0.69314
43602.6293 | 0.87499 | 1.0411 | 0.98351 | 0.81458 | 0.72527 | 0.67123 | 0.66352 | 0.69282
43602.6292 | 0.86948 | 1.0399 | 0.98487 | 0.81527 | 0.72573 | 0.67162 | 0.66381 | 0.69295
43602.6294 | 0.89127 | 1.0515 | 0.98961 | 0.81841 | 0.72797 | 0.67274 | 0.66424 | 0.69243
43602.6294 | 0.89291 | 1.0513 | 0.98925 | 0.81852 | 0.72676 | 0.67203 | 0.66362 | 0.69185
43602.6294 | 0.89133 | 1.0507 | 0.99014 | 0.81891 | 0.72775 | 0.67258 | 0.66462 | 0.69209
43602.6296 | 0.90336 | 1.0537 | 0.99018 | 0.81886 | 0.7304 | 0.67452 | 0.66554 | 0.69274
43602.6296 | 0.88504 | 1.0484 | 0.98771 | 0.81562 | 0.7273 | 0.67228 | 0.66378 | 0.69179
43602.6296 | 0.9145 | 1.0543 | 0.99105 | 0.81954 | 0.72786 | 0.67315 | 0.6643 | 0.69227
43602.6297 | 0.87956 | 1.0437 | 0.98434 | 0.81533 | 0.72423 | 0.67042 | 0.66189 | 0.69201
43602.6297 | 0.88881 | 1.0465 | 0.98483 | 0.81561 | 0.72561 | 0.67145 | 0.66744 | 0.69222
43602.6297 | 0.88948 | 1.045 | 0.98456 | 0.81538 | 0.72513 | 0.67094 | 0.66457 | 0.69198
43602.6299 | 0.88316 | 1.0462 | 0.98679 | 0.81683 | 0.72644 | 0.67186 | 0.66387 | 0.69225
43602.6299 | 0.87769 | 1.0433 | 0.98556 | 0.81511 | 0.72596 | 0.67155 | 0.66328 | 0.69226
43602.6299 | 0.88114 | 1.0423 | 0.9838 | 0.81396 | 0.72491 | 0.67092 | 0.66591 | 0.69217
43602.6301 | 0.87097 | 1.0347 | 0.97819 | 0.81138 | 0.72164 | 0.66895 | 0.66077 | 0.69202
43602.6301 | 0.8724 | 1.0363 | 0.97921 | 0.812 | 0.72267 | 0.66948 | 0.6619 | 0.69184
43602.6301 | 0.86718 | 1.0315 | 0.9767 | 0.81038 | 0.72128 | 0.66828 | 0.6595 | 0.69148
43602.6302 | 0.88782 | 1.0391 | 0.98016 | 0.81294 | 0.7226 | 0.66903 | 0.66184 | 0.69127
43602.6303 | 0.87504 | 1.0373 | 0.97917 | 0.81125 | 0.72154 | 0.6682 | 0.66013 | 0.69024
43602.6302 | 0.89943 | 1.0503 | 0.98895 | 0.81817 | 0.72554 | 0.67121 | 0.66285 | 0.69098
43602.6304 | 0.89117 | 1.0518 | 0.99004 | 0.81767 | 0.72916 | 0.67329 | 0.66485 | 0.69096
43602.6304 | 0.88996 | 1.0517 | 0.99042 | 0.81849 | 0.72749 | 0.67251 | 0.66455 | 0.69118
43602.6304 | 0.89679 | 1.0534 | 0.9915 | 0.81944 | 0.72874 | 0.67374 | 0.665 | 0.69181
43602.6306 | 0.87315 | 1.0392 | 0.98262 | 0.81234 | 0.72329 | 0.67061 | 0.66384 | 0.69197
43602.6306 | 0.87384 | 1.0396 | 0.9838 | 0.8139 | 0.72464 | 0.67156 | 0.66646 | 0.69285
43602.6306 | 0.8667 | 1.0352 | 0.97996 | 0.81178 | 0.72294 | 0.67027 | 0.66486 | 0.69284
43602.6307 | 0.85123 | 1.0169 | 0.96613 | 0.80345 | 0.71701 | 0.66634 | 0.6603 | 0.69306
43602.6308 | 0.84266 | 1.0122 | 0.9632 | 0.80103 | 0.71475 | 0.66501 | 0.65923 | 0.69227
43602.6307 | 0.84041 | 1.0075 | 0.95904 | 0.79833 | 0.71263 | 0.66363 | 0.65748 | 0.6924
43602.6309 | 0.8422 | 1.001 | 0.95264 | 0.79574 | 0.70909 | 0.66022 | 0.65378 | 0.69151
43602.6309 | 0.82565 | 0.99431 | 0.95013 | 0.79313 | 0.70833 | 0.65992 | 0.6539 | 0.69138
43602.6309 | 0.8182 | 0.99171 | 0.95002 | 0.79236 | 0.70646 | 0.65882 | 0.65347 | 0.69105
43602.6311 | 0.83579 | 0.9965 | 0.9496 | 0.7928 | 0.70611 | 0.6575 | 0.65205 | 0.68933
43602.6311 | 0.84357 | 0.99955 | 0.95058 | 0.79282 | 0.70631 | 0.6572 | 0.65129 | 0.68968
43602.6311 | 0.84167 | 1.0013 | 0.95141 | 0.79313 | 0.70569 | 0.65659 | 0.65241 | 0.68829
43602.6312 | 0.85766 | 1.0081 | 0.95531 | 0.79566 | 0.70743 | 0.65704 | 0.65038 | 0.6877
43602.6313 | 0.8697 | 1.0104 | 0.95651 | 0.7967 | 0.70813 | 0.65727 | 0.65419 | 0.68721
43602.6312 | 0.86423 | 1.0088 | 0.95469 | 0.79596 | 0.70759 | 0.65676 | 0.65031 | 0.68649
43602.6314 | 0.89976 | 1.0207 | 0.95939 | 0.7993 | 0.70995 | 0.6584 | 0.65192 | 0.68638
43602.6314 | 0.88727 | 1.0204 | 0.95947 | 0.79989 | 0.71263 | 0.66001 | 0.65289 | 0.68663
43602.6314 | 0.9002 | 1.0259 | 0.96305 | 0.8018 | 0.71139 | 0.65982 | 0.6528 | 0.68596
43602.6316 | 0.88346 | 1.0265 | 0.9649 | 0.80388 | 0.7163 | 0.66449 | 0.65697 | 0.68804
43602.6316 | 0.89136 | 1.0303 | 0.96737 | 0.80603 | 0.71728 | 0.66547 | 0.65831 | 0.68859
43602.6316 | 0.86586 | 1.0205 | 0.96284 | 0.80253 | 0.71557 | 0.66412 | 0.65764 | 0.68898
43602.6317 | 0.85689 | 1.0112 | 0.95739 | 0.80012 | 0.71333 | 0.66379 | 0.65737 | 0.6915
43602.6318 | 0.85961 | 1.0104 | 0.95567 | 0.79855 | 0.71316 | 0.66372 | 0.65609 | 0.69138
43602.6317 | 0.84987 | 1.0027 | 0.95008 | 0.79466 | 0.7107 | 0.66193 | 0.6586 | 0.69159
43602.6319 | 0.82236 | 0.98099 | 0.93623 | 0.78584 | 0.70232 | 0.65584 | 0.65212 | 0.69084
43602.6319 | 0.83527 | 0.98299 | 0.93475 | 0.78486 | 0.70171 | 0.65538 | 0.65001 | 0.69069
43602.6319 | 0.82118 | 0.97902 | 0.93489 | 0.78449 | 0.70043 | 0.65394 | 0.6493 | 0.68995
43602.6321 | 0.83247 | 0.98296 | 0.93557 | 0.78427 | 0.69932 | 0.6521 | 0.64746 | 0.68805
43602.6321 | 0.82926 | 0.98297 | 0.93693 | 0.78501 | 0.69924 | 0.6519 | 0.64633 | 0.68792
43602.6321 | 0.84568 | 0.99035 | 0.9402 | 0.78686 | 0.70034 | 0.65266 | 0.6462 | 0.68772
43602.6322 | 0.83814 | 0.9943 | 0.94337 | 0.78857 | 0.70326 | 0.65401 | 0.64727 | 0.68598
43602.6323 | 0.87356 | 1.0039 | 0.94668 | 0.79129 | 0.70382 | 0.6547 | 0.64852 | 0.68682
43602.6322 | 0.88243 | 1.0079 | 0.94885 | 0.79292 | 0.70736 | 0.65638 | 0.64958 | 0.68636
43602.6324 | 0.90762 | 1.0165 | 0.95314 | 0.79627 | 0.70936 | 0.65749 | 0.65119 | 0.68548
43602.6324 | 0.91387 | 1.0182 | 0.95298 | 0.79634 | 0.70962 | 0.65829 | 0.65117 | 0.68532
43602.6324 | 0.90639 | 1.0201 | 0.95486 | 0.79737 | 0.70964 | 0.65801 | 0.65153 | 0.68514
43602.6326 | 0.92737 | 1.0308 | 0.96235 | 0.80351 | 0.71162 | 0.65956 | 0.65535 | 0.6853
43602.6326 | 0.92992 | 1.0299 | 0.96191 | 0.80281 | 0.71818 | 0.66423 | 0.65567 | 0.68651
43602.6326 | 0.9187 | 1.0255 | 0.96003 | 0.80083 | 0.71435 | 0.66216 | 0.65451 | 0.68551
43602.6327 | 0.9318 | 1.0519 | 0.98112 | 0.81586 | 0.72646 | 0.6716 | 0.66141 | 0.68817
43602.6328 | 0.95912 | 1.0617 | 0.98855 | 0.82144 | 0.72781 | 0.67295 | 0.66365 | 0.68902
43602.6327 | 0.94796 | 1.0572 | 0.98586 | 0.8187 | 0.72788 | 0.67345 | 0.66527 | 0.69008
43602.6329 | 0.92826 | 1.0561 | 0.98687 | 0.82049 | 0.73008 | 0.67536 | 0.66967 | 0.69156
43602.6329 | 0.91845 | 1.0492 | 0.98259 | 0.81705 | 0.72952 | 0.67499 | 0.66574 | 0.69224
43602.6329 | 0.92626 | 1.0579 | 0.98933 | 0.82267 | 0.73228 | 0.67701 | 0.66803 | 0.69349
43602.6331 | 0.89946 | 1.0419 | 0.9788 | 0.81669 | 0.7281 | 0.67442 | 0.66597 | 0.69548
43602.6331 | 0.87556 | 1.0318 | 0.97311 | 0.81182 | 0.72697 | 0.67374 | 0.66844 | 0.69544
43602.6331 | 0.8698 | 1.0241 | 0.96714 | 0.80789 | 0.72098 | 0.6698 | 0.66345 | 0.69466
43602.6332 | 0.83931 | 1.0011 | 0.95265 | 0.79756 | 0.71375 | 0.66428 | 0.65753 | 0.69376
43602.6333 | 0.84455 | 1.0003 | 0.95035 | 0.79589 | 0.71122 | 0.66298 | 0.65582 | 0.69324
43602.6332 | 0.84206 | 1.0028 | 0.95276 | 0.79689 | 0.71055 | 0.66123 | 0.65473 | 0.69166
43602.6334 | 0.8753 | 1.0107 | 0.9549 | 0.79925 | 0.71189 | 0.66058 | 0.65562 | 0.68989
43602.6334 | 0.8535 | 1.0079 | 0.95518 | 0.79768 | 0.71066 | 0.65976 | 0.65421 | 0.68919
43602.6334 | 0.88074 | 1.0159 | 0.95721 | 0.79955 | 0.71123 | 0.65987 | 0.65353 | 0.68851
43602.6336 | 0.90183 | 1.0258 | 0.96143 | 0.80318 | 0.71606 | 0.66293 | 0.65999 | 0.68729
43602.6336 | 0.8878 | 1.0192 | 0.95643 | 0.79946 | 0.71245 | 0.65999 | 0.65491 | 0.68605
43602.6336 | 0.91768 | 1.0265 | 0.96134 | 0.8028 | 0.71498 | 0.66168 | 0.65485 | 0.68659
43602.6337 | 0.91278 | 1.0202 | 0.95423 | 0.79905 | 0.71343 | 0.66112 | 0.6582 | 0.68646
43602.6338 | 0.89562 | 1.0074 | 0.94611 | 0.79252 | 0.70882 | 0.65781 | 0.65264 | 0.6855
43602.6337 | 0.8904 | 1.009 | 0.94674 | 0.79402 | 0.71036 | 0.65913 | 0.65344 | 0.6864
43602.6339 | 0.91949 | 1.0109 | 0.9457 | 0.7943 | 0.70698 | 0.65686 | 0.65017 | 0.68561
43602.6339 | 0.89467 | 1.0012 | 0.93999 | 0.78953 | 0.70641 | 0.65649 | 0.64997 | 0.68561
43602.6339 | 0.89781 | 1.0023 | 0.94094 | 0.79083 | 0.70765 | 0.6573 | 0.65021 | 0.6856
43602.6341 | 0.91456 | 1.0063 | 0.94243 | 0.7918 | 0.70775 | 0.65758 | 0.64943 | 0.6855
43602.6341 | 0.91906 | 1.0066 | 0.94341 | 0.79259 | 0.70731 | 0.65707 | 0.65093 | 0.68535
43602.6341 | 0.90031 | 0.99953 | 0.93849 | 0.78903 | 0.70871 | 0.65836 | 0.65189 | 0.68601
43602.6343 | 0.89847 | 0.99996 | 0.93797 | 0.78885 | 0.70727 | 0.65698 | 0.65107 | 0.68531
43602.6343 | 0.90774 | 1.0036 | 0.94001 | 0.79027 | 0.70488 | 0.65543 | 0.64956 | 0.68502
43602.6342 | 0.91472 | 1.0163 | 0.95049 | 0.79775 | 0.71487 | 0.66268 | 0.65529 | 0.68692
43602.6344 | 0.9379 | 1.0313 | 0.96145 | 0.80546 | 0.7177 | 0.6656 | 0.6577 | 0.68785
43602.6344 | 0.9154 | 1.0212 | 0.95634 | 0.80177 | 0.72087 | 0.66767 | 0.65972 | 0.68901
43602.6344 | 0.89647 | 1.0117 | 0.94811 | 0.79757 | 0.71335 | 0.66261 | 0.65617 | 0.68929
43602.6346 | 0.86962 | 0.99368 | 0.93707 | 0.78952 | 0.70825 | 0.65892 | 0.6548 | 0.69014
43602.6346 | 0.87212 | 0.9941 | 0.93732 | 0.79021 | 0.70615 | 0.65812 | 0.65322 | 0.69024
43602.6346 | 0.84996 | 0.9825 | 0.93011 | 0.78497 | 0.70248 | 0.65542 | 0.651 | 0.69019
43602.6348 | 0.84097 | 0.97448 | 0.92434 | 0.7814 | 0.69982 | 0.65326 | 0.64848 | 0.69014
43602.6348 | 0.84803 | 0.97556 | 0.92435 | 0.78121 | 0.69914 | 0.65252 | 0.6473 | 0.69003
43602.6347 | 0.84872 | 0.97303 | 0.92176 | 0.77931 | 0.69656 | 0.65026 | 0.64852 | 0.68853
43602.6349 | 0.86209 | 0.97557 | 0.92057 | 0.77845 | 0.69607 | 0.64907 | 0.64509 | 0.68715
43602.6349 | 0.86679 | 0.97591 | 0.92076 | 0.77864 | 0.69566 | 0.64898 | 0.6446 | 0.68682
43602.6349 | 0.87479 | 0.97863 | 0.92286 | 0.77981 | 0.6971 | 0.64984 | 0.64359 | 0.68655
43602.6351 | 0.90269 | 0.99524 | 0.9338 | 0.78664 | 0.70169 | 0.653 | 0.646 | 0.68519
43602.6351 | 0.8844 | 0.98701 | 0.92898 | 0.78279 | 0.70204 | 0.65302 | 0.64573 | 0.68489
43602.6351 | 0.92759 | 1.0154 | 0.94912 | 0.79795 | 0.71296 | 0.66166 | 0.65412 | 0.68716
43602.6353 | 0.90709 | 1.0045 | 0.94186 | 0.79285 | 0.70806 | 0.65868 | 0.65189 | 0.68784
43602.6353 | 0.90992 | 1.0045 | 0.94232 | 0.79356 | 0.71141 | 0.66115 | 0.65504 | 0.68887
43602.6352 | 0.86389 | 0.98785 | 0.93252 | 0.78717 | 0.70483 | 0.65752 | 0.65267 | 0.69002
43602.6354 | 0.86625 | 0.98273 | 0.92805 | 0.78568 | 0.70443 | 0.65802 | 0.65406 | 0.69285
43602.6354 | 0.87069 | 0.98495 | 0.92929 | 0.78663 | 0.70556 | 0.65856 | 0.65333 | 0.69325
43602.6354 | 0.83398 | 0.97133 | 0.92331 | 0.78277 | 0.70215 | 0.65666 | 0.65262 | 0.69349
43602.6356 | 0.84105 | 0.96772 | 0.91813 | 0.77912 | 0.69948 | 0.65466 | 0.64984 | 0.69306
43602.6356 | 0.83922 | 0.96594 | 0.91799 | 0.77907 | 0.69877 | 0.65406 | 0.65046 | 0.6928
43602.6356 | 0.82875 | 0.9634 | 0.9164 | 0.77725 | 0.69791 | 0.653 | 0.64933 | 0.69231
43602.6358 | 0.85124 | 0.9746 | 0.92328 | 0.78199 | 0.69898 | 0.65333 | 0.64852 | 0.69156
43602.6358 | 0.84438 | 0.97439 | 0.92407 | 0.78247 | 0.69973 | 0.65339 | 0.64943 | 0.69122
43602.6358 | 0.85145 | 0.97647 | 0.92553 | 0.7835 | 0.70107 | 0.65447 | 0.6509 | 0.69128
43602.6359 | 0.87953 | 0.98936 | 0.93367 | 0.78873 | 0.70693 | 0.6577 | 0.65352 | 0.69118
43602.6359 | 0.88236 | 0.98714 | 0.93163 | 0.78712 | 0.70461 | 0.6567 | 0.65147 | 0.69054
43602.6359 | 0.87793 | 0.98613 | 0.93143 | 0.78689 | 0.70471 | 0.65703 | 0.6531 | 0.69088
43602.6361 | 0.86723 | 0.98443 | 0.92966 | 0.78667 | 0.70671 | 0.65909 | 0.65466 | 0.69237
43602.6361 | 0.85013 | 0.97918 | 0.92707 | 0.78431 | 0.70357 | 0.65708 | 0.65252 | 0.69179
43602.6361 | 0.87358 | 0.98211 | 0.92632 | 0.78516 | 0.70336 | 0.6572 | 0.6521 | 0.69301
43602.6363 | 0.86133 | 0.97273 | 0.92029 | 0.78154 | 0.70097 | 0.65562 | 0.6518 | 0.69355
43602.6363 | 0.84476 | 0.97 | 0.91948 | 0.78045 | 0.70098 | 0.65545 | 0.65124 | 0.69333
43602.6363 | 0.83318 | 0.96626 | 0.91811 | 0.77946 | 0.69918 | 0.65467 | 0.65043 | 0.69332
43602.6364 | 0.84921 | 0.96278 | 0.91174 | 0.77566 | 0.69653 | 0.65242 | 0.64931 | 0.69319
43602.6364 | 0.83337 | 0.95923 | 0.91041 | 0.77532 | 0.69558 | 0.65208 | 0.64806 | 0.69276
43602.6364 | 0.83279 | 0.95707 | 0.9089 | 0.77411 | 0.69451 | 0.65099 | 0.65039 | 0.69256
43602.6366 | 0.84638 | 0.96343 | 0.91265 | 0.77682 | 0.69643 | 0.65191 | 0.65154 | 0.69232
43602.6366 | 0.84976 | 0.96518 | 0.91288 | 0.77792 | 0.69777 | 0.65286 | 0.64898 | 0.69293
43602.6366 | 0.86414 | 0.96628 | 0.91428 | 0.77837 | 0.69868 | 0.65349 | 0.65197 | 0.6931
43602.6368 | 0.86437 | 0.9661 | 0.91436 | 0.77804 | 0.69859 | 0.65382 | 0.64857 | 0.69297
43602.6368 | 0.85645 | 0.96652 | 0.91391 | 0.77778 | 0.69938 | 0.65452 | 0.65297 | 0.69335
43602.6368 | 0.86099 | 0.96704 | 0.91444 | 0.77857 | 0.69951 | 0.65445 | 0.65305 | 0.69286
43602.6369 | 0.86435 | 0.96758 | 0.91577 | 0.7789 | 0.70031 | 0.65524 | 0.65571 | 0.69346
43602.637 | 0.85384 | 0.96682 | 0.91601 | 0.77912 | 0.69958 | 0.65469 | 0.65212 | 0.69322
43602.6369 | 0.87637 | 0.974 | 0.92052 | 0.78218 | 0.70256 | 0.65662 | 0.65179 | 0.69371
43602.6371 | 0.85964 | 0.97622 | 0.92444 | 0.78398 | 0.70559 | 0.65892 | 0.65465 | 0.69436
43602.6371 | 0.85236 | 0.97289 | 0.92181 | 0.7824 | 0.70342 | 0.65754 | 0.65575 | 0.69383
43602.6371 | 0.85679 | 0.97494 | 0.92412 | 0.78436 | 0.70336 | 0.65804 | 0.65526 | 0.69452
43602.6373 | 0.86017 | 0.97429 | 0.92403 | 0.78423 | 0.7057 | 0.65974 | 0.65475 | 0.69561
43602.6373 | 0.84985 | 0.97211 | 0.92353 | 0.78338 | 0.70346 | 0.65851 | 0.65356 | 0.69515
43602.6373 | 0.83758 | 0.97056 | 0.92301 | 0.78368 | 0.70325 | 0.65896 | 0.65522 | 0.69596
43602.6375 | 0.84421 | 0.97441 | 0.92636 | 0.78621 | 0.70451 | 0.65932 | 0.65539 | 0.69614
43602.6375 | 0.8527 | 0.97736 | 0.92695 | 0.78712 | 0.70604 | 0.66024 | 0.65629 | 0.69652
43602.6374 | 0.83253 | 0.96962 | 0.9244 | 0.78445 | 0.70494 | 0.65994 | 0.65584 | 0.69635
43602.6376 | 0.82353 | 0.96554 | 0.92119 | 0.7833 | 0.70305 | 0.65877 | 0.6546 | 0.69656
43602.6376 | 0.82368 | 0.96457 | 0.92131 | 0.78325 | 0.70247 | 0.65843 | 0.65455 | 0.69641
43602.6376 | 0.81925 | 0.95959 | 0.91646 | 0.77978 | 0.70094 | 0.65728 | 0.6528 | 0.69642
43602.6378 | 0.81439 | 0.95492 | 0.91318 | 0.77738 | 0.69986 | 0.65652 | 0.65347 | 0.69632
43602.6378 | 0.8204 | 0.95674 | 0.91375 | 0.7782 | 0.69952 | 0.65631 | 0.65395 | 0.69628
43602.6378 | 0.82164 | 0.95995 | 0.91483 | 0.77915 | 0.69934 | 0.65599 | 0.65423 | 0.69609
43602.638 | 0.81756 | 0.95771 | 0.91346 | 0.77767 | 0.69918 | 0.65611 | 0.65293 | 0.696
43602.638 | 0.83106 | 0.95982 | 0.91296 | 0.77794 | 0.69856 | 0.65536 | 0.65217 | 0.69582
43602.6379 | 0.81314 | 0.95322 | 0.91042 | 0.77505 | 0.69614 | 0.65348 | 0.64996 | 0.69497
43602.6381 | 0.81124 | 0.95545 | 0.91147 | 0.77551 | 0.6958 | 0.65286 | 0.64885 | 0.6939
43602.6381 | 0.8211 | 0.95803 | 0.91275 | 0.77668 | 0.69661 | 0.6529 | 0.64824 | 0.69399
43602.6381 | 0.82364 | 0.96393 | 0.9185 | 0.77985 | 0.6994 | 0.65451 | 0.64992 | 0.69364
43602.6383 | 0.86509 | 0.97701 | 0.92456 | 0.78445 | 0.70221 | 0.65635 | 0.65204 | 0.69392
43602.6383 | 0.85006 | 0.97624 | 0.92551 | 0.7841 | 0.70316 | 0.65671 | 0.65219 | 0.69381
43602.6383 | 0.88168 | 0.9866 | 0.93039 | 0.7889 | 0.70736 | 0.65997 | 0.65532 | 0.69437
43602.6385 | 0.8915 | 0.99162 | 0.93383 | 0.79027 | 0.70934 | 0.66168 | 0.65772 | 0.69459
43602.6385 | 0.89757 | 0.99406 | 0.93527 | 0.79151 | 0.71122 | 0.66297 | 0.65808 | 0.69495
43602.6385 | 0.8935 | 0.99713 | 0.93814 | 0.79386 | 0.71304 | 0.66449 | 0.65958 | 0.69596
43602.6386 | 0.87392 | 0.98912 | 0.93401 | 0.7924 | 0.71347 | 0.66637 | 0.66189 | 0.69884
43602.6386 | 0.85655 | 0.98356 | 0.9317 | 0.78996 | 0.71234 | 0.66596 | 0.66507 | 0.69872
43602.6386 | 0.8602 | 0.97499 | 0.92385 | 0.78566 | 0.7091 | 0.66497 | 0.66078 | 0.7008
43602.6388 | 0.83311 | 0.95952 | 0.9124 | 0.77839 | 0.70345 | 0.6612 | 0.65747 | 0.70013
43602.6388 | 0.83123 | 0.95941 | 0.91255 | 0.77868 | 0.70315 | 0.66089 | 0.65771 | 0.69996
43602.6388 | 0.82055 | 0.95226 | 0.90609 | 0.77458 | 0.69877 | 0.65742 | 0.65445 | 0.6989
43602.639 | 0.82862 | 0.95597 | 0.90853 | 0.77538 | 0.69792 | 0.65609 | 0.65695 | 0.69716
43602.639 | 0.82296 | 0.95708 | 0.91127 | 0.7771 | 0.69877 | 0.65584 | 0.65329 | 0.69664
43602.639 | 0.82187 | 0.95885 | 0.91265 | 0.77666 | 0.6985 | 0.65514 | 0.65126 | 0.69552
43602.6391 | 0.84689 | 0.96619 | 0.91746 | 0.78026 | 0.70006 | 0.65565 | 0.65228 | 0.69509
43602.6391 | 0.83478 | 0.96504 | 0.91733 | 0.77943 | 0.70007 | 0.65559 | 0.65046 | 0.69475
43602.6391 | 0.85969 | 0.97084 | 0.91939 | 0.7808 | 0.70052 | 0.65609 | 0.65741 | 0.69429
43602.6393 | 0.86044 | 0.97197 | 0.91863 | 0.77967 | 0.69932 | 0.65482 | 0.65136 | 0.69273
43602.6393 | 0.88897 | 0.98018 | 0.92261 | 0.78327 | 0.70349 | 0.65774 | 0.65504 | 0.69437
43602.6393 | 0.90199 | 0.98655 | 0.92596 | 0.78464 | 0.70381 | 0.65746 | 0.65253 | 0.69165
43602.6395 | 0.92614 | 1.0001 | 0.93659 | 0.79224 | 0.71328 | 0.66437 | 0.65825 | 0.69184
43602.6395 | 0.90086 | 0.98304 | 0.92486 | 0.7821 | 0.70652 | 0.65907 | 0.65367 | 0.69028
43602.6395 | 0.93924 | 1.001 | 0.93705 | 0.79169 | 0.71281 | 0.66431 | 0.65769 | 0.69143
43602.6396 | 0.93903 | 1.0029 | 0.93739 | 0.79243 | 0.71406 | 0.66579 | 0.6598 | 0.69261
43602.6397 | 0.91725 | 0.99572 | 0.9342 | 0.78926 | 0.71185 | 0.66427 | 0.65719 | 0.69169
43602.6396 | 0.94865 | 1.0119 | 0.94418 | 0.79821 | 0.72043 | 0.67034 | 0.6633 | 0.69385
43602.6398 | 0.92975 | 0.99804 | 0.93467 | 0.79112 | 0.71043 | 0.66345 | 0.66282 | 0.69309
43602.6398 | 0.93035 | 0.99144 | 0.93126 | 0.78772 | 0.71044 | 0.66356 | 0.65849 | 0.69295
43602.6398 | 0.93698 | 1.0069 | 0.94124 | 0.79674 | 0.71706 | 0.66848 | 0.6633 | 0.69439
43602.64 | 0.93632 | 1.0023 | 0.93927 | 0.79457 | 0.72225 | 0.67267 | 0.66895 | 0.69558
43602.64 | 0.93742 | 1.0019 | 0.93792 | 0.79364 | 0.71394 | 0.66642 | 0.66004 | 0.69395
43602.64 | 0.93118 | 0.99863 | 0.93766 | 0.79441 | 0.71376 | 0.66666 | 0.66064 | 0.69543
43602.6401 | 0.89621 | 0.97861 | 0.92265 | 0.78373 | 0.70741 | 0.66178 | 0.65665 | 0.69529
43602.6402 | 0.89699 | 0.98511 | 0.9264 | 0.78732 | 0.71005 | 0.6641 | 0.65946 | 0.69633
43602.6401 | 0.90301 | 0.97444 | 0.91951 | 0.78206 | 0.70966 | 0.66373 | 0.65869 | 0.69676
43602.6403 | 0.90051 | 0.97289 | 0.91736 | 0.78152 | 0.70572 | 0.6608 | 0.65713 | 0.69619
43602.6403 | 0.9108 | 0.98119 | 0.92242 | 0.78571 | 0.70751 | 0.66171 | 0.65782 | 0.69627
43602.6403 | 0.89141 | 0.96791 | 0.91391 | 0.77813 | 0.7049 | 0.65983 | 0.65622 | 0.69554
43602.6405 | 0.90331 | 0.973 | 0.91721 | 0.78171 | 0.70584 | 0.66088 | 0.6569 | 0.69542
43602.6405 | 0.9079 | 0.97183 | 0.91665 | 0.78075 | 0.70556 | 0.66062 | 0.65621 | 0.69503
43602.6405 | 0.91294 | 0.9721 | 0.91667 | 0.781 | 0.70625 | 0.66117 | 0.65668 | 0.6947
43602.6407 | 0.91728 | 0.96576 | 0.91114 | 0.77635 | 0.701 | 0.65765 | 0.65411 | 0.69386
43602.6407 | 0.91382 | 0.97019 | 0.91374 | 0.7794 | 0.70404 | 0.65992 | 0.65563 | 0.69484
43602.6406 | 0.8975 | 0.96231 | 0.90909 | 0.77585 | 0.70212 | 0.65872 | 0.65465 | 0.69525
43602.6408 | 0.89826 | 0.9565 | 0.90376 | 0.77366 | 0.69709 | 0.65525 | 0.65224 | 0.69529
43602.6408 | 0.90487 | 0.95719 | 0.90448 | 0.77432 | 0.70112 | 0.65792 | 0.65394 | 0.69631
43602.6408 | 0.8878 | 0.95229 | 0.89916 | 0.77199 | 0.6973 | 0.65523 | 0.6566 | 0.69564
43602.641 | 0.88372 | 0.945 | 0.89334 | 0.76733 | 0.69299 | 0.65185 | 0.64972 | 0.69484
43602.641 | 0.88735 | 0.94722 | 0.89522 | 0.76862 | 0.69572 | 0.65393 | 0.65093 | 0.69528
43602.641 | 0.89025 | 0.9409 | 0.88923 | 0.76396 | 0.69251 | 0.65139 | 0.6482 | 0.69402
43602.6412 | 0.89018 | 0.94249 | 0.88997 | 0.7645 | 0.69059 | 0.65035 | 0.64725 | 0.69287
43602.6412 | 0.89263 | 0.94379 | 0.89084 | 0.76509 | 0.69325 | 0.65194 | 0.65076 | 0.69266
43602.6412 | 0.90154 | 0.94013 | 0.88722 | 0.76246 | 0.69097 | 0.64997 | 0.6472 | 0.69213
43602.6413 | 0.89306 | 0.93907 | 0.88616 | 0.76265 | 0.69341 | 0.65206 | 0.65448 | 0.69269
43602.6413 | 0.89419 | 0.93512 | 0.88341 | 0.75986 | 0.68864 | 0.64844 | 0.64644 | 0.69122
43602.6413 | 0.87947 | 0.92934 | 0.87869 | 0.75579 | 0.68808 | 0.64824 | 0.64782 | 0.69176
43602.6415 | 0.87827 | 0.92857 | 0.87703 | 0.75616 | 0.68562 | 0.64681 | 0.6454 | 0.69198
43602.6415 | 0.88536 | 0.92704 | 0.87643 | 0.75552 | 0.68786 | 0.64851 | 0.64514 | 0.6922
43602.6415 | 0.87544 | 0.92449 | 0.87433 | 0.75495 | 0.68598 | 0.647 | 0.64498 | 0.69226
43602.6417 | 0.87405 | 0.92124 | 0.87138 | 0.75221 | 0.68468 | 0.64619 | 0.64498 | 0.69198
43602.6417 | 0.88234 | 0.92513 | 0.87409 | 0.7553 | 0.68457 | 0.64636 | 0.64406 | 0.69225
43602.6417 | 0.88847 | 0.92957 | 0.87856 | 0.75774 | 0.68769 | 0.64855 | 0.64674 | 0.69241
43602.6418 | 0.89702 | 0.92949 | 0.87891 | 0.75788 | 0.68738 | 0.6483 | 0.64601 | 0.69303
43602.6419 | 0.88472 | 0.92639 | 0.87683 | 0.75629 | 0.68798 | 0.64882 | 0.64657 | 0.69312
43602.6418 | 0.8687 | 0.92158 | 0.87389 | 0.7545 | 0.68633 | 0.6479 | 0.64624 | 0.69435
43602.642 | 0.84529 | 0.91948 | 0.8714 | 0.7535 | 0.68523 | 0.64767 | 0.64694 | 0.6954
43602.642 | 0.86533 | 0.92098 | 0.87224 | 0.75579 | 0.68663 | 0.64882 | 0.64776 | 0.69615
43602.642 | 0.84743 | 0.91435 | 0.86756 | 0.75319 | 0.68358 | 0.64683 | 0.64704 | 0.6962
43602.6422 | 0.81137 | 0.91741 | 0.86699 | 0.75272 | 0.68319 | 0.64574 | 0.64487 | 0.69557
43602.6422 | 0.82657 | 0.91592 | 0.86669 | 0.75272 | 0.68292 | 0.64607 | 0.64546 | 0.69575
43602.6422 | 0.81536 | 0.91979 | 0.86932 | 0.75554 | 0.68419 | 0.64629 | 0.64498 | 0.6951
43602.6424 | 0.80698 | 0.91729 | 0.8678 | 0.75433 | 0.68394 | 0.64599 | 0.64404 | 0.69526
43602.6424 | 0.80785 | 0.91787 | 0.8676 | 0.75405 | 0.6833 | 0.64613 | 0.64931 | 0.69548
43602.6423 | 0.81548 | 0.91254 | 0.86334 | 0.75005 | 0.68181 | 0.64537 | 0.64549 | 0.69569
43602.6425 | 0.80944 | 0.91312 | 0.86431 | 0.75242 | 0.68164 | 0.64495 | 0.64469 | 0.69549
43602.6425 | 0.80785 | 0.9155 | 0.8662 | 0.75387 | 0.68234 | 0.6449 | 0.64479 | 0.69517
43602.6425 | 0.80646 | 0.91689 | 0.86764 | 0.75362 | 0.68173 | 0.64502 | 0.64422 | 0.69509
43602.6427 | 0.83084 | 0.92517 | 0.87496 | 0.75964 | 0.68625 | 0.64747 | 0.64576 | 0.69513
43602.6427 | 0.81689 | 0.926 | 0.87542 | 0.75891 | 0.68678 | 0.64796 | 0.64618 | 0.69543
43602.6427 | 0.83378 | 0.93156 | 0.88063 | 0.76265 | 0.68913 | 0.65057 | 0.64862 | 0.69694
43602.6429 | 0.83257 | 0.93427 | 0.88247 | 0.7647 | 0.69108 | 0.65251 | 0.64996 | 0.69792
43602.6429 | 0.8313 | 0.93588 | 0.88451 | 0.76587 | 0.69229 | 0.65317 | 0.65069 | 0.69812
43602.6429 | 0.8219 | 0.92499 | 0.87681 | 0.7591 | 0.6898 | 0.65248 | 0.65032 | 0.69911
43602.643 | 0.81858 | 0.92514 | 0.87549 | 0.7603 | 0.69034 | 0.65253 | 0.65069 | 0.69956
43602.6431 | 0.81188 | 0.92454 | 0.8753 | 0.76015 | 0.68979 | 0.65229 | 0.65104 | 0.69935
43602.643 | 0.81606 | 0.92006 | 0.87098 | 0.75731 | 0.68817 | 0.65142 | 0.6509 | 0.69945
43602.6432 | 0.81259 | 0.91686 | 0.86752 | 0.75615 | 0.6875 | 0.65053 | 0.65259 | 0.69943
43602.6432 | 0.80961 | 0.91447 | 0.86654 | 0.75557 | 0.68695 | 0.65067 | 0.65151 | 0.69978
43602.6432 | 0.80809 | 0.91317 | 0.86559 | 0.75578 | 0.68666 | 0.64999 | 0.64904 | 0.69958
43602.6434 | 0.80964 | 0.91306 | 0.86467 | 0.75579 | 0.68618 | 0.64985 | 0.65276 | 0.69966
43602.6434 | 0.80484 | 0.91354 | 0.86452 | 0.7551 | 0.68659 | 0.64969 | 0.65062 | 0.69946
43602.6434 | 0.80307 | 0.91104 | 0.86262 | 0.75394 | 0.68546 | 0.64947 | 0.65001 | 0.69951
43602.6436 | 0.80286 | 0.91124 | 0.86332 | 0.75423 | 0.68495 | 0.64906 | 0.65009 | 0.6993
43602.6436 | 0.80622 | 0.91151 | 0.86348 | 0.7537 | 0.68496 | 0.64876 | 0.64902 | 0.69909
43602.6435 | 0.81066 | 0.91367 | 0.86565 | 0.75467 | 0.68512 | 0.64855 | 0.64795 | 0.69848
43602.6437 | 0.80875 | 0.9153 | 0.86687 | 0.75515 | 0.68526 | 0.64847 | 0.64778 | 0.69803
43602.6437 | 0.80737 | 0.91618 | 0.86712 | 0.75517 | 0.68529 | 0.64872 | 0.64826 | 0.69794
43602.6437 | 0.80817 | 0.91948 | 0.87096 | 0.75729 | 0.68619 | 0.64953 | 0.64666 | 0.69807
43602.6439 | 0.82608 | 0.92348 | 0.87452 | 0.75978 | 0.6888 | 0.65042 | 0.6491 | 0.69801
43602.6439 | 0.81969 | 0.92389 | 0.87423 | 0.76015 | 0.68906 | 0.6505 | 0.64972 | 0.69806
43602.6439 | 0.82448 | 0.9308 | 0.88055 | 0.7636 | 0.69232 | 0.65288 | 0.65112 | 0.69905
43602.6441 | 0.84123 | 0.93766 | 0.88695 | 0.76889 | 0.6954 | 0.65551 | 0.65333 | 0.69958
43602.6441 | 0.85487 | 0.93993 | 0.88856 | 0.77027 | 0.69712 | 0.65631 | 0.65756 | 0.69994
43602.6441 | 0.83621 | 0.93362 | 0.88526 | 0.76644 | 0.69614 | 0.65771 | 0.65717 | 0.70193
43602.6442 | 0.83119 | 0.9322 | 0.88296 | 0.76511 | 0.69651 | 0.65792 | 0.65677 | 0.70238
43602.6443 | 0.82523 | 0.92988 | 0.8811 | 0.76391 | 0.69547 | 0.6577 | 0.65576 | 0.7026
43602.6442 | 0.81689 | 0.92534 | 0.87753 | 0.763 | 0.69446 | 0.6576 | 0.65759 | 0.70316
43602.6444 | 0.81245 | 0.91932 | 0.8716 | 0.75876 | 0.69103 | 0.65503 | 0.65409 | 0.70254
43602.6444 | 0.81698 | 0.9191 | 0.87079 | 0.75757 | 0.69074 | 0.65495 | 0.65337 | 0.70249
43602.6444 | 0.81855 | 0.91259 | 0.8653 | 0.75319 | 0.68691 | 0.652 | 0.6512 | 0.70105
43602.6446 | 0.80449 | 0.91352 | 0.8665 | 0.75496 | 0.68494 | 0.64896 | 0.65127 | 0.69875
43602.6446 | 0.80509 | 0.91574 | 0.86718 | 0.75498 | 0.68477 | 0.64886 | 0.64812 | 0.69864
43602.6446 | 0.80649 | 0.91822 | 0.87004 | 0.75649 | 0.68517 | 0.64819 | 0.64731 | 0.69738
43602.6448 | 0.80369 | 0.92336 | 0.87629 | 0.76022 | 0.68667 | 0.64895 | 0.64744 | 0.69682
43602.6448 | 0.81202 | 0.92617 | 0.87836 | 0.7609 | 0.68752 | 0.64922 | 0.6471 | 0.69654
43602.6447 | 0.81741 | 0.92918 | 0.88075 | 0.76211 | 0.6889 | 0.64977 | 0.64866 | 0.69645
43602.6449 | 0.8434 | 0.93843 | 0.88811 | 0.76665 | 0.6924 | 0.65221 | 0.65355 | 0.69656
43602.6449 | 0.87234 | 0.94219 | 0.88936 | 0.76879 | 0.69442 | 0.65295 | 0.65121 | 0.69702
43602.6449 | 0.8617 | 0.94249 | 0.89184 | 0.76862 | 0.69657 | 0.65553 | 0.65413 | 0.69813
43602.6451 | 0.89256 | 0.94332 | 0.89398 | 0.76914 | 0.69972 | 0.65814 | 0.66041 | 0.69919
43602.6451 | 0.89353 | 0.94216 | 0.8932 | 0.76889 | 0.69781 | 0.65699 | 0.65582 | 0.69879
43602.6451 | 0.87345 | 0.9407 | 0.8909 | 0.76882 | 0.6978 | 0.65794 | 0.65692 | 0.70034
43602.6453 | 0.86012 | 0.93815 | 0.88874 | 0.76742 | 0.69886 | 0.65856 | 0.65992 | 0.70111
43602.6453 | 0.86354 | 0.93771 | 0.88822 | 0.76738 | 0.69755 | 0.65828 | 0.65785 | 0.70158
43602.6453 | 0.86708 | 0.94368 | 0.89353 | 0.77245 | 0.70172 | 0.6609 | 0.65941 | 0.70278
43602.6454 | 0.86071 | 0.94393 | 0.89449 | 0.77344 | 0.70252 | 0.66238 | 0.66068 | 0.70393
43602.6454 | 0.85987 | 0.94413 | 0.8951 | 0.77305 | 0.70277 | 0.6624 | 0.66056 | 0.70413
43602.6454 | 0.845 | 0.94212 | 0.8934 | 0.77189 | 0.70218 | 0.663 | 0.66114 | 0.70465
43602.6456 | 0.83754 | 0.93624 | 0.88811 | 0.7691 | 0.70061 | 0.66188 | 0.6599 | 0.70495
43602.6456 | 0.83444 | 0.93373 | 0.88652 | 0.76721 | 0.6996 | 0.66164 | 0.66143 | 0.70498
43602.6456 | 0.82713 | 0.92708 | 0.87948 | 0.76366 | 0.69648 | 0.65942 | 0.65909 | 0.70473
43602.6458 | 0.81824 | 0.92226 | 0.87453 | 0.76113 | 0.69348 | 0.65707 | 0.65685 | 0.70434
43602.6458 | 0.8151 | 0.92046 | 0.8733 | 0.76081 | 0.69292 | 0.65713 | 0.65675 | 0.70435
43602.6458 | 0.81213 | 0.91586 | 0.8686 | 0.75717 | 0.69039 | 0.65503 | 0.65547 | 0.70361
43602.646 | 0.80832 | 0.91174 | 0.86456 | 0.75396 | 0.68737 | 0.65192 | 0.6543 | 0.70215
43602.646 | 0.80203 | 0.90894 | 0.86331 | 0.75253 | 0.68652 | 0.65177 | 0.65369 | 0.7022
43602.646 | 0.80496 | 0.91256 | 0.86405 | 0.75211 | 0.68432 | 0.64946 | 0.64868 | 0.69981
43602.6461 | 0.80284 | 0.92286 | 0.87596 | 0.75975 | 0.68655 | 0.64918 | 0.64868 | 0.69782
43602.6462 | 0.79853 | 0.92288 | 0.87712 | 0.76039 | 0.68721 | 0.64938 | 0.6477 | 0.69755
43602.6461 | 0.81718 | 0.93943 | 0.89289 | 0.76918 | 0.69316 | 0.65267 | 0.65114 | 0.69707
43602.6463 | 0.83852 | 0.95426 | 0.90747 | 0.77755 | 0.69941 | 0.65666 | 0.6579 | 0.69768
43602.6463 | 0.83303 | 0.95449 | 0.90865 | 0.77821 | 0.70041 | 0.65755 | 0.65443 | 0.698
43602.6463 | 0.854 | 0.96288 | 0.91359 | 0.78227 | 0.70376 | 0.66077 | 0.65739 | 0.6995
43602.6465 | 0.84352 | 0.95642 | 0.91006 | 0.77922 | 0.70349 | 0.66088 | 0.65751 | 0.70025
43602.6465 | 0.8334 | 0.95252 | 0.90748 | 0.77745 | 0.70192 | 0.66047 | 0.65706 | 0.70028
43602.6465 | 0.83096 | 0.9515 | 0.90533 | 0.77716 | 0.70184 | 0.66051 | 0.65804 | 0.70075
43602.6467 | 0.85199 | 0.95638 | 0.90682 | 0.77981 | 0.70373 | 0.66148 | 0.65857 | 0.70126
43602.6467 | 0.83879 | 0.95121 | 0.9044 | 0.77689 | 0.70265 | 0.66072 | 0.65778 | 0.70067
43602.6466 | 0.83022 | 0.94905 | 0.90323 | 0.77708 | 0.70094 | 0.66031 | 0.65803 | 0.70133
43602.6468 | 0.84773 | 0.95632 | 0.90777 | 0.77988 | 0.70409 | 0.66173 | 0.65786 | 0.7017
43602.6468 | 0.84996 | 0.95644 | 0.90892 | 0.78034 | 0.70431 | 0.66214 | 0.65865 | 0.7017
43602.6468 | 0.85739 | 0.95974 | 0.91139 | 0.78297 | 0.70557 | 0.66305 | 0.66044 | 0.70214
43602.647 | 0.83799 | 0.95665 | 0.90986 | 0.78158 | 0.70729 | 0.66521 | 0.66167 | 0.70325
43602.647 | 0.83457 | 0.95361 | 0.9087 | 0.78037 | 0.70546 | 0.66476 | 0.66218 | 0.70337
43602.647 | 0.84871 | 0.95903 | 0.91033 | 0.78348 | 0.70761 | 0.66593 | 0.66193 | 0.70415
43602.6472 | 0.84846 | 0.95258 | 0.9053 | 0.77843 | 0.70542 | 0.66468 | 0.662 | 0.70411
43602.6472 | 0.83482 | 0.95104 | 0.90438 | 0.77855 | 0.70495 | 0.66412 | 0.66249 | 0.70402
43602.6472 | 0.83046 | 0.95193 | 0.90492 | 0.77955 | 0.70498 | 0.66363 | 0.66202 | 0.70386
43602.6474 | 0.83604 | 0.95452 | 0.90666 | 0.78069 | 0.70586 | 0.66408 | 0.66155 | 0.70395
43602.6474 | 0.84425 | 0.95578 | 0.90665 | 0.78088 | 0.70622 | 0.6641 | 0.66172 | 0.70398
43602.6474 | 0.84532 | 0.95956 | 0.90987 | 0.78326 | 0.7078 | 0.66511 | 0.66226 | 0.70399
43602.6476 | 0.85784 | 0.96171 | 0.91135 | 0.78381 | 0.70879 | 0.66613 | 0.66347 | 0.70452
43602.6476 | 0.87117 | 0.96511 | 0.91277 | 0.78525 | 0.70933 | 0.66652 | 0.66315 | 0.70468
43602.6476 | 0.88507 | 0.96994 | 0.91654 | 0.78826 | 0.71317 | 0.66851 | 0.66614 | 0.70565
43602.6478 | 0.8733 | 0.96567 | 0.91436 | 0.78585 | 0.71186 | 0.66832 | 0.66515 | 0.70611
43602.6478 | 0.87837 | 0.96907 | 0.91568 | 0.78781 | 0.71314 | 0.66947 | 0.66663 | 0.70684
43602.6477 | 0.88022 | 0.96337 | 0.9126 | 0.78536 | 0.71106 | 0.66827 | 0.66972 | 0.70719
43602.6479 | 0.85429 | 0.96044 | 0.91041 | 0.78336 | 0.71129 | 0.66892 | 0.66831 | 0.70793
43602.6479 | 0.87358 | 0.96234 | 0.91107 | 0.78463 | 0.71136 | 0.66843 | 0.66651 | 0.70807
43602.6479 | 0.86061 | 0.96686 | 0.91521 | 0.78771 | 0.71358 | 0.66996 | 0.66749 | 0.70853
43602.6481 | 0.86608 | 0.96649 | 0.91483 | 0.78776 | 0.7148 | 0.67121 | 0.66807 | 0.70921
43602.6481 | 0.86079 | 0.96584 | 0.91442 | 0.78745 | 0.71458 | 0.6706 | 0.66699 | 0.70916
43602.6481 | 0.86033 | 0.96463 | 0.91467 | 0.78679 | 0.71391 | 0.67077 | 0.66687 | 0.70974
43602.6483 | 0.863 | 0.97037 | 0.91906 | 0.79038 | 0.71684 | 0.67268 | 0.67225 | 0.71051
43602.6483 | 0.85578 | 0.96964 | 0.91827 | 0.78977 | 0.71674 | 0.6729 | 0.67053 | 0.71089
43602.6483 | 0.86749 | 0.97067 | 0.91926 | 0.79113 | 0.71688 | 0.67269 | 0.67011 | 0.71105
43602.6485 | 0.86065 | 0.96779 | 0.9183 | 0.78927 | 0.71612 | 0.67263 | 0.67005 | 0.71151
43602.6485 | 0.85708 | 0.97131 | 0.92004 | 0.79136 | 0.71747 | 0.67332 | 0.67032 | 0.71164
43602.6485 | 0.85787 | 0.96607 | 0.91762 | 0.78829 | 0.71621 | 0.67293 | 0.6707 | 0.7119
43602.6486 | 0.85369 | 0.96543 | 0.9157 | 0.78713 | 0.71649 | 0.67281 | 0.6701 | 0.71209
43602.6486 | 0.84472 | 0.96166 | 0.91362 | 0.78611 | 0.7149 | 0.67198 | 0.66953 | 0.71204
43602.6486 | 0.84668 | 0.96061 | 0.91146 | 0.78417 | 0.71417 | 0.67122 | 0.66819 | 0.7122
43602.6488 | 0.83436 | 0.95468 | 0.90734 | 0.78198 | 0.71174 | 0.66939 | 0.66663 | 0.7118
43602.6488 | 0.83802 | 0.95468 | 0.90735 | 0.78188 | 0.71125 | 0.66912 | 0.67092 | 0.71152
43602.6488 | 0.82905 | 0.94843 | 0.90106 | 0.77726 | 0.70792 | 0.66656 | 0.66521 | 0.71104
43602.649 | 0.835 | 0.94586 | 0.89768 | 0.77601 | 0.7065 | 0.66453 | 0.66289 | 0.71019
43602.649 | 0.83218 | 0.94399 | 0.8964 | 0.77483 | 0.706 | 0.66443 | 0.66226 | 0.71038
43602.649 | 0.82452 | 0.94026 | 0.89196 | 0.77186 | 0.70286 | 0.66187 | 0.6631 | 0.70936
43602.6492 | 0.83087 | 0.94354 | 0.89537 | 0.77417 | 0.70262 | 0.66037 | 0.65784 | 0.70788
43602.6492 | 0.82997 | 0.94458 | 0.89593 | 0.77365 | 0.70288 | 0.65996 | 0.66108 | 0.70772
43602.6491 | 0.83947 | 0.95197 | 0.90153 | 0.77648 | 0.70498 | 0.66144 | 0.65893 | 0.70754
43602.6493 | 0.87663 | 0.96694 | 0.9132 | 0.78492 | 0.71101 | 0.6652 | 0.66202 | 0.70864
43602.6493 | 0.89765 | 0.97168 | 0.91532 | 0.7867 | 0.71302 | 0.66666 | 0.66347 | 0.70913
43602.6493 | 0.92803 | 0.97842 | 0.92276 | 0.79014 | 0.7189 | 0.67154 | 0.66773 | 0.71084
43602.6495 | 0.9061 | 0.97154 | 0.91824 | 0.78657 | 0.71844 | 0.6721 | 0.66918 | 0.7118
43602.6495 | 0.8923 | 0.97021 | 0.91738 | 0.7855 | 0.71616 | 0.67085 | 0.67217 | 0.71188
43602.6495 | 0.89217 | 0.96964 | 0.91731 | 0.78823 | 0.71867 | 0.67303 | 0.67141 | 0.71474
43602.6497 | 0.85825 | 0.96208 | 0.91112 | 0.78407 | 0.71554 | 0.67198 | 0.67061 | 0.71598
43602.6497 | 0.85942 | 0.96103 | 0.91082 | 0.78481 | 0.71611 | 0.67223 | 0.67115 | 0.7159
43602.6497 | 0.84932 | 0.95171 | 0.90229 | 0.77808 | 0.71141 | 0.66916 | 0.66667 | 0.71553
43602.6499 | 0.8247 | 0.94633 | 0.89719 | 0.7765 | 0.70783 | 0.66625 | 0.66465 | 0.7143
43602.6499 | 0.83155 | 0.94596 | 0.89684 | 0.77556 | 0.70758 | 0.66571 | 0.66385 | 0.71396
43602.6498 | 0.83596 | 0.94788 | 0.89771 | 0.77562 | 0.70629 | 0.66385 | 0.66202 | 0.71284
43602.65 | 0.83419 | 0.95173 | 0.90238 | 0.77658 | 0.70656 | 0.66361 | 0.66297 | 0.71188
43602.65 | 0.83946 | 0.95277 | 0.90312 | 0.77781 | 0.70744 | 0.66434 | 0.66362 | 0.7122
43602.65 | 0.83305 | 0.95635 | 0.90678 | 0.77956 | 0.70892 | 0.66441 | 0.66201 | 0.7117
43602.6502 | 0.83846 | 0.95909 | 0.90891 | 0.78072 | 0.7094 | 0.66484 | 0.66224 | 0.71199
43602.6502 | 0.83836 | 0.96028 | 0.90903 | 0.78074 | 0.70886 | 0.66449 | 0.66136 | 0.71198
43602.6502 | 0.8538 | 0.96383 | 0.9113 | 0.7817 | 0.71015 | 0.66523 | 0.66251 | 0.71197
43602.6504 | 0.86557 | 0.96595 | 0.9132 | 0.78293 | 0.71124 | 0.66607 | 0.66287 | 0.71205
43602.6504 | 0.8648 | 0.96398 | 0.91272 | 0.78163 | 0.71187 | 0.66639 | 0.66287 | 0.71235
43602.6504 | 0.87022 | 0.97005 | 0.91622 | 0.78364 | 0.71357 | 0.66721 | 0.6637 | 0.71227
43602.6505 | 0.89635 | 0.98 | 0.92289 | 0.78911 | 0.71781 | 0.67061 | 0.66616 | 0.71363
43602.6506 | 0.89847 | 0.97886 | 0.92222 | 0.78815 | 0.7177 | 0.67033 | 0.66604 | 0.71323
43602.6505 | 0.89475 | 0.97667 | 0.9232 | 0.78707 | 0.71693 | 0.66983 | 0.669 | 0.71265
43602.6507 | 0.90428 | 0.98003 | 0.92463 | 0.7882 | 0.7181 | 0.6711 | 0.66875 | 0.71386
43602.6507 | 0.91681 | 0.98261 | 0.92687 | 0.79024 | 0.72044 | 0.67269 | 0.67269 | 0.71527
43602.6507 | 0.91097 | 0.98438 | 0.92749 | 0.79165 | 0.7205 | 0.67301 | 0.67014 | 0.71568
43602.6509 | 0.88298 | 0.97616 | 0.92237 | 0.7877 | 0.71888 | 0.67198 | 0.6683 | 0.716
43602.6509 | 0.90199 | 0.97957 | 0.92372 | 0.78923 | 0.71868 | 0.67206 | 0.67031 | 0.71627
43602.6509 | 0.91907 | 0.99203 | 0.93319 | 0.79655 | 0.72438 | 0.676 | 0.6712 | 0.71759
43602.6511 | 0.9299 | 0.99415 | 0.93641 | 0.79755 | 0.72717 | 0.67831 | 0.67287 | 0.71779
43602.6511 | 0.91582 | 0.99073 | 0.93334 | 0.79467 | 0.72596 | 0.67714 | 0.67557 | 0.7174
43602.6511 | 0.90274 | 0.99413 | 0.93621 | 0.79815 | 0.72838 | 0.67901 | 0.67496 | 0.71932
43602.6512 | 0.89247 | 0.98825 | 0.93169 | 0.79424 | 0.72604 | 0.67754 | 0.67338 | 0.7192
43602.6513 | 0.8847 | 0.98109 | 0.92696 | 0.78977 | 0.72187 | 0.67497 | 0.67499 | 0.71854
43602.6512 | 0.89336 | 0.98614 | 0.92862 | 0.7931 | 0.72176 | 0.67479 | 0.67117 | 0.71932
43602.6514 | 0.88027 | 0.97736 | 0.92289 | 0.78734 | 0.71919 | 0.67299 | 0.66955 | 0.71901
43602.6514 | 0.86593 | 0.97976 | 0.92402 | 0.78945 | 0.71917 | 0.67322 | 0.66995 | 0.71892
43602.6514 | 0.87944 | 0.97962 | 0.9236 | 0.78825 | 0.72002 | 0.67302 | 0.6697 | 0.71855
43602.6516 | 0.87794 | 0.97979 | 0.92357 | 0.78835 | 0.71933 | 0.67256 | 0.66953 | 0.71854
43602.6516 | 0.88752 | 0.9846 | 0.92511 | 0.79082 | 0.72005 | 0.67333 | 0.66933 | 0.71907
43602.6516 | 0.89803 | 0.985 | 0.92525 | 0.79063 | 0.71982 | 0.67321 | 0.6725 | 0.71905
43602.6518 | 0.90213 | 0.98415 | 0.9245 | 0.78944 | 0.71973 | 0.67251 | 0.66953 | 0.71868
43602.6518 | 0.90455 | 0.98831 | 0.92766 | 0.79186 | 0.7206 | 0.67338 | 0.66924 | 0.71894
43602.6518 | 0.89472 | 0.98262 | 0.92332 | 0.78804 | 0.71844 | 0.67201 | 0.6683 | 0.71821
43602.6519 | 0.90909 | 0.97858 | 0.92041 | 0.7861 | 0.7197 | 0.67246 | 0.67164 | 0.71892
43602.652 | 0.87843 | 0.9697 | 0.91575 | 0.78098 | 0.71557 | 0.66967 | 0.66675 | 0.71802
43602.6519 | 0.88347 | 0.97135 | 0.91442 | 0.78169 | 0.71494 | 0.66918 | 0.66609 | 0.71841
43602.6521 | 0.88514 | 0.97231 | 0.91425 | 0.7826 | 0.71688 | 0.67015 | 0.66608 | 0.71877
43602.6521 | 0.90133 | 0.96961 | 0.91266 | 0.78059 | 0.71344 | 0.66852 | 0.66566 | 0.71809
43602.6521 | 0.90662 | 0.9729 | 0.91429 | 0.78308 | 0.7165 | 0.66969 | 0.66861 | 0.71847
43602.6523 | 0.90834 | 0.96633 | 0.90914 | 0.77884 | 0.71224 | 0.66704 | 0.66393 | 0.71774
43602.6523 | 0.90339 | 0.96425 | 0.90814 | 0.77769 | 0.71169 | 0.66626 | 0.66653 | 0.7174
43602.6523 | 0.91423 | 0.96487 | 0.90861 | 0.77755 | 0.71238 | 0.66694 | 0.66279 | 0.71711
43602.6525 | 0.91553 | 0.97057 | 0.91144 | 0.77936 | 0.71286 | 0.66721 | 0.66475 | 0.71655
43602.6525 | 0.91558 | 0.97189 | 0.91254 | 0.78062 | 0.71429 | 0.66836 | 0.6645 | 0.71677
43602.6524 | 0.92617 | 0.98347 | 0.9201 | 0.78587 | 0.71854 | 0.67161 | 0.66589 | 0.71673
43602.6526 | 0.91158 | 0.97106 | 0.91135 | 0.77778 | 0.71316 | 0.66774 | 0.66369 | 0.71579
43602.6526 | 0.9288 | 0.97629 | 0.91529 | 0.78177 | 0.71113 | 0.66636 | 0.66233 | 0.71622
43602.6526 | 0.91816 | 0.9747 | 0.91459 | 0.78079 | 0.71588 | 0.66981 | 0.66502 | 0.7174
43602.6528 | 0.93136 | 0.97679 | 0.91577 | 0.78247 | 0.71432 | 0.66846 | 0.66624 | 0.71748
43602.6528 | 0.92153 | 0.97562 | 0.91604 | 0.78246 | 0.7171 | 0.67079 | 0.66646 | 0.71823
43602.6528 | 0.91182 | 0.97716 | 0.91605 | 0.7828 | 0.7157 | 0.67035 | 0.66836 | 0.71862
43602.653 | 0.91926 | 0.97595 | 0.91612 | 0.78258 | 0.71791 | 0.67134 | 0.66966 | 0.71935
43602.653 | 0.9277 | 0.97961 | 0.91869 | 0.78492 | 0.71691 | 0.67073 | 0.66711 | 0.7191
43602.653 | 0.91814 | 0.97775 | 0.91779 | 0.78459 | 0.71667 | 0.67062 | 0.66888 | 0.72039
43602.6532 | 0.89975 | 0.9727 | 0.91549 | 0.78212 | 0.71571 | 0.66981 | 0.66633 | 0.7205
43602.6532 | 0.88765 | 0.97058 | 0.9135 | 0.7801 | 0.71317 | 0.6683 | 0.66829 | 0.7197
43602.6531 | 0.88002 | 0.96849 | 0.91239 | 0.77926 | 0.7138 | 0.66814 | 0.66476 | 0.7204
43602.6533 | 0.85565 | 0.96501 | 0.90884 | 0.77731 | 0.71032 | 0.66619 | 0.66525 | 0.71982
43602.6533 | 0.8573 | 0.96464 | 0.90894 | 0.77756 | 0.71026 | 0.66633 | 0.66355 | 0.72008
43602.6533 | 0.85595 | 0.96296 | 0.9074 | 0.77669 | 0.70828 | 0.66468 | 0.66155 | 0.71949
43602.6535 | 0.84541 | 0.96192 | 0.90566 | 0.77549 | 0.70656 | 0.6626 | 0.66005 | 0.71868
43602.6535 | 0.85143 | 0.96517 | 0.90731 | 0.77707 | 0.70707 | 0.66259 | 0.65938 | 0.71842
43602.6535 | 0.84249 | 0.96251 | 0.90601 | 0.77484 | 0.70618 | 0.66178 | 0.65894 | 0.71791
43602.6537 | 0.84517 | 0.96557 | 0.90859 | 0.77587 | 0.70637 | 0.66158 | 0.65762 | 0.7174
43602.6537 | 0.84678 | 0.96586 | 0.90894 | 0.77666 | 0.70657 | 0.66186 | 0.66081 | 0.71756
43602.6537 | 0.85755 | 0.97581 | 0.91671 | 0.78095 | 0.71018 | 0.66399 | 0.66121 | 0.71741
43602.6539 | 0.86578 | 0.9832 | 0.92306 | 0.78441 | 0.71236 | 0.66523 | 0.66089 | 0.71778
43602.6539 | 0.88765 | 0.98645 | 0.92389 | 0.78516 | 0.71257 | 0.66563 | 0.66104 | 0.71793
43602.6538 | 0.8642 | 0.98253 | 0.92204 | 0.78418 | 0.71237 | 0.66633 | 0.66558 | 0.71888
43602.654 | 0.84596 | 0.97001 | 0.91405 | 0.77775 | 0.70912 | 0.66368 | 0.65999 | 0.71842
43602.654 | 0.83869 | 0.96731 | 0.91267 | 0.7769 | 0.70702 | 0.66284 | 0.65889 | 0.71816
43602.654 | 0.82971 | 0.96034 | 0.90609 | 0.77229 | 0.70327 | 0.66 | 0.65673 | 0.7176
43602.6542 | 0.81721 | 0.95479 | 0.90111 | 0.76828 | 0.69837 | 0.65576 | 0.65255 | 0.71541
43602.6542 | 0.82566 | 0.95583 | 0.90158 | 0.76834 | 0.69884 | 0.6556 | 0.65225 | 0.71511
43602.6542 | 0.81903 | 0.95286 | 0.89921 | 0.76596 | 0.6961 | 0.65248 | 0.64945 | 0.71326
43602.6545 | 0.83165 | 0.9609 | 0.90506 | 0.76805 | 0.6954 | 0.65115 | 0.64738 | 0.71151
43602.6544 | 0.86936 | 0.97457 | 0.91238 | 0.77342 | 0.69936 | 0.65339 | 0.64899 | 0.71123
43602.6547 | 0.88327 | 0.97848 | 0.91534 | 0.77394 | 0.7027 | 0.65545 | 0.65285 | 0.71078
43602.6546 | 0.88313 | 0.98349 | 0.91743 | 0.77537 | 0.70315 | 0.65554 | 0.65022 | 0.70992
43602.6548 | 0.90053 | 0.98158 | 0.91792 | 0.77386 | 0.70394 | 0.65577 | 0.65034 | 0.70912
43602.6548 | 0.90316 | 0.98488 | 0.91992 | 0.77559 | 0.70217 | 0.6546 | 0.65212 | 0.70888
43602.6548 | 0.90628 | 0.9879 | 0.92189 | 0.77736 | 0.70444 | 0.65655 | 0.65139 | 0.7096
43602.655 | 0.90617 | 0.98929 | 0.92117 | 0.77608 | 0.70161 | 0.65468 | 0.64919 | 0.70866
43602.655 | 0.90568 | 0.99182 | 0.92328 | 0.77821 | 0.70682 | 0.6583 | 0.65264 | 0.71018
43602.655 | 0.89214 | 0.98313 | 0.91733 | 0.77355 | 0.70159 | 0.65444 | 0.64955 | 0.70916
43602.6552 | 0.91621 | 0.99503 | 0.92445 | 0.7794 | 0.70509 | 0.6574 | 0.65206 | 0.71065
43602.6552 | 0.89374 | 0.98761 | 0.92037 | 0.77582 | 0.70412 | 0.6563 | 0.65191 | 0.70994
43602.6552 | 0.90123 | 0.99172 | 0.92289 | 0.77663 | 0.70488 | 0.6572 | 0.65147 | 0.7102
43602.6554 | 0.89403 | 0.99361 | 0.92596 | 0.77929 | 0.70797 | 0.65946 | 0.65482 | 0.71098
43602.6554 | 0.91274 | 0.99743 | 0.92818 | 0.78103 | 0.70748 | 0.65917 | 0.65361 | 0.71125
43602.6553 | 0.89435 | 0.9924 | 0.92454 | 0.77965 | 0.70525 | 0.65768 | 0.65211 | 0.71194
43602.6555 | 0.87983 | 0.98686 | 0.92081 | 0.77763 | 0.70536 | 0.65801 | 0.6528 | 0.71293
43602.6555 | 0.86022 | 0.98286 | 0.91935 | 0.77632 | 0.70424 | 0.65733 | 0.65577 | 0.71309
43602.6555 | 0.87549 | 0.98437 | 0.91797 | 0.77516 | 0.70274 | 0.65624 | 0.65205 | 0.71303
43602.6557 | 0.85194 | 0.97613 | 0.91461 | 0.77253 | 0.70026 | 0.65438 | 0.65004 | 0.71249
43602.6557 | 0.86846 | 0.9813 | 0.91734 | 0.77485 | 0.70135 | 0.65519 | 0.65002 | 0.71329
43602.6557 | 0.88935 | 0.99368 | 0.9253 | 0.78057 | 0.7062 | 0.65797 | 0.65511 | 0.71366
43602.6559 | 0.86883 | 0.98501 | 0.92127 | 0.77645 | 0.70462 | 0.65739 | 0.65346 | 0.71325
43602.6559 | 0.8755 | 0.98678 | 0.92326 | 0.7773 | 0.70246 | 0.65588 | 0.65123 | 0.71263
43602.6559 | 0.86545 | 0.98835 | 0.9247 | 0.77852 | 0.70566 | 0.65804 | 0.65421 | 0.7131
43602.6561 | 0.87637 | 0.99075 | 0.92549 | 0.7799 | 0.70731 | 0.65897 | 0.65561 | 0.71441
43602.6561 | 0.86323 | 0.98483 | 0.92302 | 0.77733 | 0.70446 | 0.65778 | 0.65247 | 0.71328
43602.6561 | 0.85752 | 0.98263 | 0.92106 | 0.77648 | 0.70346 | 0.65741 | 0.65264 | 0.71445
43602.6562 | 0.85207 | 0.97823 | 0.91727 | 0.77308 | 0.70035 | 0.65535 | 0.65184 | 0.71403
43602.6563 | 0.83101 | 0.97431 | 0.91612 | 0.77238 | 0.70086 | 0.65502 | 0.65165 | 0.71397
43602.6562 | 0.84157 | 0.97141 | 0.9123 | 0.76909 | 0.6967 | 0.65213 | 0.65034 | 0.7131
43602.6564 | 0.84554 | 0.97293 | 0.91289 | 0.76918 | 0.69655 | 0.65133 | 0.64683 | 0.71203
43602.6564 | 0.83141 | 0.97428 | 0.91511 | 0.77036 | 0.69626 | 0.65112 | 0.6492 | 0.71198
43602.6564 | 0.83712 | 0.97979 | 0.91988 | 0.77325 | 0.69823 | 0.65234 | 0.64907 | 0.71178
43602.6566 | 0.86782 | 0.99543 | 0.93043 | 0.78049 | 0.70362 | 0.65563 | 0.65038 | 0.71233
43602.6566 | 0.8761 | 0.99797 | 0.93253 | 0.78202 | 0.7045 | 0.65627 | 0.65131 | 0.71251
43602.6566 | 0.85839 | 0.99952 | 0.93474 | 0.78269 | 0.70626 | 0.65838 | 0.65369 | 0.71318
43602.6568 | 0.8558 | 0.99942 | 0.93625 | 0.78406 | 0.70777 | 0.66006 | 0.65609 | 0.71432
43602.6568 | 0.84163 | 0.99665 | 0.93554 | 0.78329 | 0.7077 | 0.6603 | 0.6552 | 0.7149
43602.6568 | 0.84016 | 0.99204 | 0.93203 | 0.78151 | 0.70684 | 0.65951 | 0.65404 | 0.71562
43602.657 | 0.82022 | 0.97578 | 0.92092 | 0.77395 | 0.70106 | 0.65642 | 0.6521 | 0.7157
43602.657 | 0.82621 | 0.97768 | 0.92127 | 0.77452 | 0.70096 | 0.65634 | 0.65168 | 0.71572
43602.657 | 0.8114 | 0.96892 | 0.9157 | 0.77116 | 0.6981 | 0.65422 | 0.65199 | 0.71498
43602.6571 | 0.80579 | 0.96267 | 0.9117 | 0.76792 | 0.69575 | 0.65193 | 0.64807 | 0.71432
43602.6572 | 0.80079 | 0.96134 | 0.91127 | 0.7674 | 0.695 | 0.65136 | 0.64972 | 0.71435
43602.6571 | 0.80639 | 0.96015 | 0.90785 | 0.76447 | 0.692 | 0.64889 | 0.64466 | 0.71289
43602.6573 | 0.7953 | 0.95508 | 0.90604 | 0.76206 | 0.68869 | 0.6455 | 0.64176 | 0.71064
43602.6573 | 0.80249 | 0.95748 | 0.90601 | 0.76217 | 0.68875 | 0.64506 | 0.64378 | 0.71044
43602.6573 | 0.80874 | 0.96466 | 0.91162 | 0.76423 | 0.68886 | 0.64377 | 0.63949 | 0.70817
43602.6575 | 0.82384 | 0.97588 | 0.92114 | 0.76876 | 0.69056 | 0.64425 | 0.64085 | 0.70686
43602.6575 | 0.83052 | 0.98026 | 0.92365 | 0.77017 | 0.69148 | 0.64445 | 0.63928 | 0.70678
43602.6575 | 0.84516 | 0.99534 | 0.93395 | 0.77639 | 0.69668 | 0.64769 | 0.64196 | 0.70663
43602.6577 | 0.8778 | 1.0138 | 0.94486 | 0.78461 | 0.70424 | 0.65269 | 0.64862 | 0.70742
43602.6577 | 0.86401 | 1.0119 | 0.94415 | 0.78364 | 0.70442 | 0.65321 | 0.64604 | 0.70754
43602.6577 | 0.88662 | 1.0204 | 0.94697 | 0.78694 | 0.70746 | 0.65583 | 0.64876 | 0.70774
43602.6579 | 0.89415 | 1.0175 | 0.94342 | 0.78594 | 0.70924 | 0.65771 | 0.65076 | 0.70933
43602.6579 | 0.87528 | 1.0135 | 0.94128 | 0.78388 | 0.70631 | 0.65575 | 0.65169 | 0.70829
43602.6579 | 0.86625 | 1.0039 | 0.93493 | 0.78042 | 0.70385 | 0.65519 | 0.6488 | 0.71061
43602.6581 | 0.87025 | 0.99962 | 0.93078 | 0.7785 | 0.70269 | 0.65512 | 0.64958 | 0.71194
43602.6581 | 0.85129 | 0.99476 | 0.92906 | 0.77752 | 0.70222 | 0.65463 | 0.65141 | 0.71177
43602.658 | 0.83094 | 0.98382 | 0.9225 | 0.77252 | 0.69896 | 0.65287 | 0.64793 | 0.71207
43602.6582 | 0.85683 | 0.98637 | 0.92018 | 0.77245 | 0.69805 | 0.65182 | 0.64767 | 0.7123
43602.6582 | 0.86235 | 0.98857 | 0.92144 | 0.77332 | 0.69836 | 0.65212 | 0.64711 | 0.7122
43602.6582 | 0.85631 | 0.98122 | 0.91662 | 0.77 | 0.69573 | 0.6503 | 0.64513 | 0.71177
43602.6584 | 0.86061 | 0.98264 | 0.91559 | 0.76887 | 0.69477 | 0.64903 | 0.64348 | 0.71075
43602.6584 | 0.86458 | 0.98182 | 0.91486 | 0.76825 | 0.69464 | 0.64877 | 0.64701 | 0.71059
43602.6584 | 0.8631 | 0.98173 | 0.91494 | 0.76717 | 0.69481 | 0.64826 | 0.64545 | 0.709
43602.6586 | 0.87804 | 0.98809 | 0.91693 | 0.76956 | 0.69658 | 0.65024 | 0.64418 | 0.70946
43602.6586 | 0.88696 | 0.99074 | 0.91795 | 0.76972 | 0.6954 | 0.64879 | 0.64511 | 0.70882
43602.6586 | 0.8999 | 0.98954 | 0.91621 | 0.76904 | 0.69524 | 0.64884 | 0.64344 | 0.70882
43602.6588 | 0.88497 | 0.98374 | 0.91186 | 0.76618 | 0.69174 | 0.64688 | 0.64169 | 0.7084
43602.6588 | 0.87835 | 0.97743 | 0.90828 | 0.76297 | 0.69385 | 0.64815 | 0.64723 | 0.70891
43602.6588 | 0.87087 | 0.97434 | 0.90498 | 0.76176 | 0.68869 | 0.64471 | 0.63956 | 0.70822
43602.659 | 0.85679 | 0.96198 | 0.89569 | 0.75459 | 0.68568 | 0.64277 | 0.63833 | 0.70768
43602.659 | 0.87715 | 0.96653 | 0.89776 | 0.75636 | 0.68513 | 0.64236 | 0.63847 | 0.70835
43602.6589 | 0.88111 | 0.96258 | 0.89414 | 0.75387 | 0.6841 | 0.64184 | 0.63777 | 0.70789
43602.6591 | 0.87488 | 0.95942 | 0.89065 | 0.75164 | 0.68198 | 0.63982 | 0.63696 | 0.7071
43602.6592 | 0.88026 | 0.95851 | 0.89015 | 0.75084 | 0.68324 | 0.64079 | 0.63659 | 0.70725
43602.6591 | 0.89047 | 0.96172 | 0.8917 | 0.7515 | 0.68371 | 0.64115 | 0.63602 | 0.70625
43602.6593 | 0.90733 | 0.96786 | 0.89495 | 0.75425 | 0.68445 | 0.64155 | 0.63827 | 0.70578
43602.6593 | 0.89608 | 0.96179 | 0.89074 | 0.75024 | 0.68397 | 0.64145 | 0.63638 | 0.70566
43602.6593 | 0.90207 | 0.96906 | 0.89494 | 0.75469 | 0.68537 | 0.64248 | 0.6394 | 0.70635
43602.6595 | 0.88278 | 0.96187 | 0.88972 | 0.74992 | 0.68367 | 0.64165 | 0.63699 | 0.70598
43602.6595 | 0.92665 | 0.97727 | 0.90154 | 0.75999 | 0.68521 | 0.64276 | 0.6385 | 0.70603
43602.6595 | 0.87601 | 0.95276 | 0.88293 | 0.74489 | 0.67986 | 0.63884 | 0.63425 | 0.70543
43602.6597 | 0.88729 | 0.94844 | 0.87814 | 0.74129 | 0.67723 | 0.63658 | 0.63429 | 0.70484
43602.6597 | 0.88423 | 0.95191 | 0.88081 | 0.7442 | 0.67619 | 0.63551 | 0.63188 | 0.70459
43602.6597 | 0.88371 | 0.94775 | 0.87688 | 0.74099 | 0.67726 | 0.63667 | 0.63298 | 0.70458
43602.6599 | 0.88578 | 0.94877 | 0.87675 | 0.7415 | 0.67741 | 0.63663 | 0.63227 | 0.70457
43602.6599 | 0.88225 | 0.9419 | 0.87162 | 0.73734 | 0.67422 | 0.63409 | 0.63185 | 0.70415
43602.6599 | 0.91801 | 0.96014 | 0.88533 | 0.74982 | 0.67856 | 0.63755 | 0.63316 | 0.70486
43602.66 | 0.89996 | 0.95163 | 0.87853 | 0.74482 | 0.67598 | 0.63622 | 0.63111 | 0.70477
43602.6601 | 0.89587 | 0.94762 | 0.87537 | 0.74201 | 0.67746 | 0.63724 | 0.63626 | 0.70536
43602.66 | 0.90001 | 0.95271 | 0.87877 | 0.74576 | 0.67638 | 0.63697 | 0.63274 | 0.70544
43602.6602 | 0.86735 | 0.934 | 0.86411 | 0.7333 | 0.67335 | 0.63443 | 0.63038 | 0.70547
43602.6602 | 0.90287 | 0.94471 | 0.87288 | 0.74144 | 0.67226 | 0.63402 | 0.63022 | 0.70547
43602.6602 | 0.87805 | 0.93213 | 0.86206 | 0.7336 | 0.67058 | 0.63274 | 0.62974 | 0.70609
43602.6604 | 0.86694 | 0.92575 | 0.85713 | 0.73111 | 0.66646 | 0.62958 | 0.62735 | 0.70583
43602.6604 | 0.87214 | 0.92612 | 0.85776 | 0.73213 | 0.66991 | 0.63257 | 0.62965 | 0.70705
43602.6604 | 0.86271 | 0.91651 | 0.84955 | 0.72666 | 0.66404 | 0.62788 | 0.62701 | 0.70597
43602.6606 | 0.84812 | 0.91336 | 0.84694 | 0.72383 | 0.66463 | 0.62797 | 0.62754 | 0.70537
43602.6606 | 0.86016 | 0.91567 | 0.84915 | 0.72616 | 0.66182 | 0.62627 | 0.62482 | 0.70547
43602.6606 | 0.86291 | 0.91749 | 0.8498 | 0.72718 | 0.66487 | 0.62847 | 0.62588 | 0.70559
43602.6608 | 0.85993 | 0.91822 | 0.85 | 0.72702 | 0.6637 | 0.62763 | 0.62587 | 0.70535
43602.6608 | 0.87295 | 0.92177 | 0.85248 | 0.72968 | 0.6649 | 0.62872 | 0.62946 | 0.70555
43602.6608 | 0.86072 | 0.91625 | 0.84866 | 0.72675 | 0.66537 | 0.62922 | 0.6275 | 0.70642
43602.661 | 0.85497 | 0.90776 | 0.84271 | 0.72257 | 0.66093 | 0.62626 | 0.62578 | 0.70647
43602.661 | 0.86459 | 0.91243 | 0.8462 | 0.72571 | 0.6628 | 0.62799 | 0.62635 | 0.70725
43602.6609 | 0.85211 | 0.90484 | 0.84063 | 0.7221 | 0.66087 | 0.62626 | 0.62552 | 0.70693
43602.6611 | 0.8289 | 0.9026 | 0.83775 | 0.72054 | 0.65868 | 0.62468 | 0.6255 | 0.70691
43602.6612 | 0.84069 | 0.9004 | 0.83654 | 0.7193 | 0.65812 | 0.6242 | 0.62355 | 0.70672
43602.6611 | 0.83086 | 0.90227 | 0.8367 | 0.7191 | 0.65892 | 0.62419 | 0.62329 | 0.70628
43602.6613 | 0.84393 | 0.89821 | 0.83367 | 0.71768 | 0.65633 | 0.62291 | 0.622 | 0.70651
43602.6613 | 0.83178 | 0.89926 | 0.83408 | 0.71791 | 0.65692 | 0.62294 | 0.6228 | 0.7063
43602.6613 | 0.82891 | 0.89608 | 0.83154 | 0.71635 | 0.6552 | 0.62184 | 0.62135 | 0.70598
43602.6615 | 0.82586 | 0.89391 | 0.82952 | 0.71513 | 0.65397 | 0.62088 | 0.62178 | 0.70576
43602.6615 | 0.82083 | 0.89311 | 0.82916 | 0.71448 | 0.65398 | 0.62092 | 0.62014 | 0.70563
43602.6615 | 0.8019 | 0.88867 | 0.82439 | 0.71169 | 0.65082 | 0.61924 | 0.6191 | 0.70546
43602.6617 | 0.80599 | 0.88539 | 0.82063 | 0.70983 | 0.64864 | 0.61748 | 0.61713 | 0.70471
43602.6617 | 0.79754 | 0.88648 | 0.82115 | 0.70977 | 0.64882 | 0.61744 | 0.61895 | 0.70476
43602.6617 | 0.80153 | 0.88643 | 0.82147 | 0.71016 | 0.64894 | 0.6173 | 0.61781 | 0.70437
43602.6619 | 0.80663 | 0.88391 | 0.81958 | 0.7082 | 0.64835 | 0.61714 | 0.61735 | 0.7046
43602.6619 | 0.80926 | 0.88499 | 0.81998 | 0.70885 | 0.6482 | 0.61691 | 0.61654 | 0.70469
43602.6619 | 0.81768 | 0.88325 | 0.82003 | 0.70909 | 0.64879 | 0.61776 | 0.618 | 0.7051
43602.6621 | 0.81454 | 0.88707 | 0.82269 | 0.71107 | 0.65096 | 0.6193 | 0.61874 | 0.70579
43602.6621 | 0.80529 | 0.88734 | 0.82252 | 0.7105 | 0.65077 | 0.61932 | 0.62157 | 0.70609
43602.662 | 0.80736 | 0.88812 | 0.82298 | 0.71135 | 0.65174 | 0.62061 | 0.62253 | 0.70706
43602.6622 | 0.79788 | 0.88508 | 0.82075 | 0.71029 | 0.65183 | 0.62153 | 0.62228 | 0.70831
43602.6623 | 0.78821 | 0.88495 | 0.82016 | 0.70981 | 0.65107 | 0.62096 | 0.62066 | 0.70829
43602.6622 | 0.78178 | 0.881 | 0.81688 | 0.7087 | 0.64961 | 0.6202 | 0.62223 | 0.70868
43602.6624 | 0.78118 | 0.87532 | 0.81142 | 0.70462 | 0.64692 | 0.61787 | 0.61918 | 0.7077
43602.6624 | 0.77883 | 0.87319 | 0.80916 | 0.70338 | 0.64571 | 0.61738 | 0.61828 | 0.70771
43602.6624 | 0.77272 | 0.86695 | 0.80469 | 0.69994 | 0.64232 | 0.61465 | 0.61672 | 0.70667
43602.6626 | 0.76752 | 0.86722 | 0.80327 | 0.69935 | 0.64038 | 0.61224 | 0.61399 | 0.70519
43602.6626 | 0.76304 | 0.86744 | 0.80353 | 0.6995 | 0.63995 | 0.61186 | 0.61476 | 0.70491
43602.6626 | 0.76722 | 0.87493 | 0.80934 | 0.70325 | 0.64221 | 0.61215 | 0.61479 | 0.70403
43602.6628 | 0.78861 | 0.87824 | 0.81291 | 0.70582 | 0.64433 | 0.61444 | 0.61662 | 0.70439
43602.6628 | 0.7743 | 0.88012 | 0.81427 | 0.7065 | 0.64456 | 0.61428 | 0.61528 | 0.70419
43602.6628 | 0.80449 | 0.88277 | 0.81796 | 0.70819 | 0.64758 | 0.61684 | 0.61992 | 0.70519
43602.663 | 0.8258 | 0.88283 | 0.81824 | 0.70923 | 0.64937 | 0.61985 | 0.62086 | 0.70713
43602.663 | 0.81818 | 0.87939 | 0.81682 | 0.70795 | 0.65004 | 0.6198 | 0.61985 | 0.707
43602.663 | 0.79533 | 0.87615 | 0.81262 | 0.70514 | 0.64705 | 0.61848 | 0.6205 | 0.70783
43602.6632 | 0.80914 | 0.87503 | 0.81242 | 0.70604 | 0.64767 | 0.61916 | 0.62158 | 0.70849
43602.6632 | 0.82274 | 0.87816 | 0.81432 | 0.70803 | 0.64938 | 0.61963 | 0.62031 | 0.70818
43602.6632 | 0.81121 | 0.87517 | 0.81244 | 0.706 | 0.64836 | 0.61982 | 0.62067 | 0.70901
43602.6633 | 0.79856 | 0.87459 | 0.81062 | 0.70508 | 0.64819 | 0.61942 | 0.62198 | 0.70871
43602.6634 | 0.78926 | 0.8736 | 0.80985 | 0.7039 | 0.6469 | 0.61877 | 0.62001 | 0.70878
43602.6633 | 0.79032 | 0.87089 | 0.80781 | 0.70369 | 0.64642 | 0.61862 | 0.62024 | 0.70922
43602.6635 | 0.80362 | 0.87477 | 0.80973 | 0.7056 | 0.64787 | 0.61909 | 0.62169 | 0.70877
43602.6635 | 0.79565 | 0.87111 | 0.80821 | 0.70408 | 0.64729 | 0.61892 | 0.61994 | 0.70886
43602.6635 | 0.79437 | 0.87266 | 0.80992 | 0.70531 | 0.648 | 0.61935 | 0.62082 | 0.70905
43602.6637 | 0.78822 | 0.86833 | 0.80678 | 0.70238 | 0.64606 | 0.61864 | 0.62049 | 0.70917
43602.6637 | 0.79309 | 0.8699 | 0.80771 | 0.70366 | 0.64621 | 0.61936 | 0.62189 | 0.70963
43602.6637 | 0.78419 | 0.86857 | 0.80632 | 0.70267 | 0.64601 | 0.61847 | 0.61968 | 0.70929
43602.6639 | 0.78251 | 0.86714 | 0.80512 | 0.70278 | 0.64524 | 0.61794 | 0.62118 | 0.70905
43602.6639 | 0.78227 | 0.86565 | 0.80472 | 0.70229 | 0.64462 | 0.61773 | 0.61849 | 0.70919
43602.6639 | 0.78142 | 0.86455 | 0.80205 | 0.70038 | 0.64419 | 0.6172 | 0.61894 | 0.70924
43602.6641 | 0.78262 | 0.86497 | 0.80121 | 0.69972 | 0.64317 | 0.61639 | 0.61717 | 0.70891
43602.6641 | 0.78592 | 0.86814 | 0.80496 | 0.70195 | 0.64515 | 0.61769 | 0.61931 | 0.7091
43602.6644 | 0.79546 | 0.86876 | 0.80626 | 0.70231 | 0.64611 | 0.61901 | 0.62058 | 0.71029
43602.6644 | 0.8045 | 0.8728 | 0.80869 | 0.70511 | 0.64743 | 0.61996 | 0.6226 | 0.71029
43602.6643 | 0.79478 | 0.87345 | 0.80906 | 0.70526 | 0.64813 | 0.61994 | 0.62126 | 0.71026
43602.6645 | 0.78604 | 0.86898 | 0.80567 | 0.70339 | 0.64625 | 0.61879 | 0.62137 | 0.71028
43602.6646 | 0.79226 | 0.87121 | 0.80706 | 0.70411 | 0.64667 | 0.61924 | 0.62029 | 0.71041
43602.6645 | 0.78002 | 0.86894 | 0.80494 | 0.70251 | 0.64492 | 0.61802 | 0.61986 | 0.71023
43602.6647 | 0.7844 | 0.87009 | 0.8064 | 0.70443 | 0.64685 | 0.61896 | 0.62035 | 0.7102
43602.6647 | 0.77582 | 0.86785 | 0.80474 | 0.70303 | 0.64543 | 0.61819 | 0.62299 | 0.71032
43602.6647 | 0.78154 | 0.86897 | 0.80459 | 0.70332 | 0.64568 | 0.61808 | 0.62151 | 0.7103
43602.6649 | 0.78562 | 0.87325 | 0.80857 | 0.70543 | 0.64726 | 0.6198 | 0.62086 | 0.71083
43602.6649 | 0.78399 | 0.87304 | 0.80783 | 0.70568 | 0.64743 | 0.62004 | 0.62034 | 0.71079
43602.6649 | 0.78429 | 0.87418 | 0.80939 | 0.70644 | 0.64714 | 0.61996 | 0.62096 | 0.71096
43602.6651 | 0.78207 | 0.87369 | 0.80901 | 0.70588 | 0.64728 | 0.62047 | 0.62132 | 0.71136
43602.6651 | 0.78145 | 0.87222 | 0.8081 | 0.70552 | 0.64708 | 0.61989 | 0.6224 | 0.71081
43602.6651 | 0.77797 | 0.86996 | 0.80622 | 0.70364 | 0.64637 | 0.61998 | 0.6214 | 0.71137
43602.6653 | 0.77514 | 0.86886 | 0.80566 | 0.70349 | 0.64642 | 0.62028 | 0.62194 | 0.71203
43602.6653 | 0.77529 | 0.86967 | 0.80621 | 0.70392 | 0.64625 | 0.61993 | 0.62162 | 0.71164
43602.6653 | 0.77394 | 0.86789 | 0.80508 | 0.7031 | 0.64586 | 0.61998 | 0.62058 | 0.71177
43602.6655 | 0.77775 | 0.86674 | 0.80325 | 0.70241 | 0.64546 | 0.61983 | 0.62103 | 0.71201
43602.6655 | 0.77571 | 0.86671 | 0.80288 | 0.70192 | 0.64495 | 0.61924 | 0.62237 | 0.71162
43602.6654 | 0.77224 | 0.86577 | 0.80204 | 0.70158 | 0.64465 | 0.61942 | 0.6207 | 0.71186
43602.6656 | 0.77489 | 0.86766 | 0.80378 | 0.70248 | 0.64549 | 0.61925 | 0.62055 | 0.71188
43602.6657 | 0.77337 | 0.86862 | 0.8044 | 0.70323 | 0.6456 | 0.61936 | 0.62158 | 0.71168
43602.6656 | 0.77502 | 0.86466 | 0.80246 | 0.70079 | 0.64459 | 0.61911 | 0.6208 | 0.71215
43602.6658 | 0.77969 | 0.86854 | 0.80374 | 0.70246 | 0.64526 | 0.61912 | 0.62195 | 0.71181
43602.6658 | 0.7795 | 0.86704 | 0.80357 | 0.70241 | 0.64558 | 0.61942 | 0.62144 | 0.71211
43602.6658 | 0.7777 | 0.8667 | 0.80271 | 0.70143 | 0.6457 | 0.61992 | 0.62159 | 0.71224
43602.666 | 0.7773 | 0.86703 | 0.8039 | 0.70266 | 0.6454 | 0.62012 | 0.62236 | 0.71257
43602.666 | 0.78144 | 0.86716 | 0.80366 | 0.70343 | 0.64614 | 0.61998 | 0.62314 | 0.71239
43602.666 | 0.78296 | 0.86821 | 0.80393 | 0.70297 | 0.64594 | 0.61984 | 0.62314 | 0.71214
43602.6662 | 0.7772 | 0.86862 | 0.80415 | 0.70383 | 0.64672 | 0.62011 | 0.62347 | 0.71266
43602.6662 | 0.77909 | 0.8683 | 0.8045 | 0.70354 | 0.64635 | 0.61969 | 0.62123 | 0.71242
43602.6662 | 0.78569 | 0.87336 | 0.80844 | 0.70599 | 0.64804 | 0.62135 | 0.6222 | 0.71273
43602.6664 | 0.78949 | 0.87213 | 0.80773 | 0.70485 | 0.64823 | 0.62185 | 0.62321 | 0.71303
43602.6664 | 0.78719 | 0.87125 | 0.80712 | 0.70462 | 0.64795 | 0.62163 | 0.62314 | 0.71297
43602.6664 | 0.77816 | 0.86971 | 0.80532 | 0.70407 | 0.64688 | 0.6209 | 0.6243 | 0.7128
43602.6666 | 0.78043 | 0.86716 | 0.80314 | 0.70245 | 0.64578 | 0.62012 | 0.62433 | 0.713
43602.6666 | 0.77843 | 0.86628 | 0.80289 | 0.70246 | 0.64569 | 0.6201 | 0.62196 | 0.7127
43602.6666 | 0.77589 | 0.86463 | 0.80197 | 0.70199 | 0.645 | 0.61944 | 0.62399 | 0.71233
43602.6667 | 0.77349 | 0.86199 | 0.79886 | 0.69973 | 0.64305 | 0.61822 | 0.62008 | 0.71193
43602.6668 | 0.78329 | 0.86458 | 0.80029 | 0.69955 | 0.64343 | 0.61864 | 0.62175 | 0.71212
43602.6667 | 0.77153 | 0.86051 | 0.79702 | 0.69806 | 0.64178 | 0.61673 | 0.61899 | 0.71108
43602.6669 | 0.77579 | 0.85986 | 0.79601 | 0.69712 | 0.64078 | 0.61575 | 0.61904 | 0.71064
43602.6669 | 0.77437 | 0.85929 | 0.79517 | 0.69712 | 0.64003 | 0.61494 | 0.61699 | 0.7102
43602.6669 | 0.77448 | 0.85601 | 0.79194 | 0.69364 | 0.63816 | 0.6136 | 0.61574 | 0.70958
43602.6671 | 0.78191 | 0.85805 | 0.79405 | 0.69531 | 0.6381 | 0.61315 | 0.61471 | 0.70864
43602.6671 | 0.77911 | 0.85755 | 0.79332 | 0.69456 | 0.63794 | 0.61254 | 0.61691 | 0.70818
43602.6671 | 0.77268 | 0.85494 | 0.79188 | 0.69282 | 0.63662 | 0.61186 | 0.61424 | 0.70796
43602.6673 | 0.78159 | 0.85521 | 0.79151 | 0.69263 | 0.63627 | 0.61209 | 0.61385 | 0.70787
43602.6673 | 0.77923 | 0.85566 | 0.79208 | 0.69246 | 0.63636 | 0.61201 | 0.61605 | 0.70776
43602.6673 | 0.79022 | 0.85844 | 0.79424 | 0.69359 | 0.63749 | 0.61251 | 0.61562 | 0.70742
43602.6675 | 0.79958 | 0.8625 | 0.79763 | 0.6959 | 0.64036 | 0.61424 | 0.61756 | 0.70774
43602.6675 | 0.7816 | 0.85722 | 0.7935 | 0.69288 | 0.63782 | 0.61237 | 0.61392 | 0.70733
43602.6675 | 0.80266 | 0.85898 | 0.79427 | 0.69355 | 0.63766 | 0.61304 | 0.61447 | 0.70774
43602.6677 | 0.79679 | 0.85543 | 0.79127 | 0.6912 | 0.63557 | 0.61148 | 0.61414 | 0.7074
43602.6677 | 0.7939 | 0.85569 | 0.79123 | 0.69107 | 0.63646 | 0.61179 | 0.61534 | 0.70728
43602.6677 | 0.78928 | 0.85657 | 0.79102 | 0.69128 | 0.6357 | 0.61133 | 0.61535 | 0.70699
43602.6679 | 0.78478 | 0.85378 | 0.78934 | 0.68989 | 0.63488 | 0.61064 | 0.61234 | 0.70688
43602.6679 | 0.79295 | 0.85526 | 0.79008 | 0.69036 | 0.63467 | 0.6106 | 0.61269 | 0.7068
43602.6678 | 0.80067 | 0.85659 | 0.79108 | 0.691 | 0.63533 | 0.61076 | 0.61442 | 0.70659
43602.668 | 0.79762 | 0.85404 | 0.78922 | 0.68915 | 0.63373 | 0.61015 | 0.61191 | 0.70649
43602.668 | 0.79791 | 0.85698 | 0.79145 | 0.69112 | 0.63478 | 0.61052 | 0.61457 | 0.70637
43602.668 | 0.79702 | 0.85748 | 0.79161 | 0.69117 | 0.63593 | 0.61162 | 0.61341 | 0.70658
43602.6682 | 0.80306 | 0.85807 | 0.79291 | 0.69177 | 0.63613 | 0.61184 | 0.6138 | 0.7069
43602.6682 | 0.80605 | 0.86008 | 0.79409 | 0.69236 | 0.63624 | 0.61167 | 0.61285 | 0.7066
43602.6682 | 0.7893 | 0.85386 | 0.79021 | 0.68989 | 0.6348 | 0.61088 | 0.61293 | 0.70712
43602.6684 | 0.78183 | 0.85564 | 0.79086 | 0.69054 | 0.63484 | 0.6106 | 0.61271 | 0.70659
43602.6684 | 0.78652 | 0.85481 | 0.79032 | 0.69063 | 0.63421 | 0.61056 | 0.61405 | 0.70708
43602.6684 | 0.79679 | 0.85909 | 0.79321 | 0.69219 | 0.63634 | 0.6114 | 0.61447 | 0.70693
43602.6686 | 0.78482 | 0.85464 | 0.79143 | 0.69109 | 0.63533 | 0.61135 | 0.61366 | 0.70757
43602.6686 | 0.78038 | 0.85674 | 0.79176 | 0.69158 | 0.63573 | 0.61221 | 0.614 | 0.70791
43602.6686 | 0.77924 | 0.85482 | 0.79141 | 0.69068 | 0.63525 | 0.6113 | 0.61455 | 0.70773
43602.6688 | 0.7791 | 0.85481 | 0.79006 | 0.69103 | 0.63498 | 0.6117 | 0.61366 | 0.7078
43602.6688 | 0.77883 | 0.85353 | 0.78883 | 0.68966 | 0.6347 | 0.6113 | 0.61336 | 0.70782
43602.6688 | 0.76508 | 0.85131 | 0.78683 | 0.68863 | 0.63234 | 0.60901 | 0.61181 | 0.70714
43602.669 | 0.77055 | 0.85168 | 0.78649 | 0.6878 | 0.63167 | 0.60892 | 0.6126 | 0.70684
43602.669 | 0.76973 | 0.85121 | 0.78635 | 0.68756 | 0.63218 | 0.60912 | 0.61148 | 0.70711
43602.6689 | 0.77041 | 0.85827 | 0.79259 | 0.69254 | 0.63409 | 0.60974 | 0.61159 | 0.70656
43602.6691 | 0.77701 | 0.86701 | 0.80038 | 0.69728 | 0.63851 | 0.61318 | 0.61466 | 0.70728
43602.6692 | 0.77935 | 0.86605 | 0.80009 | 0.69693 | 0.63837 | 0.61329 | 0.61681 | 0.70772
43602.6691 | 0.78682 | 0.8669 | 0.80145 | 0.69705 | 0.63953 | 0.61541 | 0.6172 | 0.70967
43602.6693 | 0.77475 | 0.86393 | 0.7989 | 0.69648 | 0.63997 | 0.61545 | 0.61715 | 0.71033
43602.6693 | 0.77822 | 0.8628 | 0.79766 | 0.69542 | 0.63996 | 0.61631 | 0.62004 | 0.71103
43602.6693 | 0.77073 | 0.85678 | 0.79239 | 0.69247 | 0.6376 | 0.61432 | 0.61843 | 0.71063
43602.6695 | 0.76511 | 0.85335 | 0.78872 | 0.6902 | 0.6342 | 0.61149 | 0.61338 | 0.70914
43602.6695 | 0.76707 | 0.85223 | 0.78812 | 0.68916 | 0.63397 | 0.61136 | 0.61596 | 0.70916
43602.6695 | 0.75994 | 0.85184 | 0.78724 | 0.68817 | 0.63165 | 0.60881 | 0.61138 | 0.70765
43602.6697 | 0.75989 | 0.85319 | 0.78755 | 0.68774 | 0.63012 | 0.6067 | 0.60968 | 0.70614
43602.6697 | 0.76122 | 0.85443 | 0.78818 | 0.68797 | 0.62994 | 0.60642 | 0.61168 | 0.70579
43602.6697 | 0.75511 | 0.86015 | 0.79362 | 0.6916 | 0.63109 | 0.60685 | 0.60868 | 0.70503
43602.6699 | 0.75649 | 0.86549 | 0.79817 | 0.69402 | 0.63196 | 0.60671 | 0.60804 | 0.70418
43602.6699 | 0.76094 | 0.86504 | 0.79812 | 0.69356 | 0.63195 | 0.60676 | 0.60815 | 0.70404
43602.6699 | 0.77076 | 0.87289 | 0.8048 | 0.69777 | 0.63467 | 0.60875 | 0.61027 | 0.70393
43602.6701 | 0.76797 | 0.87538 | 0.80666 | 0.69815 | 0.6353 | 0.60942 | 0.61175 | 0.70383
43602.6701 | 0.76957 | 0.87575 | 0.80665 | 0.69817 | 0.63621 | 0.60983 | 0.6103 | 0.70392
43602.6701 | 0.77566 | 0.87975 | 0.80972 | 0.69899 | 0.6374 | 0.6105 | 0.61071 | 0.70377
43602.6702 | 0.80975 | 0.87909 | 0.81213 | 0.70081 | 0.63855 | 0.61125 | 0.61349 | 0.7039
43602.6703 | 0.79839 | 0.88293 | 0.81319 | 0.70231 | 0.63958 | 0.61168 | 0.61204 | 0.70376
43602.6702 | 0.80961 | 0.88132 | 0.81329 | 0.70201 | 0.64011 | 0.61226 | 0.61496 | 0.70423
43602.6704 | 0.82229 | 0.88711 | 0.81908 | 0.70478 | 0.64395 | 0.6154 | 0.61489 | 0.7049
43602.6704 | 0.82398 | 0.8895 | 0.82075 | 0.70629 | 0.64315 | 0.61525 | 0.6152 | 0.70532
43602.6704 | 0.83352 | 0.89212 | 0.82393 | 0.70725 | 0.64552 | 0.61707 | 0.61685 | 0.70584
43602.6706 | 0.84623 | 0.89315 | 0.82608 | 0.70937 | 0.64763 | 0.619 | 0.61773 | 0.7069
43602.6706 | 0.84791 | 0.89818 | 0.82873 | 0.71168 | 0.64848 | 0.61918 | 0.62001 | 0.70694
43602.6706 | 0.83311 | 0.89225 | 0.8249 | 0.70868 | 0.64753 | 0.61933 | 0.61922 | 0.70785
43602.6708 | 0.82557 | 0.89433 | 0.82575 | 0.71018 | 0.64929 | 0.62044 | 0.62164 | 0.70818
43602.6708 | 0.81273 | 0.89179 | 0.82439 | 0.70833 | 0.64746 | 0.61947 | 0.61959 | 0.70833
43602.6708 | 0.80709 | 0.89407 | 0.82516 | 0.71024 | 0.64734 | 0.6197 | 0.6197 | 0.70858
43602.671 | 0.80361 | 0.88997 | 0.82138 | 0.708 | 0.64589 | 0.61857 | 0.61857 | 0.70846
43602.671 | 0.81159 | 0.89048 | 0.82147 | 0.70951 | 0.64691 | 0.61905 | 0.61879 | 0.70868
43602.671 | 0.77839 | 0.88531 | 0.81566 | 0.7049 | 0.64323 | 0.61674 | 0.61717 | 0.7082
43602.6712 | 0.7735 | 0.88178 | 0.81267 | 0.70302 | 0.64078 | 0.61446 | 0.61531 | 0.70689
43602.6712 | 0.77725 | 0.88092 | 0.81176 | 0.70235 | 0.64037 | 0.614 | 0.61466 | 0.70702
43602.6712 | 0.78677 | 0.88158 | 0.81248 | 0.70295 | 0.64041 | 0.61326 | 0.61385 | 0.70605
43602.6713 | 0.77495 | 0.88052 | 0.81133 | 0.70142 | 0.63837 | 0.61177 | 0.61209 | 0.70519
43602.6714 | 0.79355 | 0.88009 | 0.81082 | 0.70261 | 0.63936 | 0.61228 | 0.61294 | 0.70526
43602.6713 | 0.78531 | 0.87833 | 0.80881 | 0.69822 | 0.63762 | 0.61187 | 0.61247 | 0.7053
43602.6715 | 0.81057 | 0.88193 | 0.81303 | 0.70243 | 0.64062 | 0.61345 | 0.61355 | 0.70542
43602.6715 | 0.81256 | 0.88013 | 0.81257 | 0.70194 | 0.64053 | 0.61349 | 0.61312 | 0.70519
43602.6715 | 0.84451 | 0.88774 | 0.81836 | 0.70613 | 0.64277 | 0.61497 | 0.61526 | 0.70588
43602.6717 | 0.79884 | 0.87952 | 0.81134 | 0.70096 | 0.64147 | 0.61473 | 0.6154 | 0.70635
43602.6717 | 0.81294 | 0.87694 | 0.8094 | 0.70021 | 0.64023 | 0.6142 | 0.61543 | 0.70667
43602.6717 | 0.80519 | 0.87431 | 0.80795 | 0.69927 | 0.64086 | 0.61484 | 0.61577 | 0.70722
43602.6719 | 0.81743 | 0.88088 | 0.81363 | 0.70405 | 0.64464 | 0.61742 | 0.61776 | 0.70824
43602.6719 | 0.81568 | 0.8814 | 0.81361 | 0.70413 | 0.64385 | 0.61711 | 0.61894 | 0.70848
43602.6719 | 0.82376 | 0.88272 | 0.8149 | 0.70547 | 0.64613 | 0.61966 | 0.61978 | 0.70942
43602.6721 | 0.81802 | 0.8822 | 0.81507 | 0.70658 | 0.64533 | 0.61964 | 0.621 | 0.71054
43602.6721 | 0.81526 | 0.88316 | 0.81551 | 0.70674 | 0.64695 | 0.62075 | 0.62213 | 0.71071
43602.6721 | 0.79113 | 0.88018 | 0.81252 | 0.70438 | 0.6452 | 0.62002 | 0.6209 | 0.71135
43602.6723 | 0.78885 | 0.87737 | 0.81048 | 0.70369 | 0.64443 | 0.61972 | 0.62172 | 0.71171
43602.6723 | 0.7814 | 0.87723 | 0.8101 | 0.70407 | 0.64482 | 0.61986 | 0.62072 | 0.7117
43602.6723 | 0.77911 | 0.87148 | 0.80555 | 0.70124 | 0.64216 | 0.61793 | 0.61891 | 0.71129
43602.6725 | 0.77519 | 0.87254 | 0.80568 | 0.70131 | 0.64133 | 0.61696 | 0.61801 | 0.71029
43602.6725 | 0.77346 | 0.87238 | 0.80522 | 0.70045 | 0.64097 | 0.61657 | 0.61841 | 0.71006
43602.6724 | 0.77271 | 0.8709 | 0.80332 | 0.69902 | 0.63943 | 0.61576 | 0.617 | 0.70982
43602.6726 | 0.77027 | 0.87176 | 0.80438 | 0.69858 | 0.63834 | 0.6143 | 0.61562 | 0.70867
43602.6727 | 0.76232 | 0.87082 | 0.80452 | 0.69921 | 0.63802 | 0.61375 | 0.61505 | 0.70859
43602.6726 | 0.76444 | 0.8732 | 0.80628 | 0.69995 | 0.63798 | 0.61312 | 0.61454 | 0.70757
43602.6728 | 0.77327 | 0.87508 | 0.80696 | 0.69903 | 0.63829 | 0.61327 | 0.61394 | 0.70722
43602.6728 | 0.76774 | 0.87574 | 0.80768 | 0.69977 | 0.63765 | 0.61324 | 0.61383 | 0.70731
43602.6728 | 0.76747 | 0.87856 | 0.80906 | 0.70013 | 0.63817 | 0.61296 | 0.61365 | 0.70656
43602.673 | 0.77723 | 0.88317 | 0.81389 | 0.70388 | 0.64015 | 0.61374 | 0.61613 | 0.7064
43602.673 | 0.77729 | 0.88426 | 0.81456 | 0.70361 | 0.64021 | 0.61356 | 0.61363 | 0.70612
43602.673 | 0.77792 | 0.8845 | 0.81512 | 0.70349 | 0.64021 | 0.61392 | 0.61473 | 0.70618
43602.6732 | 0.78399 | 0.8891 | 0.81764 | 0.70517 | 0.64113 | 0.61413 | 0.6147 | 0.70578
43602.6732 | 0.79859 | 0.8882 | 0.81868 | 0.70548 | 0.64134 | 0.61472 | 0.61638 | 0.70612
43602.6732 | 0.78685 | 0.89456 | 0.82404 | 0.70837 | 0.64394 | 0.61584 | 0.6179 | 0.70595
43602.6734 | 0.80687 | 0.89783 | 0.8273 | 0.71026 | 0.64618 | 0.61755 | 0.61816 | 0.70686
43602.6734 | 0.81336 | 0.89894 | 0.82785 | 0.71141 | 0.6463 | 0.61785 | 0.61775 | 0.70704
43602.6734 | 0.82327 | 0.89804 | 0.82802 | 0.71073 | 0.64698 | 0.61836 | 0.61848 | 0.70714
43602.6736 | 0.79225 | 0.89271 | 0.8235 | 0.70622 | 0.64455 | 0.61728 | 0.61716 | 0.70674
43602.6736 | 0.78583 | 0.89255 | 0.82335 | 0.70669 | 0.64321 | 0.61711 | 0.61734 | 0.70746
43602.6736 | 0.81356 | 0.89905 | 0.82728 | 0.71159 | 0.64636 | 0.61772 | 0.61716 | 0.70657
43602.6738 | 0.7814 | 0.89363 | 0.82268 | 0.70702 | 0.64275 | 0.61537 | 0.61595 | 0.70553
43602.6738 | 0.77989 | 0.89253 | 0.82163 | 0.70601 | 0.64214 | 0.61496 | 0.61433 | 0.7056
43602.6737 | 0.77865 | 0.89116 | 0.82064 | 0.70534 | 0.64077 | 0.61381 | 0.61454 | 0.70504
43602.6739 | 0.77615 | 0.89063 | 0.81992 | 0.70586 | 0.64042 | 0.61333 | 0.61522 | 0.7042
43602.6739 | 0.77854 | 0.8893 | 0.81925 | 0.7038 | 0.63958 | 0.6124 | 0.61246 | 0.70392
43602.6739 | 0.77631 | 0.88707 | 0.81651 | 0.7021 | 0.63809 | 0.61134 | 0.61112 | 0.70385
43602.6741 | 0.77016 | 0.88688 | 0.81637 | 0.70168 | 0.63739 | 0.61111 | 0.61137 | 0.70341
43602.6741 | 0.78662 | 0.88843 | 0.8175 | 0.70314 | 0.63768 | 0.61142 | 0.61125 | 0.70348
43602.6741 | 0.77262 | 0.88677 | 0.81578 | 0.7011 | 0.63657 | 0.6103 | 0.61321 | 0.70307
43602.6743 | 0.78015 | 0.88762 | 0.81519 | 0.70185 | 0.63655 | 0.60949 | 0.61043 | 0.70241
43602.6743 | 0.78427 | 0.88655 | 0.8145 | 0.70085 | 0.63616 | 0.6092 | 0.60984 | 0.70205
43602.6743 | 0.798 | 0.88754 | 0.81605 | 0.70099 | 0.63628 | 0.60913 | 0.60877 | 0.70188
43602.6745 | 0.80144 | 0.8932 | 0.82077 | 0.70412 | 0.63883 | 0.60985 | 0.61067 | 0.70151
43602.6745 | 0.80074 | 0.88988 | 0.81894 | 0.70278 | 0.63777 | 0.60993 | 0.60996 | 0.70146
43602.6745 | 0.80607 | 0.88792 | 0.81752 | 0.70071 | 0.63677 | 0.60915 | 0.61018 | 0.70116
43602.6747 | 0.81284 | 0.88793 | 0.81725 | 0.70174 | 0.63545 | 0.60885 | 0.60931 | 0.702
43602.6747 | 0.82757 | 0.89143 | 0.8198 | 0.70356 | 0.63826 | 0.60991 | 0.60952 | 0.70172
43602.6747 | 0.82834 | 0.88799 | 0.81729 | 0.70161 | 0.6365 | 0.60846 | 0.60883 | 0.70136
43602.6749 | 0.795 | 0.8854 | 0.81405 | 0.69846 | 0.63436 | 0.60762 | 0.6098 | 0.7008
43602.6749 | 0.80432 | 0.88332 | 0.81361 | 0.69845 | 0.63374 | 0.6074 | 0.6082 | 0.70061
43602.6748 | 0.79043 | 0.88395 | 0.81275 | 0.69812 | 0.63377 | 0.60679 | 0.60835 | 0.70026
43602.675 | 0.79924 | 0.8775 | 0.80834 | 0.69481 | 0.63049 | 0.60482 | 0.60718 | 0.69965
43602.6751 | 0.79061 | 0.87906 | 0.8089 | 0.6947 | 0.63064 | 0.60436 | 0.60427 | 0.69922
43602.675 | 0.77952 | 0.87631 | 0.80593 | 0.69255 | 0.62861 | 0.60341 | 0.60336 | 0.69864
43602.6752 | 0.78929 | 0.87428 | 0.80388 | 0.6913 | 0.62786 | 0.6026 | 0.60271 | 0.69832
43602.6752 | 0.79991 | 0.87522 | 0.80486 | 0.69228 | 0.62819 | 0.60245 | 0.60482 | 0.69799
43602.6752 | 0.7924 | 0.8715 | 0.80115 | 0.68884 | 0.62555 | 0.60103 | 0.6026 | 0.69751
43602.6754 | 0.80302 | 0.87042 | 0.80102 | 0.68937 | 0.62499 | 0.60003 | 0.60089 | 0.69668
43602.6754 | 0.81472 | 0.87259 | 0.80308 | 0.69064 | 0.62709 | 0.60105 | 0.60196 | 0.6971
43602.6754 | 0.80142 | 0.87226 | 0.80249 | 0.68953 | 0.62759 | 0.60112 | 0.60185 | 0.69659
43602.6756 | 0.80726 | 0.86618 | 0.79776 | 0.68589 | 0.62453 | 0.59962 | 0.60167 | 0.69642
43602.6756 | 0.81094 | 0.86825 | 0.79911 | 0.68691 | 0.62401 | 0.59926 | 0.59983 | 0.69636
43602.6756 | 0.80992 | 0.86543 | 0.79785 | 0.68479 | 0.62454 | 0.59935 | 0.59921 | 0.69594
43602.6758 | 0.82406 | 0.87099 | 0.8022 | 0.68837 | 0.62567 | 0.60074 | 0.60213 | 0.69589
43602.6758 | 0.8271 | 0.87203 | 0.80248 | 0.68847 | 0.62701 | 0.60136 | 0.60082 | 0.69593
43602.6758 | 0.82082 | 0.87605 | 0.80588 | 0.69186 | 0.62828 | 0.60224 | 0.60323 | 0.6965
43602.676 | 0.82805 | 0.87327 | 0.80346 | 0.68866 | 0.62827 | 0.6026 | 0.60203 | 0.69658
43602.676 | 0.81985 | 0.87377 | 0.80434 | 0.6898 | 0.62711 | 0.60208 | 0.60266 | 0.6963
43602.676 | 0.83231 | 0.88029 | 0.81003 | 0.69395 | 0.63056 | 0.60465 | 0.60514 | 0.69758
43602.6762 | 0.81371 | 0.87294 | 0.80561 | 0.69095 | 0.63099 | 0.60529 | 0.60524 | 0.69903
43602.6762 | 0.80365 | 0.87372 | 0.80542 | 0.6906 | 0.62896 | 0.60435 | 0.60442 | 0.69929
43602.6762 | 0.80635 | 0.87332 | 0.80475 | 0.69157 | 0.63055 | 0.60579 | 0.60618 | 0.70027
43602.6763 | 0.76701 | 0.87134 | 0.80191 | 0.69067 | 0.62863 | 0.60408 | 0.60517 | 0.70002
43602.6764 | 0.76841 | 0.8697 | 0.8004 | 0.68973 | 0.62736 | 0.60363 | 0.60644 | 0.70017
43602.6763 | 0.76407 | 0.86788 | 0.79809 | 0.68821 | 0.62612 | 0.60248 | 0.60355 | 0.69964
43602.6765 | 0.76115 | 0.86569 | 0.79687 | 0.68728 | 0.62479 | 0.60095 | 0.6036 | 0.69881
43602.6765 | 0.75514 | 0.86321 | 0.79471 | 0.68615 | 0.62393 | 0.6006 | 0.6019 | 0.69892
43602.6765 | 0.75131 | 0.86157 | 0.79267 | 0.68455 | 0.6215 | 0.59842 | 0.60025 | 0.69782
43602.6767 | 0.74554 | 0.86345 | 0.79463 | 0.68625 | 0.62076 | 0.59692 | 0.59904 | 0.69648
43602.6767 | 0.75509 | 0.86337 | 0.79442 | 0.68514 | 0.62055 | 0.59703 | 0.60034 | 0.69644
43602.6767 | 0.75284 | 0.86507 | 0.79595 | 0.68494 | 0.62042 | 0.5962 | 0.59771 | 0.69555
43602.6769 | 0.75513 | 0.86905 | 0.79993 | 0.68821 | 0.62192 | 0.59737 | 0.59767 | 0.69546
43602.6769 | 0.75702 | 0.87001 | 0.80099 | 0.68875 | 0.62226 | 0.59704 | 0.59983 | 0.6952
43602.6769 | 0.76671 | 0.87426 | 0.80405 | 0.69001 | 0.62429 | 0.5982 | 0.59911 | 0.69533
43602.6771 | 0.76202 | 0.87339 | 0.80241 | 0.68954 | 0.62407 | 0.59831 | 0.59889 | 0.69557
43602.6771 | 0.76155 | 0.87136 | 0.8017 | 0.68845 | 0.62365 | 0.59823 | 0.60171 | 0.69576
43602.6771 | 0.7635 | 0.87098 | 0.80132 | 0.68863 | 0.62319 | 0.59823 | 0.60087 | 0.69584
43602.6773 | 0.75649 | 0.86835 | 0.79856 | 0.68712 | 0.62218 | 0.5974 | 0.5992 | 0.69554
43602.6773 | 0.75206 | 0.86808 | 0.79844 | 0.68718 | 0.6221 | 0.59776 | 0.59906 | 0.6958
43602.6773 | 0.75384 | 0.87018 | 0.80017 | 0.68875 | 0.62254 | 0.5983 | 0.59892 | 0.69611
43602.6775 | 0.75519 | 0.87267 | 0.80287 | 0.68996 | 0.62501 | 0.59942 | 0.60106 | 0.69597
43602.6775 | 0.7588 | 0.87086 | 0.80133 | 0.6886 | 0.62376 | 0.59907 | 0.59928 | 0.69605
43602.6775 | 0.7666 | 0.87347 | 0.80271 | 0.69004 | 0.62455 | 0.59971 | 0.60025 | 0.69647
43602.6777 | 0.75192 | 0.87137 | 0.80135 | 0.68973 | 0.62448 | 0.60016 | 0.60179 | 0.69703
43602.6777 | 0.75886 | 0.87348 | 0.80269 | 0.68983 | 0.62453 | 0.59999 | 0.60009 | 0.69695
43602.6776 | 0.75377 | 0.86855 | 0.79882 | 0.68725 | 0.62322 | 0.5995 | 0.60029 | 0.69713
43602.6778 | 0.74769 | 0.86699 | 0.79822 | 0.68783 | 0.6224 | 0.59843 | 0.60008 | 0.69655
43602.6779 | 0.75053 | 0.86669 | 0.79785 | 0.68647 | 0.6222 | 0.59815 | 0.59888 | 0.69665
43602.6778 | 0.75796 | 0.86974 | 0.79981 | 0.68786 | 0.62332 | 0.59864 | 0.60007 | 0.69664
43602.678 | 0.76449 | 0.87349 | 0.80407 | 0.69087 | 0.62536 | 0.60075 | 0.603 | 0.69737
43602.678 | 0.75279 | 0.87289 | 0.8042 | 0.69144 | 0.62527 | 0.60032 | 0.60092 | 0.69728
43602.678 | 0.75587 | 0.87208 | 0.80275 | 0.68978 | 0.62437 | 0.59991 | 0.60058 | 0.6972
43602.6782 | 0.74986 | 0.8698 | 0.80186 | 0.6891 | 0.62448 | 0.59918 | 0.59999 | 0.69678
43602.6782 | 0.74912 | 0.86714 | 0.80002 | 0.68718 | 0.62319 | 0.59917 | 0.60254 | 0.69689
43602.6782 | 0.74919 | 0.8675 | 0.79842 | 0.6868 | 0.62251 | 0.59848 | 0.60113 | 0.69682
43602.6784 | 0.74543 | 0.866 | 0.79753 | 0.68692 | 0.62157 | 0.59818 | 0.59967 | 0.69678
43602.6784 | 0.74666 | 0.86582 | 0.79756 | 0.68654 | 0.6216 | 0.59754 | 0.59972 | 0.69637
43602.6784 | 0.74743 | 0.86487 | 0.79629 | 0.68507 | 0.621 | 0.59716 | 0.59788 | 0.69607
43602.6786 | 0.7442 | 0.86412 | 0.79572 | 0.68482 | 0.62059 | 0.59645 | 0.59933 | 0.69577
43602.6786 | 0.74549 | 0.86381 | 0.79537 | 0.68445 | 0.62009 | 0.59615 | 0.59749 | 0.69573
43602.6786 | 0.74874 | 0.86365 | 0.79431 | 0.6827 | 0.619 | 0.59592 | 0.59846 | 0.69535
43602.6788 | 0.74225 | 0.86406 | 0.7963 | 0.68523 | 0.61896 | 0.59491 | 0.59643 | 0.69467
43602.6788 | 0.74243 | 0.86464 | 0.79698 | 0.68461 | 0.61935 | 0.59488 | 0.59576 | 0.69425
43602.6788 | 0.74781 | 0.86965 | 0.80146 | 0.68674 | 0.62018 | 0.59506 | 0.5974 | 0.69381
43602.679 | 0.74797 | 0.87352 | 0.80741 | 0.69031 | 0.62173 | 0.59688 | 0.60031 | 0.69372
43602.679 | 0.7486 | 0.87437 | 0.80735 | 0.69123 | 0.62241 | 0.5968 | 0.59721 | 0.69382
43602.679 | 0.76249 | 0.88157 | 0.81217 | 0.69335 | 0.62537 | 0.59855 | 0.59918 | 0.6942
43602.6792 | 0.76502 | 0.88586 | 0.81622 | 0.69686 | 0.62729 | 0.60045 | 0.60103 | 0.69479
43602.6792 | 0.76244 | 0.88388 | 0.81411 | 0.69493 | 0.62678 | 0.60012 | 0.59954 | 0.69448
43602.6791 | 0.76552 | 0.88345 | 0.81485 | 0.69525 | 0.62702 | 0.60114 | 0.60113 | 0.69547
43602.6793 | 0.75736 | 0.88101 | 0.81371 | 0.69431 | 0.62662 | 0.6012 | 0.60182 | 0.69601
43602.6793 | 0.76397 | 0.88416 | 0.81422 | 0.69586 | 0.62748 | 0.60123 | 0.60152 | 0.69592
43602.6793 | 0.75489 | 0.88024 | 0.81238 | 0.69405 | 0.62601 | 0.60119 | 0.60249 | 0.69621
43602.6795 | 0.75526 | 0.87857 | 0.8098 | 0.69313 | 0.62535 | 0.6001 | 0.59996 | 0.69575
43602.6795 | 0.75759 | 0.87826 | 0.80962 | 0.69263 | 0.62574 | 0.60001 | 0.60221 | 0.69564
43602.6795 | 0.75734 | 0.87526 | 0.80753 | 0.69049 | 0.62381 | 0.59824 | 0.59947 | 0.6948
43602.6797 | 0.75317 | 0.87694 | 0.80964 | 0.69235 | 0.62425 | 0.59831 | 0.59921 | 0.69464
43602.6797 | 0.74997 | 0.8766 | 0.80921 | 0.69206 | 0.62413 | 0.59816 | 0.59781 | 0.69452
43602.6797 | 0.75594 | 0.87933 | 0.81061 | 0.69327 | 0.62471 | 0.59858 | 0.60002 | 0.69468
43602.6799 | 0.75906 | 0.87928 | 0.81113 | 0.69258 | 0.62436 | 0.59823 | 0.59911 | 0.69421
43602.6799 | 0.76527 | 0.88186 | 0.81171 | 0.69312 | 0.62499 | 0.59847 | 0.5985 | 0.69433
43602.6799 | 0.77297 | 0.88419 | 0.81343 | 0.69448 | 0.62584 | 0.59891 | 0.59908 | 0.69413
43602.6801 | 0.76947 | 0.88268 | 0.81317 | 0.69343 | 0.62564 | 0.59931 | 0.5994 | 0.69441
43602.6801 | 0.78716 | 0.88429 | 0.81408 | 0.69418 | 0.62598 | 0.59976 | 0.59977 | 0.6947
43602.6801 | 0.78525 | 0.88551 | 0.81593 | 0.69567 | 0.62815 | 0.60083 | 0.60055 | 0.69498
43602.6803 | 0.79403 | 0.88697 | 0.81682 | 0.69711 | 0.62957 | 0.60267 | 0.60341 | 0.6962
43602.6803 | 0.78121 | 0.88651 | 0.81699 | 0.69664 | 0.62969 | 0.60252 | 0.60218 | 0.69623
43602.6803 | 0.78187 | 0.88656 | 0.81478 | 0.69629 | 0.62933 | 0.60269 | 0.60327 | 0.69664
43602.6805 | 0.76112 | 0.87999 | 0.81085 | 0.69409 | 0.62691 | 0.60163 | 0.60192 | 0.69651
43602.6805 | 0.7651 | 0.87805 | 0.80902 | 0.69264 | 0.62653 | 0.60189 | 0.60438 | 0.69686
43602.6804 | 0.76898 | 0.87996 | 0.81014 | 0.69251 | 0.62618 | 0.6016 | 0.60127 | 0.69649
43602.6806 | 0.75881 | 0.87534 | 0.80609 | 0.69063 | 0.62491 | 0.60049 | 0.60125 | 0.69627
43602.6807 | 0.76496 | 0.87661 | 0.80689 | 0.69066 | 0.6246 | 0.60036 | 0.60022 | 0.69642
43602.6806 | 0.76497 | 0.87735 | 0.80803 | 0.69154 | 0.6253 | 0.60046 | 0.60303 | 0.69607
43602.6808 | 0.75663 | 0.87594 | 0.80725 | 0.69128 | 0.62404 | 0.59986 | 0.60123 | 0.69607
43602.6808 | 0.78601 | 0.88042 | 0.80944 | 0.69467 | 0.62619 | 0.60045 | 0.60095 | 0.69622
43602.6808 | 0.7601 | 0.87815 | 0.80897 | 0.69227 | 0.62595 | 0.60019 | 0.60206 | 0.696
43602.681 | 0.78924 | 0.89039 | 0.81803 | 0.69964 | 0.6311 | 0.60428 | 0.60425 | 0.69727
43602.681 | 0.7758 | 0.88401 | 0.81491 | 0.69564 | 0.62987 | 0.60311 | 0.60245 | 0.69639
43602.681 | 0.77983 | 0.88736 | 0.81681 | 0.69785 | 0.6304 | 0.60384 | 0.60345 | 0.69704
43602.6812 | 0.77029 | 0.8833 | 0.81437 | 0.69545 | 0.62959 | 0.60348 | 0.60332 | 0.69727
43602.6812 | 0.7716 | 0.88471 | 0.81514 | 0.69642 | 0.62904 | 0.6035 | 0.60485 | 0.69744
43602.6812 | 0.76645 | 0.88067 | 0.8111 | 0.69403 | 0.62728 | 0.60228 | 0.60235 | 0.69703
43602.6814 | 0.75656 | 0.87667 | 0.8079 | 0.69163 | 0.626 | 0.60104 | 0.60134 | 0.69673
43602.6814 | 0.75566 | 0.87607 | 0.80763 | 0.69088 | 0.6254 | 0.60067 | 0.60346 | 0.69657
43602.6814 | 0.75944 | 0.87889 | 0.80968 | 0.69351 | 0.62575 | 0.60019 | 0.60106 | 0.69625
43602.6816 | 0.75536 | 0.87733 | 0.8089 | 0.69272 | 0.62565 | 0.60054 | 0.60131 | 0.69632
43602.6816 | 0.76439 | 0.87784 | 0.80837 | 0.69258 | 0.62553 | 0.59986 | 0.60168 | 0.6962
43602.6816 | 0.75613 | 0.87589 | 0.80754 | 0.69115 | 0.62467 | 0.59976 | 0.601 | 0.69625
43602.6818 | 0.75192 | 0.87619 | 0.8076 | 0.69141 | 0.62492 | 0.5998 | 0.60238 | 0.69588
43602.6818 | 0.75996 | 0.87617 | 0.8072 | 0.69094 | 0.62455 | 0.59962 | 0.60017 | 0.69608
43602.6818 | 0.76461 | 0.88065 | 0.81002 | 0.69391 | 0.62572 | 0.60057 | 0.60362 | 0.69607
43602.682 | 0.76198 | 0.87885 | 0.80858 | 0.692 | 0.62554 | 0.60067 | 0.60087 | 0.69624
43602.682 | 0.75594 | 0.88014 | 0.81012 | 0.69336 | 0.62588 | 0.60097 | 0.60146 | 0.69617
43602.682 | 0.77167 | 0.88351 | 0.81278 | 0.69583 | 0.62789 | 0.60177 | 0.60223 | 0.69648
43602.6822 | 0.76641 | 0.88208 | 0.81141 | 0.69449 | 0.62694 | 0.60122 | 0.60194 | 0.69643
43602.6822 | 0.76393 | 0.87972 | 0.81033 | 0.69293 | 0.62654 | 0.60118 | 0.60199 | 0.69631
43602.6821 | 0.77574 | 0.88067 | 0.81166 | 0.69493 | 0.6278 | 0.60189 | 0.6015 | 0.69664
43602.6823 | 0.76234 | 0.87939 | 0.81013 | 0.69327 | 0.62609 | 0.60125 | 0.60221 | 0.69656
43602.6824 | 0.75926 | 0.87972 | 0.8103 | 0.69363 | 0.62686 | 0.60194 | 0.60178 | 0.69687
43602.6823 | 0.76252 | 0.88117 | 0.81071 | 0.69401 | 0.62774 | 0.60256 | 0.60437 | 0.69702
43602.6825 | 0.76277 | 0.88164 | 0.8128 | 0.6948 | 0.62881 | 0.60286 | 0.60261 | 0.69696
43602.6826 | 0.76771 | 0.87971 | 0.81112 | 0.69269 | 0.6274 | 0.6025 | 0.60394 | 0.69716
43602.6825 | 0.77608 | 0.88687 | 0.81642 | 0.69797 | 0.63058 | 0.6044 | 0.60404 | 0.69748
43602.6827 | 0.78001 | 0.89222 | 0.82096 | 0.70099 | 0.63199 | 0.60601 | 0.60701 | 0.69842
43602.6827 | 0.79457 | 0.89524 | 0.82198 | 0.70296 | 0.63421 | 0.60673 | 0.60581 | 0.69851
43602.6827 | 0.77328 | 0.89223 | 0.82152 | 0.70159 | 0.63334 | 0.6065 | 0.60576 | 0.69847
43602.6829 | 0.77393 | 0.88894 | 0.81997 | 0.69896 | 0.63244 | 0.60627 | 0.60702 | 0.69888
43602.6829 | 0.77036 | 0.88953 | 0.82019 | 0.69954 | 0.63232 | 0.60664 | 0.6062 | 0.69918
43602.6829 | 0.78175 | 0.89588 | 0.82537 | 0.70396 | 0.63517 | 0.60812 | 0.60806 | 0.69965
43602.6831 | 0.77187 | 0.89311 | 0.82358 | 0.70253 | 0.63432 | 0.60786 | 0.60703 | 0.69941
43602.6831 | 0.76163 | 0.8901 | 0.82214 | 0.70096 | 0.63342 | 0.60723 | 0.60947 | 0.69939
43602.6831 | 0.76207 | 0.88775 | 0.82054 | 0.69998 | 0.63294 | 0.6072 | 0.60757 | 0.69938
43602.6833 | 0.7712 | 0.89044 | 0.82241 | 0.70161 | 0.63402 | 0.60776 | 0.60855 | 0.69975
43602.6833 | 0.76195 | 0.89116 | 0.82296 | 0.70233 | 0.63368 | 0.60759 | 0.60694 | 0.6995
43602.6833 | 0.76243 | 0.88763 | 0.81991 | 0.69946 | 0.63281 | 0.60725 | 0.60723 | 0.69988
43602.6835 | 0.7606 | 0.88735 | 0.82012 | 0.69938 | 0.63276 | 0.60728 | 0.60769 | 0.6999
43602.6835 | 0.7602 | 0.88663 | 0.81991 | 0.69913 | 0.63232 | 0.60684 | 0.60697 | 0.69954
43602.6835 | 0.75908 | 0.88548 | 0.8199 | 0.69977 | 0.63218 | 0.6068 | 0.60697 | 0.69958
43602.6837 | 0.7513 | 0.88514 | 0.82017 | 0.70028 | 0.6319 | 0.60626 | 0.60733 | 0.69926
43602.6837 | 0.75599 | 0.88499 | 0.81905 | 0.69925 | 0.6321 | 0.6063 | 0.60613 | 0.69941
43602.6837 | 0.76228 | 0.8871 | 0.82033 | 0.69951 | 0.63241 | 0.60637 | 0.6052 | 0.69927
43602.6839 | 0.75573 | 0.88369 | 0.81785 | 0.69782 | 0.63074 | 0.60536 | 0.60751 | 0.69894
43602.6839 | 0.75647 | 0.8846 | 0.81809 | 0.69789 | 0.63017 | 0.60438 | 0.60451 | 0.69846
43602.6839 | 0.75584 | 0.88668 | 0.82056 | 0.69936 | 0.6307 | 0.60428 | 0.60369 | 0.69795
43602.6841 | 0.76212 | 0.89249 | 0.82652 | 0.70225 | 0.63217 | 0.6045 | 0.6037 | 0.69702
43602.6841 | 0.75809 | 0.89159 | 0.82649 | 0.70219 | 0.63187 | 0.60429 | 0.60385 | 0.69676
43602.684 | 0.77233 | 0.89541 | 0.83 | 0.70378 | 0.63286 | 0.60503 | 0.60683 | 0.69702
43602.6842 | 0.76428 | 0.9013 | 0.83554 | 0.70721 | 0.63527 | 0.60684 | 0.60656 | 0.69745
43602.6843 | 0.77381 | 0.90468 | 0.83758 | 0.70847 | 0.6364 | 0.60774 | 0.60625 | 0.69772
43602.6842 | 0.79404 | 0.91383 | 0.84457 | 0.71381 | 0.64077 | 0.61116 | 0.60871 | 0.69871
43602.6844 | 0.81593 | 0.92466 | 0.85231 | 0.72039 | 0.64572 | 0.61511 | 0.61434 | 0.70039
43602.6844 | 0.8046 | 0.92068 | 0.85066 | 0.71835 | 0.64778 | 0.61616 | 0.61362 | 0.70046
43602.6844 | 0.79372 | 0.91991 | 0.85198 | 0.72002 | 0.64858 | 0.61766 | 0.61539 | 0.70225
43602.6846 | 0.78465 | 0.91159 | 0.84569 | 0.71596 | 0.64548 | 0.6172 | 0.61625 | 0.70347
43602.6846 | 0.78497 | 0.91274 | 0.8466 | 0.71655 | 0.64672 | 0.61776 | 0.61755 | 0.70378
43602.6846 | 0.77121 | 0.90485 | 0.84094 | 0.71318 | 0.64397 | 0.61657 | 0.61481 | 0.70374
43602.6848 | 0.76793 | 0.90165 | 0.83665 | 0.71051 | 0.64129 | 0.61398 | 0.61341 | 0.70281
43602.6848 | 0.76789 | 0.90072 | 0.83507 | 0.70946 | 0.64073 | 0.61346 | 0.61348 | 0.70224
43602.6848 | 0.75836 | 0.8917 | 0.82827 | 0.70342 | 0.63624 | 0.61013 | 0.60938 | 0.70096
43602.685 | 0.76012 | 0.89106 | 0.82707 | 0.70225 | 0.63311 | 0.60621 | 0.60747 | 0.69831
43602.685 | 0.75872 | 0.89163 | 0.82771 | 0.70194 | 0.63225 | 0.60527 | 0.6054 | 0.69786
43602.685 | 0.75573 | 0.89281 | 0.82887 | 0.70155 | 0.63048 | 0.60349 | 0.60274 | 0.69631
43602.6852 | 0.76911 | 0.90174 | 0.83686 | 0.70598 | 0.63191 | 0.60281 | 0.60138 | 0.69421
43602.6852 | 0.78198 | 0.9078 | 0.84052 | 0.70874 | 0.6341 | 0.60392 | 0.60591 | 0.69448
43602.6852 | 0.80049 | 0.9139 | 0.84392 | 0.71117 | 0.63572 | 0.60484 | 0.60385 | 0.69401
43602.6854 | 0.8221 | 0.92505 | 0.85095 | 0.71544 | 0.64301 | 0.61015 | 0.60738 | 0.69423
43602.6854 | 0.83156 | 0.92766 | 0.8512 | 0.71579 | 0.64085 | 0.60884 | 0.60737 | 0.69408
43602.6854 | 0.8402 | 0.92833 | 0.85397 | 0.71589 | 0.64347 | 0.61086 | 0.60834 | 0.69334
43602.6856 | 0.85837 | 0.93236 | 0.85599 | 0.71862 | 0.6459 | 0.61348 | 0.61059 | 0.69498
43602.6856 | 0.8646 | 0.93192 | 0.85611 | 0.71838 | 0.64713 | 0.61432 | 0.61093 | 0.69528
43602.6856 | 0.85626 | 0.93798 | 0.86021 | 0.72303 | 0.64954 | 0.617 | 0.61547 | 0.69782
43602.6858 | 0.82333 | 0.9266 | 0.85344 | 0.71916 | 0.64787 | 0.61659 | 0.6162 | 0.69933
43602.6858 | 0.84866 | 0.931 | 0.85659 | 0.72181 | 0.64963 | 0.61781 | 0.61609 | 0.70028
43602.6858 | 0.82984 | 0.92797 | 0.85522 | 0.72104 | 0.65056 | 0.61876 | 0.6163 | 0.70151
43602.686 | 0.791 | 0.918 | 0.84907 | 0.71776 | 0.64663 | 0.61719 | 0.61572 | 0.70253
43602.686 | 0.79404 | 0.9184 | 0.8487 | 0.71766 | 0.64689 | 0.61708 | 0.6152 | 0.70252
43602.686 | 0.77883 | 0.90789 | 0.84165 | 0.71237 | 0.6423 | 0.61445 | 0.61307 | 0.70231
43602.6862 | 0.77315 | 0.90361 | 0.83721 | 0.71009 | 0.64022 | 0.61244 | 0.61146 | 0.70153
43602.6862 | 0.77529 | 0.90599 | 0.83813 | 0.71136 | 0.64049 | 0.6124 | 0.61346 | 0.70144
43602.6861 | 0.76485 | 0.89813 | 0.83284 | 0.70706 | 0.6375 | 0.61025 | 0.60961 | 0.70039
43602.6863 | 0.76605 | 0.89711 | 0.83142 | 0.70687 | 0.63614 | 0.60849 | 0.60912 | 0.69972
43602.6864 | 0.76076 | 0.89566 | 0.83076 | 0.70559 | 0.63583 | 0.60838 | 0.60747 | 0.69947
43602.6863 | 0.7607 | 0.89601 | 0.83014 | 0.70538 | 0.63565 | 0.60829 | 0.60774 | 0.69947
43602.6865 | 0.76348 | 0.89549 | 0.83 | 0.70438 | 0.63464 | 0.60792 | 0.60826 | 0.69934
43602.6865 | 0.76309 | 0.8958 | 0.83016 | 0.7049 | 0.63531 | 0.60842 | 0.60924 | 0.69949
43602.6865 | 0.75909 | 0.89406 | 0.82903 | 0.70337 | 0.63396 | 0.60733 | 0.60623 | 0.69898
43602.6867 | 0.76068 | 0.89401 | 0.82843 | 0.70356 | 0.63358 | 0.60561 | 0.60543 | 0.69771
43602.6867 | 0.76228 | 0.89366 | 0.82768 | 0.7023 | 0.63281 | 0.60547 | 0.60599 | 0.69752
43602.6867 | 0.7624 | 0.89233 | 0.82598 | 0.7009 | 0.63153 | 0.60426 | 0.60475 | 0.69651
43602.6869 | 0.7585 | 0.89267 | 0.82721 | 0.70124 | 0.63029 | 0.60318 | 0.60327 | 0.69604
43602.6869 | 0.76229 | 0.89371 | 0.8271 | 0.70144 | 0.63053 | 0.60304 | 0.60255 | 0.69587
43602.6869 | 0.76857 | 0.89515 | 0.82774 | 0.70091 | 0.63023 | 0.60253 | 0.60172 | 0.69514
43602.6871 | 0.78925 | 0.90787 | 0.83727 | 0.70807 | 0.6344 | 0.60523 | 0.60355 | 0.69565
43602.6871 | 0.7916 | 0.90777 | 0.83717 | 0.70802 | 0.63537 | 0.60556 | 0.60524 | 0.69551
43602.6871 | 0.81938 | 0.9164 | 0.84217 | 0.71179 | 0.63856 | 0.6083 | 0.60687 | 0.6967
43602.6873 | 0.79953 | 0.91238 | 0.84149 | 0.71027 | 0.64096 | 0.61052 | 0.6097 | 0.69696
43602.6873 | 0.83564 | 0.92132 | 0.84534 | 0.71445 | 0.64068 | 0.61088 | 0.60921 | 0.69753
43602.6873 | 0.81158 | 0.91337 | 0.84139 | 0.71205 | 0.64143 | 0.61179 | 0.6107 | 0.6991
43602.6875 | 0.7955 | 0.90924 | 0.83989 | 0.71155 | 0.64097 | 0.61222 | 0.61183 | 0.70024
43602.6875 | 0.80363 | 0.91277 | 0.84008 | 0.71306 | 0.64226 | 0.61289 | 0.61233 | 0.70048
43602.6875 | 0.78779 | 0.90857 | 0.83833 | 0.71131 | 0.64193 | 0.61216 | 0.61114 | 0.7005
43602.6877 | 0.76734 | 0.89787 | 0.83066 | 0.70543 | 0.63655 | 0.6092 | 0.60965 | 0.69982
43602.6877 | 0.76835 | 0.89625 | 0.82932 | 0.70429 | 0.63616 | 0.60936 | 0.60933 | 0.69995
43602.6877 | 0.77503 | 0.89677 | 0.82897 | 0.7043 | 0.63486 | 0.60765 | 0.60766 | 0.69919
43602.6879 | 0.76535 | 0.89383 | 0.8262 | 0.70213 | 0.63323 | 0.6067 | 0.60652 | 0.69849
43602.6879 | 0.7692 | 0.8944 | 0.82653 | 0.70228 | 0.63292 | 0.60618 | 0.60513 | 0.69807
43602.6879 | 0.76449 | 0.89419 | 0.82625 | 0.70202 | 0.63215 | 0.60497 | 0.60534 | 0.69742
43602.6881 | 0.76132 | 0.89328 | 0.82626 | 0.70177 | 0.63127 | 0.60358 | 0.6033 | 0.69665
43602.6881 | 0.77401 | 0.89517 | 0.82696 | 0.70273 | 0.63144 | 0.6042 | 0.60376 | 0.69664
43602.6881 | 0.77543 | 0.89638 | 0.82663 | 0.70215 | 0.63154 | 0.6042 | 0.60315 | 0.69637
43602.6883 | 0.77414 | 0.89543 | 0.82564 | 0.70133 | 0.63108 | 0.6041 | 0.60414 | 0.69613
43602.6883 | 0.77884 | 0.89655 | 0.82609 | 0.70194 | 0.63181 | 0.60434 | 0.60355 | 0.69624
43602.6883 | 0.7907 | 0.90024 | 0.82791 | 0.70334 | 0.63265 | 0.60462 | 0.60354 | 0.69583
43602.6885 | 0.82041 | 0.90748 | 0.83166 | 0.70644 | 0.63353 | 0.60551 | 0.60553 | 0.69635
43602.6885 | 0.82203 | 0.90855 | 0.83365 | 0.7071 | 0.63609 | 0.60679 | 0.60568 | 0.69623
43602.6885 | 0.8217 | 0.90624 | 0.83382 | 0.70607 | 0.63695 | 0.60757 | 0.60743 | 0.69632
43602.6887 | 0.84093 | 0.90948 | 0.8352 | 0.70731 | 0.63601 | 0.60742 | 0.60616 | 0.6963
43602.6887 | 0.81874 | 0.90905 | 0.83635 | 0.70745 | 0.63842 | 0.60896 | 0.60764 | 0.69635
43602.6886 | 0.8333 | 0.90678 | 0.83368 | 0.70632 | 0.63658 | 0.60749 | 0.60729 | 0.69667
43602.6889 | 0.82599 | 0.90739 | 0.83379 | 0.7072 | 0.63628 | 0.60782 | 0.60661 | 0.69701
43602.6889 | 0.80244 | 0.90314 | 0.83209 | 0.70445 | 0.63632 | 0.60724 | 0.60576 | 0.69658
43602.6888 | 0.80637 | 0.90204 | 0.82904 | 0.70361 | 0.63398 | 0.60615 | 0.60553 | 0.69613
43602.689 | 0.80079 | 0.8982 | 0.82588 | 0.70117 | 0.63173 | 0.60445 | 0.6036 | 0.6959
43602.6891 | 0.79579 | 0.89689 | 0.82459 | 0.70003 | 0.6316 | 0.60404 | 0.60327 | 0.69557
43602.689 | 0.79476 | 0.89578 | 0.82356 | 0.69923 | 0.63137 | 0.60382 | 0.60317 | 0.69535
43602.6892 | 0.82305 | 0.89927 | 0.82498 | 0.70137 | 0.6309 | 0.6034 | 0.60411 | 0.69552
43602.6892 | 0.80211 | 0.89538 | 0.82338 | 0.69913 | 0.63125 | 0.60355 | 0.60238 | 0.69472
43602.6892 | 0.82066 | 0.89721 | 0.82345 | 0.69986 | 0.63097 | 0.60352 | 0.60298 | 0.69507
43602.6894 | 0.82546 | 0.89635 | 0.82283 | 0.69856 | 0.63058 | 0.60315 | 0.60344 | 0.69427
43602.6894 | 0.83661 | 0.90441 | 0.82956 | 0.7036 | 0.63368 | 0.60531 | 0.60411 | 0.69465
43602.6894 | 0.81463 | 0.89296 | 0.82162 | 0.69718 | 0.63041 | 0.60302 | 0.60206 | 0.6939
43602.6896 | 0.82643 | 0.88924 | 0.81851 | 0.69464 | 0.6294 | 0.60193 | 0.602 | 0.69331
43602.6896 | 0.84235 | 0.89324 | 0.82135 | 0.6973 | 0.62831 | 0.6013 | 0.6004 | 0.69339
43602.6896 | 0.8353 | 0.89565 | 0.82268 | 0.69849 | 0.63115 | 0.60303 | 0.60176 | 0.69352
43602.6898 | 0.8288 | 0.89141 | 0.81976 | 0.69573 | 0.62886 | 0.60183 | 0.60232 | 0.69325
43602.6898 | 0.82945 | 0.89332 | 0.82125 | 0.69718 | 0.62981 | 0.60283 | 0.60284 | 0.69362
43602.6898 | 0.84541 | 0.89703 | 0.82388 | 0.69932 | 0.6308 | 0.60341 | 0.60294 | 0.69365
43602.69 | 0.83751 | 0.90312 | 0.82878 | 0.70331 | 0.63566 | 0.60754 | 0.60532 | 0.69505
43602.69 | 0.84492 | 0.90499 | 0.82963 | 0.70418 | 0.63491 | 0.60697 | 0.60483 | 0.69467
43602.69 | 0.83556 | 0.8961 | 0.82356 | 0.69912 | 0.63297 | 0.60559 | 0.60615 | 0.69534
43602.6902 | 0.83181 | 0.89626 | 0.8242 | 0.7023 | 0.63462 | 0.60745 | 0.60656 | 0.69788
43602.6902 | 0.82413 | 0.89506 | 0.82334 | 0.70139 | 0.63468 | 0.60739 | 0.60872 | 0.69795
43602.6902 | 0.79738 | 0.88868 | 0.81739 | 0.69763 | 0.63151 | 0.60578 | 0.60545 | 0.6981
43602.6904 | 0.76785 | 0.88123 | 0.81061 | 0.69297 | 0.62719 | 0.60272 | 0.60547 | 0.69739
43602.6904 | 0.7752 | 0.88183 | 0.81047 | 0.69427 | 0.6273 | 0.60302 | 0.60302 | 0.69764
43602.6904 | 0.77123 | 0.87684 | 0.8066 | 0.69126 | 0.62489 | 0.60026 | 0.60092 | 0.69604
43602.6906 | 0.76059 | 0.87373 | 0.8033 | 0.68904 | 0.62252 | 0.59841 | 0.60096 | 0.69521
43602.6906 | 0.75619 | 0.87277 | 0.80313 | 0.68843 | 0.62188 | 0.59801 | 0.59907 | 0.69497
43602.6906 | 0.78384 | 0.8782 | 0.80617 | 0.69155 | 0.6236 | 0.59824 | 0.59875 | 0.69422
43602.6908 | 0.78962 | 0.87944 | 0.80768 | 0.69153 | 0.62459 | 0.59879 | 0.59915 | 0.69431
43602.6908 | 0.80067 | 0.87955 | 0.80812 | 0.6921 | 0.62438 | 0.59937 | 0.6011 | 0.6945
43602.6908 | 0.80692 | 0.87806 | 0.80804 | 0.6914 | 0.62588 | 0.60036 | 0.60044 | 0.69502
43602.691 | 0.81399 | 0.88094 | 0.80985 | 0.69298 | 0.62767 | 0.60193 | 0.602 | 0.69565
43602.691 | 0.81425 | 0.88031 | 0.80919 | 0.69255 | 0.62726 | 0.60189 | 0.6031 | 0.69568
43602.691 | 0.79738 | 0.87704 | 0.80607 | 0.69087 | 0.62544 | 0.60101 | 0.60134 | 0.69621
43602.6912 | 0.78972 | 0.87529 | 0.80416 | 0.68989 | 0.62494 | 0.60125 | 0.60369 | 0.697
43602.6912 | 0.79417 | 0.87604 | 0.80514 | 0.69128 | 0.62548 | 0.60134 | 0.60315 | 0.69683
43602.6911 | 0.77954 | 0.87557 | 0.80464 | 0.69068 | 0.62568 | 0.60229 | 0.60285 | 0.6975
43602.6913 | 0.78065 | 0.87514 | 0.80482 | 0.6911 | 0.6266 | 0.60296 | 0.6049 | 0.69824
43602.6914 | 0.78335 | 0.87513 | 0.8054 | 0.69213 | 0.62624 | 0.60234 | 0.60309 | 0.69806
43602.6913 | 0.7758 | 0.87358 | 0.80298 | 0.69051 | 0.62612 | 0.60288 | 0.60556 | 0.6985
43602.6915 | 0.76034 | 0.86602 | 0.79675 | 0.68799 | 0.62342 | 0.60063 | 0.60213 | 0.69808
43602.6916 | 0.76283 | 0.86513 | 0.79503 | 0.68623 | 0.62244 | 0.6 | 0.602 | 0.69789
43602.6915 | 0.74936 | 0.85715 | 0.78755 | 0.68095 | 0.61818 | 0.5971 | 0.59855 | 0.69698
43602.6917 | 0.74324 | 0.85159 | 0.78337 | 0.67756 | 0.61422 | 0.5932 | 0.59526 | 0.69499
43602.6917 | 0.74146 | 0.85106 | 0.78277 | 0.67735 | 0.61353 | 0.59294 | 0.595 | 0.69509
43602.6917 | 0.7583 | 0.85485 | 0.7859 | 0.68 | 0.61416 | 0.59173 | 0.59418 | 0.69344
43602.6919 | 0.76561 | 0.86056 | 0.79074 | 0.68222 | 0.61468 | 0.59197 | 0.59536 | 0.69248
43602.6919 | 0.75722 | 0.86309 | 0.79254 | 0.68338 | 0.61539 | 0.59157 | 0.59278 | 0.69205
43602.6919 | 0.77081 | 0.8687 | 0.79803 | 0.68643 | 0.61879 | 0.59478 | 0.59509 | 0.69266
43602.6921 | 0.79292 | 0.86996 | 0.80005 | 0.68715 | 0.62119 | 0.59757 | 0.59865 | 0.69401
43602.6921 | 0.82743 | 0.87442 | 0.80426 | 0.69078 | 0.62263 | 0.5985 | 0.6 | 0.69453
43602.6921 | 0.79451 | 0.86938 | 0.80051 | 0.68734 | 0.62241 | 0.59891 | 0.59975 | 0.69514
43602.6923 | 0.77721 | 0.86621 | 0.79678 | 0.68539 | 0.62122 | 0.5982 | 0.59896 | 0.69534
43602.6923 | 0.7798 | 0.86391 | 0.79541 | 0.68448 | 0.62044 | 0.59809 | 0.59947 | 0.69553
43602.6923 | 0.76564 | 0.86255 | 0.79257 | 0.68259 | 0.61942 | 0.59702 | 0.59803 | 0.69555
43602.6925 | 0.76221 | 0.85884 | 0.79035 | 0.68172 | 0.61822 | 0.59629 | 0.59746 | 0.69549
43602.6925 | 0.76468 | 0.8596 | 0.78987 | 0.68154 | 0.61773 | 0.59628 | 0.59693 | 0.69543
43602.6925 | 0.76147 | 0.86268 | 0.79161 | 0.68316 | 0.61832 | 0.59601 | 0.60035 | 0.69508
43602.6927 | 0.75759 | 0.8602 | 0.79027 | 0.68234 | 0.61812 | 0.59635 | 0.59825 | 0.69551
43602.6927 | 0.75934 | 0.85842 | 0.7894 | 0.68143 | 0.61737 | 0.59554 | 0.59694 | 0.69506
43602.6927 | 0.76077 | 0.86206 | 0.79242 | 0.68358 | 0.61859 | 0.59648 | 0.59781 | 0.69523
43602.6929 | 0.76205 | 0.85862 | 0.79062 | 0.681 | 0.61859 | 0.59645 | 0.60052 | 0.69534
43602.6929 | 0.76215 | 0.85577 | 0.78878 | 0.67986 | 0.61727 | 0.59633 | 0.59873 | 0.69599
43602.6929 | 0.76158 | 0.86042 | 0.7905 | 0.68304 | 0.61814 | 0.59688 | 0.59779 | 0.69595
43602.6931 | 0.76897 | 0.86123 | 0.79132 | 0.68395 | 0.61882 | 0.59673 | 0.59842 | 0.69582
43602.6931 | 0.7585 | 0.86156 | 0.79181 | 0.68363 | 0.61829 | 0.59595 | 0.59775 | 0.69513
43602.6931 | 0.754 | 0.85956 | 0.79046 | 0.68195 | 0.61761 | 0.59586 | 0.59718 | 0.69531
43602.6933 | 0.75132 | 0.85871 | 0.78964 | 0.6817 | 0.61747 | 0.59602 | 0.59774 | 0.69535
43602.6933 | 0.74706 | 0.85789 | 0.78937 | 0.68173 | 0.61701 | 0.59589 | 0.59765 | 0.69539
43602.6933 | 0.75566 | 0.85676 | 0.78817 | 0.68068 | 0.61681 | 0.59549 | 0.59674 | 0.69517
43602.6935 | 0.74357 | 0.85213 | 0.78502 | 0.679 | 0.61493 | 0.59408 | 0.59754 | 0.69476
43602.6935 | 0.75079 | 0.8517 | 0.78393 | 0.67707 | 0.61457 | 0.59422 | 0.59656 | 0.69491
43602.6935 | 0.74675 | 0.85083 | 0.78265 | 0.67729 | 0.61359 | 0.59323 | 0.59508 | 0.69447
43602.6937 | 0.74543 | 0.84923 | 0.78206 | 0.67706 | 0.6131 | 0.59279 | 0.59471 | 0.69439
43602.6937 | 0.7483 | 0.84783 | 0.78113 | 0.67646 | 0.61324 | 0.59239 | 0.59607 | 0.69406
43602.6937 | 0.75215 | 0.84923 | 0.78248 | 0.67695 | 0.61323 | 0.59275 | 0.59462 | 0.69392
43602.6939 | 0.75222 | 0.85324 | 0.78428 | 0.67864 | 0.61404 | 0.59287 | 0.59674 | 0.69405
43602.6939 | 0.74851 | 0.8541 | 0.78522 | 0.67943 | 0.61421 | 0.59289 | 0.59513 | 0.69386
43602.6939 | 0.75876 | 0.85464 | 0.78652 | 0.67906 | 0.61498 | 0.59379 | 0.59505 | 0.69384
43602.6941 | 0.76842 | 0.86016 | 0.79123 | 0.68292 | 0.61808 | 0.59572 | 0.59776 | 0.69457
43602.6941 | 0.77014 | 0.86025 | 0.79173 | 0.68254 | 0.61778 | 0.5955 | 0.59713 | 0.69438
43602.6941 | 0.7921 | 0.86896 | 0.79992 | 0.68804 | 0.62368 | 0.59971 | 0.59978 | 0.69555
43602.6943 | 0.78328 | 0.86949 | 0.80082 | 0.6881 | 0.62352 | 0.60002 | 0.60112 | 0.69598
43602.6943 | 0.77582 | 0.86792 | 0.79898 | 0.68706 | 0.62261 | 0.59978 | 0.60114 | 0.69632
43602.6943 | 0.77485 | 0.86304 | 0.79669 | 0.68566 | 0.62123 | 0.59883 | 0.6006 | 0.69658
43602.6945 | 0.7559 | 0.86647 | 0.79829 | 0.68723 | 0.62186 | 0.59958 | 0.60086 | 0.69675
43602.6945 | 0.76432 | 0.86618 | 0.79849 | 0.6864 | 0.62153 | 0.5992 | 0.60002 | 0.69669
43602.6945 | 0.75992 | 0.87131 | 0.80235 | 0.69006 | 0.62399 | 0.60032 | 0.60159 | 0.69651
43602.6947 | 0.75658 | 0.8673 | 0.79945 | 0.68763 | 0.62221 | 0.59983 | 0.60092 | 0.69709
43602.6947 | 0.75635 | 0.86915 | 0.80078 | 0.68798 | 0.62245 | 0.59995 | 0.60165 | 0.69695
43602.6947 | 0.75324 | 0.86334 | 0.79586 | 0.6854 | 0.62098 | 0.59881 | 0.60013 | 0.69687
43602.6949 | 0.75108 | 0.86041 | 0.79315 | 0.68358 | 0.61871 | 0.59717 | 0.59852 | 0.69622
43602.6949 | 0.75232 | 0.85906 | 0.79279 | 0.68373 | 0.61883 | 0.59726 | 0.59872 | 0.69635
43602.6949 | 0.74751 | 0.85612 | 0.78883 | 0.6808 | 0.61735 | 0.59596 | 0.5979 | 0.69586
43602.6951 | 0.74265 | 0.85351 | 0.78666 | 0.67936 | 0.61516 | 0.59437 | 0.59632 | 0.69515
43602.6951 | 0.74589 | 0.85348 | 0.78624 | 0.67957 | 0.61546 | 0.59428 | 0.59693 | 0.6952
43602.6951 | 0.74037 | 0.85254 | 0.78656 | 0.67932 | 0.61466 | 0.59403 | 0.59562 | 0.69483
43602.6953 | 0.74256 | 0.85236 | 0.78571 | 0.67827 | 0.61355 | 0.59262 | 0.59437 | 0.69383
43602.6953 | 0.74639 | 0.85281 | 0.78532 | 0.67791 | 0.61321 | 0.59237 | 0.59665 | 0.69367
43602.6953 | 0.74157 | 0.85505 | 0.78872 | 0.67966 | 0.61323 | 0.59151 | 0.59357 | 0.69264
43602.6955 | 0.74342 | 0.86129 | 0.79384 | 0.68252 | 0.61546 | 0.5923 | 0.59348 | 0.69229
43602.6955 | 0.7459 | 0.86049 | 0.79325 | 0.68196 | 0.61567 | 0.59294 | 0.5941 | 0.69223
43602.6955 | 0.7666 | 0.87135 | 0.80283 | 0.68999 | 0.62056 | 0.5955 | 0.5967 | 0.69293
43602.6957 | 0.76265 | 0.8744 | 0.80544 | 0.69115 | 0.62211 | 0.59804 | 0.59951 | 0.69455
43602.6957 | 0.76853 | 0.8777 | 0.80831 | 0.69298 | 0.62445 | 0.59914 | 0.5995 | 0.69445
43602.6957 | 0.75456 | 0.87317 | 0.80566 | 0.69095 | 0.62439 | 0.60027 | 0.60018 | 0.69545
43602.6959 | 0.76294 | 0.86963 | 0.8026 | 0.68835 | 0.62411 | 0.60087 | 0.60192 | 0.6967
43602.6959 | 0.76166 | 0.87063 | 0.80368 | 0.69049 | 0.62441 | 0.60125 | 0.6012 | 0.69722
43602.6959 | 0.76135 | 0.87014 | 0.80245 | 0.69018 | 0.62476 | 0.60097 | 0.60139 | 0.69719
43602.6961 | 0.75389 | 0.86317 | 0.79683 | 0.68596 | 0.62215 | 0.60002 | 0.60201 | 0.69722
43602.6961 | 0.75409 | 0.86224 | 0.79586 | 0.68537 | 0.62148 | 0.59929 | 0.60052 | 0.69695
43602.6961 | 0.74829 | 0.86037 | 0.79422 | 0.68448 | 0.62059 | 0.59811 | 0.59895 | 0.69643
43602.6963 | 0.74773 | 0.86094 | 0.79358 | 0.68373 | 0.61886 | 0.5968 | 0.59904 | 0.6956
43602.6963 | 0.74785 | 0.85978 | 0.79331 | 0.68407 | 0.61904 | 0.59652 | 0.5982 | 0.69555
43602.6962 | 0.74369 | 0.85953 | 0.7944 | 0.68374 | 0.61777 | 0.59506 | 0.59568 | 0.69434
43602.6965 | 0.74818 | 0.86367 | 0.7962 | 0.68469 | 0.61901 | 0.59532 | 0.59722 | 0.69376
43602.6965 | 0.75039 | 0.86524 | 0.7975 | 0.68501 | 0.61877 | 0.59526 | 0.59683 | 0.6938
43602.6964 | 0.77341 | 0.87187 | 0.80326 | 0.6903 | 0.62133 | 0.59674 | 0.59766 | 0.69366
43602.6967 | 0.76155 | 0.87355 | 0.8059 | 0.69014 | 0.62294 | 0.59787 | 0.59873 | 0.69388
43602.6967 | 0.7736 | 0.8747 | 0.80663 | 0.69141 | 0.62313 | 0.59819 | 0.59855 | 0.69405
43602.6967 | 0.7988 | 0.8808 | 0.81182 | 0.69384 | 0.62625 | 0.6005 | 0.6003 | 0.69464
43602.6969 | 0.81054 | 0.89174 | 0.82129 | 0.70003 | 0.63308 | 0.60537 | 0.60645 | 0.69619
43602.6969 | 0.84798 | 0.89737 | 0.82704 | 0.70516 | 0.63425 | 0.60658 | 0.60548 | 0.69623
43602.6969 | 0.84486 | 0.89849 | 0.82828 | 0.70424 | 0.63667 | 0.60796 | 0.60846 | 0.69675
43602.6971 | 0.82914 | 0.89711 | 0.8278 | 0.70437 | 0.63538 | 0.60864 | 0.6095 | 0.69811
43602.6971 | 0.83502 | 0.89834 | 0.82848 | 0.70514 | 0.63881 | 0.61019 | 0.60917 | 0.6987
43602.6971 | 0.82129 | 0.89596 | 0.8272 | 0.7046 | 0.63669 | 0.60907 | 0.6099 | 0.69911
43602.6973 | 0.78314 | 0.89196 | 0.82394 | 0.70189 | 0.63558 | 0.60911 | 0.61024 | 0.69984
43602.6973 | 0.80222 | 0.8959 | 0.8254 | 0.70506 | 0.63613 | 0.60962 | 0.60873 | 0.70036
43602.6973 | 0.78596 | 0.89503 | 0.8254 | 0.70524 | 0.63685 | 0.60959 | 0.60908 | 0.7
43602.6975 | 0.77504 | 0.88821 | 0.82108 | 0.70164 | 0.6344 | 0.60798 | 0.60874 | 0.69948
43602.6975 | 0.76466 | 0.88719 | 0.81929 | 0.70067 | 0.63385 | 0.60747 | 0.60694 | 0.6996
43602.6975 | 0.77181 | 0.88495 | 0.81826 | 0.69865 | 0.63117 | 0.60579 | 0.60611 | 0.69892
43602.6977 | 0.77029 | 0.88677 | 0.81853 | 0.7003 | 0.63126 | 0.60451 | 0.60612 | 0.69778
43602.6977 | 0.75778 | 0.88351 | 0.81711 | 0.69853 | 0.6306 | 0.60405 | 0.60461 | 0.69746
43602.6976 | 0.77258 | 0.88615 | 0.81839 | 0.69928 | 0.63002 | 0.60372 | 0.60541 | 0.6971
43602.6979 | 0.77632 | 0.88913 | 0.81868 | 0.69996 | 0.6315 | 0.60436 | 0.60439 | 0.69672
43602.6979 | 0.77421 | 0.8856 | 0.81822 | 0.69758 | 0.63016 | 0.6035 | 0.60296 | 0.69632
43602.6978 | 0.78184 | 0.885 | 0.81594 | 0.69695 | 0.62947 | 0.60341 | 0.6037 | 0.69671
43602.6981 | 0.7891 | 0.88434 | 0.81551 | 0.69651 | 0.62981 | 0.60311 | 0.6036 | 0.6968
43602.6981 | 0.78444 | 0.8845 | 0.81539 | 0.69671 | 0.6295 | 0.60345 | 0.60352 | 0.6967
43602.698 | 0.81693 | 0.88619 | 0.81715 | 0.69852 | 0.63059 | 0.60389 | 0.60444 | 0.69708
43602.6983 | 0.80878 | 0.88269 | 0.8144 | 0.69661 | 0.63081 | 0.60443 | 0.60492 | 0.69751
43602.6983 | 0.81247 | 0.88221 | 0.81394 | 0.6959 | 0.63061 | 0.604 | 0.60328 | 0.69752
43602.6983 | 0.79085 | 0.88049 | 0.81192 | 0.69434 | 0.62978 | 0.60415 | 0.60418 | 0.69776
43602.6985 | 0.7937 | 0.8806 | 0.81227 | 0.69505 | 0.63106 | 0.60467 | 0.60643 | 0.69773
43602.6985 | 0.79119 | 0.87718 | 0.80996 | 0.69331 | 0.62886 | 0.60362 | 0.60414 | 0.69781
43602.6985 | 0.80422 | 0.88088 | 0.8125 | 0.69532 | 0.63137 | 0.60474 | 0.60559 | 0.69801
43602.6987 | 0.78781 | 0.87908 | 0.81149 | 0.69377 | 0.63112 | 0.6051 | 0.60828 | 0.69805
43602.6987 | 0.80145 | 0.87972 | 0.81123 | 0.69525 | 0.62941 | 0.60431 | 0.60454 | 0.69842
43602.6987 | 0.80449 | 0.8775 | 0.81011 | 0.69398 | 0.62921 | 0.60417 | 0.60621 | 0.69845
43602.6989 | 0.7949 | 0.87809 | 0.81132 | 0.69452 | 0.63117 | 0.60526 | 0.60518 | 0.69853
43602.6989 | 0.80455 | 0.8802 | 0.81223 | 0.69642 | 0.63046 | 0.60509 | 0.60584 | 0.6989
43602.6988 | 0.8204 | 0.88416 | 0.81658 | 0.69962 | 0.63385 | 0.60722 | 0.60749 | 0.69917
43602.6991 | 0.80603 | 0.88336 | 0.81586 | 0.6988 | 0.63377 | 0.60756 | 0.60696 | 0.69963
43602.6991 | 0.80428 | 0.88272 | 0.81556 | 0.69788 | 0.63298 | 0.60692 | 0.60888 | 0.69944
43602.6991 | 0.80136 | 0.88297 | 0.8159 | 0.69813 | 0.63215 | 0.60705 | 0.60761 | 0.7004
43602.6993 | 0.81037 | 0.88931 | 0.82105 | 0.70275 | 0.63511 | 0.6092 | 0.60929 | 0.70113
43602.6993 | 0.81524 | 0.89092 | 0.82243 | 0.70423 | 0.63751 | 0.61023 | 0.61154 | 0.70145
43602.6993 | 0.79993 | 0.8881 | 0.82013 | 0.70212 | 0.63538 | 0.60964 | 0.61002 | 0.70154
43602.6995 | 0.76922 | 0.88211 | 0.81456 | 0.6982 | 0.63294 | 0.60854 | 0.60907 | 0.70187
43602.6995 | 0.78088 | 0.88333 | 0.81611 | 0.70016 | 0.63374 | 0.60883 | 0.60964 | 0.70191
43602.6995 | 0.77139 | 0.88114 | 0.8142 | 0.69868 | 0.63253 | 0.60777 | 0.60821 | 0.7013
43602.6997 | 0.76079 | 0.88209 | 0.81472 | 0.69886 | 0.63131 | 0.60654 | 0.60766 | 0.70027
43602.6997 | 0.75758 | 0.88051 | 0.8144 | 0.69825 | 0.63153 | 0.60674 | 0.60804 | 0.70051
43602.6997 | 0.76347 | 0.8846 | 0.81687 | 0.69954 | 0.63263 | 0.60685 | 0.60704 | 0.70008
43602.6999 | 0.76501 | 0.8887 | 0.82206 | 0.7023 | 0.63408 | 0.60811 | 0.61033 | 0.70038
43602.6999 | 0.7661 | 0.8904 | 0.82264 | 0.70337 | 0.63478 | 0.60891 | 0.60916 | 0.70066
43602.6999 | 0.77186 | 0.89348 | 0.82572 | 0.70533 | 0.63653 | 0.60955 | 0.60937 | 0.70093
43602.7001 | 0.77051 | 0.89518 | 0.82749 | 0.70671 | 0.63868 | 0.61113 | 0.61081 | 0.70111
43602.7001 | 0.7729 | 0.89337 | 0.82647 | 0.70515 | 0.63765 | 0.61125 | 0.61083 | 0.70134
43602.7001 | 0.78199 | 0.89595 | 0.82826 | 0.7068 | 0.63887 | 0.61174 | 0.61284 | 0.7019
43602.7003 | 0.77154 | 0.89246 | 0.82549 | 0.70523 | 0.63759 | 0.61158 | 0.61371 | 0.70209
43602.7003 | 0.77448 | 0.89243 | 0.82598 | 0.70544 | 0.6376 | 0.61165 | 0.61157 | 0.70245
43602.7003 | 0.76546 | 0.88941 | 0.82414 | 0.70396 | 0.63717 | 0.61133 | 0.61185 | 0.70254
43602.7005 | 0.77558 | 0.89167 | 0.82483 | 0.70479 | 0.6375 | 0.61161 | 0.61184 | 0.70255
43602.7005 | 0.76675 | 0.89075 | 0.82425 | 0.70507 | 0.63711 | 0.61127 | 0.61178 | 0.70255
43602.7005 | 0.76843 | 0.89187 | 0.82485 | 0.70588 | 0.63775 | 0.61148 | 0.6112 | 0.70247
43602.7007 | 0.76579 | 0.89222 | 0.82633 | 0.70629 | 0.63821 | 0.61176 | 0.6124 | 0.70248
43602.7007 | 0.77947 | 0.89265 | 0.82692 | 0.70654 | 0.63828 | 0.61194 | 0.6124 | 0.70272
43602.7007 | 0.76207 | 0.88976 | 0.82535 | 0.70554 | 0.63759 | 0.61192 | 0.61104 | 0.70273
43602.7009 | 0.7686 | 0.89434 | 0.82865 | 0.70812 | 0.63984 | 0.61354 | 0.61307 | 0.70312
43602.7009 | 0.77335 | 0.8967 | 0.83025 | 0.70951 | 0.63977 | 0.6131 | 0.61292 | 0.70305
43602.7009 | 0.77532 | 0.89909 | 0.83293 | 0.71053 | 0.6417 | 0.6145 | 0.61378 | 0.70339
43602.7011 | 0.77889 | 0.90599 | 0.84047 | 0.71577 | 0.64527 | 0.61743 | 0.61666 | 0.70436
43602.7011 | 0.77495 | 0.90804 | 0.84208 | 0.71658 | 0.6456 | 0.61749 | 0.61627 | 0.70419
43602.7011 | 0.7804 | 0.91018 | 0.84472 | 0.7176 | 0.6476 | 0.61952 | 0.62094 | 0.70498
43602.7013 | 0.77688 | 0.90992 | 0.84587 | 0.71803 | 0.64852 | 0.62096 | 0.61967 | 0.70602
43602.7013 | 0.77899 | 0.91082 | 0.8464 | 0.71883 | 0.64882 | 0.62087 | 0.61966 | 0.7059
43602.7013 | 0.77718 | 0.90735 | 0.84364 | 0.71733 | 0.64828 | 0.62043 | 0.61981 | 0.70619
43602.7015 | 0.76893 | 0.90252 | 0.84008 | 0.71508 | 0.64686 | 0.61932 | 0.61851 | 0.70613
43602.7015 | 0.77403 | 0.90276 | 0.83989 | 0.71516 | 0.64653 | 0.61907 | 0.61941 | 0.70622
43602.7015 | 0.77095 | 0.89917 | 0.83733 | 0.71346 | 0.64587 | 0.61796 | 0.61801 | 0.70562
43602.7017 | 0.76443 | 0.89117 | 0.8285 | 0.70683 | 0.63989 | 0.61355 | 0.6144 | 0.70363
43602.7017 | 0.76171 | 0.89107 | 0.82862 | 0.70648 | 0.63905 | 0.61303 | 0.61259 | 0.7034
43602.7017 | 0.76066 | 0.891 | 0.82814 | 0.70498 | 0.63729 | 0.61071 | 0.61231 | 0.70132
43602.7019 | 0.7656 | 0.89838 | 0.83619 | 0.7086 | 0.63753 | 0.60903 | 0.60757 | 0.69904
43602.7019 | 0.76245 | 0.89719 | 0.83614 | 0.70827 | 0.63806 | 0.60954 | 0.61075 | 0.69913
43602.7019 | 0.77393 | 0.90748 | 0.84384 | 0.71294 | 0.64 | 0.60963 | 0.60998 | 0.69806
43602.7021 | 0.8017 | 0.91917 | 0.85228 | 0.71816 | 0.64257 | 0.61085 | 0.61104 | 0.69724
43602.7021 | 0.81811 | 0.92338 | 0.85429 | 0.72006 | 0.64497 | 0.61206 | 0.60981 | 0.69768
43602.7021 | 0.82599 | 0.9292 | 0.85724 | 0.72209 | 0.64768 | 0.61464 | 0.61328 | 0.69842
43602.7023 | 0.85436 | 0.93065 | 0.85718 | 0.72153 | 0.64875 | 0.61642 | 0.6144 | 0.69808
43602.7023 | 0.86269 | 0.92616 | 0.85482 | 0.71959 | 0.64925 | 0.61674 | 0.61347 | 0.69809
43602.7023 | 0.85959 | 0.92659 | 0.85446 | 0.71989 | 0.65146 | 0.61923 | 0.61631 | 0.6994
43602.7025 | 0.8556 | 0.92179 | 0.85023 | 0.71949 | 0.64889 | 0.61808 | 0.61607 | 0.70155
43602.7025 | 0.83845 | 0.9166 | 0.84661 | 0.7162 | 0.64979 | 0.61874 | 0.61613 | 0.70183
43602.7025 | 0.83015 | 0.91473 | 0.8445 | 0.71588 | 0.64934 | 0.6189 | 0.61781 | 0.70344
43602.7027 | 0.8198 | 0.90347 | 0.83695 | 0.7103 | 0.64674 | 0.61713 | 0.61674 | 0.70351
43602.7027 | 0.8194 | 0.90457 | 0.83644 | 0.71064 | 0.64417 | 0.61623 | 0.61565 | 0.70371
43602.7027 | 0.80971 | 0.90361 | 0.83538 | 0.71118 | 0.6447 | 0.61647 | 0.61528 | 0.70433
43602.7029 | 0.82837 | 0.90675 | 0.83792 | 0.71346 | 0.64702 | 0.61735 | 0.61582 | 0.70449
43602.7029 | 0.82167 | 0.90589 | 0.83788 | 0.71276 | 0.64565 | 0.61649 | 0.61899 | 0.70406
43602.7029 | 0.85108 | 0.91193 | 0.84283 | 0.71661 | 0.6497 | 0.61979 | 0.61921 | 0.70495
43602.7031 | 0.85187 | 0.9144 | 0.84485 | 0.717 | 0.65275 | 0.62225 | 0.61997 | 0.70519
43602.7031 | 0.87279 | 0.91951 | 0.8491 | 0.72085 | 0.65099 | 0.62102 | 0.62051 | 0.70468
43602.7031 | 0.87231 | 0.92044 | 0.85038 | 0.72268 | 0.65315 | 0.6228 | 0.62116 | 0.70613
43602.7033 | 0.83187 | 0.91488 | 0.84474 | 0.71834 | 0.65203 | 0.62239 | 0.6203 | 0.70648
43602.7033 | 0.84875 | 0.91502 | 0.84586 | 0.71904 | 0.65126 | 0.62164 | 0.62165 | 0.70626
43602.7033 | 0.84283 | 0.91365 | 0.84503 | 0.71873 | 0.65183 | 0.62218 | 0.6207 | 0.70708
43602.7035 | 0.8441 | 0.91958 | 0.84987 | 0.72158 | 0.65483 | 0.62408 | 0.62154 | 0.70755
43602.7035 | 0.84993 | 0.92334 | 0.85246 | 0.72424 | 0.6545 | 0.62408 | 0.62368 | 0.70743
43602.7035 | 0.84571 | 0.92049 | 0.85166 | 0.72245 | 0.65453 | 0.6247 | 0.62289 | 0.70769
43602.7037 | 0.84248 | 0.92598 | 0.85586 | 0.72669 | 0.6591 | 0.62821 | 0.62721 | 0.70967
43602.7037 | 0.83871 | 0.92662 | 0.85563 | 0.72655 | 0.65829 | 0.62782 | 0.62535 | 0.70938
43602.7037 | 0.83711 | 0.92335 | 0.8549 | 0.72604 | 0.65854 | 0.62819 | 0.62899 | 0.71026
43602.7039 | 0.82162 | 0.92366 | 0.85489 | 0.72808 | 0.659 | 0.62835 | 0.62707 | 0.71088
43602.7039 | 0.81189 | 0.92341 | 0.85508 | 0.72747 | 0.65889 | 0.62855 | 0.62634 | 0.71073
43602.7039 | 0.79838 | 0.91953 | 0.85202 | 0.72613 | 0.65719 | 0.62801 | 0.62594 | 0.7111
43602.7041 | 0.79594 | 0.91769 | 0.85054 | 0.72422 | 0.65636 | 0.62661 | 0.62692 | 0.71025
43602.7041 | 0.80463 | 0.91739 | 0.84952 | 0.7236 | 0.65534 | 0.62628 | 0.62467 | 0.71026
43602.7041 | 0.79141 | 0.91299 | 0.84559 | 0.721 | 0.65324 | 0.62441 | 0.62409 | 0.70968
43602.7043 | 0.78861 | 0.91349 | 0.84519 | 0.7209 | 0.65203 | 0.62265 | 0.62222 | 0.70826
43602.7043 | 0.78319 | 0.91207 | 0.84589 | 0.7213 | 0.65218 | 0.62326 | 0.62165 | 0.70847
43602.7043 | 0.79822 | 0.91618 | 0.84742 | 0.72237 | 0.65308 | 0.62221 | 0.6205 | 0.70758
43602.7045 | 0.79191 | 0.91522 | 0.8464 | 0.72086 | 0.65249 | 0.62206 | 0.62286 | 0.70726
43602.7045 | 0.78546 | 0.91185 | 0.84513 | 0.71867 | 0.6509 | 0.62191 | 0.62044 | 0.70734
43602.7045 | 0.80075 | 0.91362 | 0.84478 | 0.7193 | 0.65027 | 0.6214 | 0.61961 | 0.70699
43602.7047 | 0.82781 | 0.91597 | 0.84661 | 0.72109 | 0.65233 | 0.62235 | 0.62063 | 0.70734
43602.7047 | 0.81048 | 0.9136 | 0.84472 | 0.71917 | 0.65186 | 0.62206 | 0.62199 | 0.70751
43602.7047 | 0.81761 | 0.91313 | 0.84397 | 0.71894 | 0.65123 | 0.62218 | 0.62054 | 0.70775
43602.7049 | 0.82521 | 0.91427 | 0.8441 | 0.71876 | 0.65353 | 0.62337 | 0.62177 | 0.70757
43602.7049 | 0.81183 | 0.90882 | 0.84032 | 0.71517 | 0.64957 | 0.62112 | 0.61935 | 0.70704
43602.7049 | 0.83279 | 0.90933 | 0.84014 | 0.71701 | 0.6504 | 0.62143 | 0.62163 | 0.70747
43602.7051 | 0.82723 | 0.90857 | 0.83891 | 0.716 | 0.6502 | 0.62106 | 0.61965 | 0.70694
43602.7051 | 0.82086 | 0.90628 | 0.83695 | 0.7146 | 0.64916 | 0.62073 | 0.61928 | 0.7071
43602.7051 | 0.84945 | 0.91424 | 0.84356 | 0.71983 | 0.65285 | 0.62273 | 0.62086 | 0.70757
43602.7053 | 0.84602 | 0.91508 | 0.84447 | 0.71948 | 0.65371 | 0.6239 | 0.62347 | 0.70795
43602.7053 | 0.84796 | 0.91401 | 0.84409 | 0.71907 | 0.65259 | 0.62328 | 0.62254 | 0.70734
43602.7053 | 0.85389 | 0.91537 | 0.84522 | 0.72059 | 0.65449 | 0.6247 | 0.62317 | 0.70837
43602.7055 | 0.85896 | 0.91372 | 0.84429 | 0.71941 | 0.65425 | 0.62408 | 0.62297 | 0.70847
43602.7056 | 0.8401 | 0.90997 | 0.84096 | 0.71611 | 0.65193 | 0.62236 | 0.62034 | 0.70762
43602.7055 | 0.84786 | 0.9115 | 0.84149 | 0.71773 | 0.65182 | 0.6222 | 0.62185 | 0.70773
43602.7059 | 0.85438 | 0.9096 | 0.8416 | 0.71728 | 0.65183 | 0.6222 | 0.6208 | 0.70766
43602.7059 | 0.84497 | 0.90996 | 0.84092 | 0.71709 | 0.65174 | 0.62209 | 0.62046 | 0.70766
43602.7058 | 0.85127 | 0.91103 | 0.84124 | 0.71664 | 0.65112 | 0.62178 | 0.6207 | 0.70764
43602.7061 | 0.8514 | 0.91321 | 0.84404 | 0.7182 | 0.6521 | 0.62249 | 0.62129 | 0.70787
43602.7061 | 0.85334 | 0.91649 | 0.84597 | 0.72076 | 0.65362 | 0.62339 | 0.62142 | 0.70835
43602.7061 | 0.86147 | 0.91875 | 0.84745 | 0.72145 | 0.65507 | 0.62508 | 0.62467 | 0.7082
43602.7063 | 0.8433 | 0.91616 | 0.84667 | 0.72093 | 0.6557 | 0.62588 | 0.62456 | 0.70943
43602.7063 | 0.84976 | 0.91802 | 0.84748 | 0.72192 | 0.65409 | 0.62483 | 0.62508 | 0.70905
43602.7063 | 0.82702 | 0.91588 | 0.84651 | 0.72079 | 0.65599 | 0.62597 | 0.62417 | 0.70959
43602.7065 | 0.82352 | 0.91438 | 0.84522 | 0.72125 | 0.65473 | 0.62592 | 0.62437 | 0.71051
43602.7065 | 0.81956 | 0.91568 | 0.84632 | 0.72227 | 0.65563 | 0.62642 | 0.62461 | 0.71021
43602.7065 | 0.82565 | 0.91839 | 0.84815 | 0.7242 | 0.657 | 0.62744 | 0.62537 | 0.71087
43602.7067 | 0.81002 | 0.91605 | 0.84805 | 0.72213 | 0.65672 | 0.62759 | 0.626 | 0.7112
43602.7067 | 0.80084 | 0.91628 | 0.84784 | 0.72281 | 0.65609 | 0.62731 | 0.62567 | 0.71131
43602.7067 | 0.80453 | 0.91757 | 0.84869 | 0.72445 | 0.65738 | 0.62775 | 0.62594 | 0.71137
43602.7069 | 0.78876 | 0.90833 | 0.84035 | 0.7179 | 0.65263 | 0.62518 | 0.6238 | 0.711
43602.7069 | 0.7869 | 0.90657 | 0.83913 | 0.71619 | 0.6518 | 0.62469 | 0.62299 | 0.71064
43602.7069 | 0.78432 | 0.90293 | 0.83605 | 0.71527 | 0.64941 | 0.62271 | 0.62264 | 0.7099
43602.7071 | 0.78168 | 0.9034 | 0.83597 | 0.71468 | 0.64823 | 0.62073 | 0.61999 | 0.70864
43602.7071 | 0.78109 | 0.90426 | 0.83689 | 0.71578 | 0.64824 | 0.62081 | 0.62039 | 0.70837
43602.7071 | 0.77367 | 0.89951 | 0.83328 | 0.7118 | 0.64511 | 0.61831 | 0.6187 | 0.70706
43602.7073 | 0.78169 | 0.90354 | 0.83517 | 0.71267 | 0.6456 | 0.61772 | 0.61643 | 0.70605
43602.7073 | 0.77747 | 0.9018 | 0.83427 | 0.71172 | 0.64481 | 0.61714 | 0.61603 | 0.70566
43602.7073 | 0.79848 | 0.90881 | 0.83889 | 0.71591 | 0.64625 | 0.61698 | 0.6159 | 0.70497
43602.7075 | 0.81112 | 0.90789 | 0.83727 | 0.71375 | 0.64545 | 0.61739 | 0.61547 | 0.70511
43602.7075 | 0.80978 | 0.91042 | 0.83888 | 0.71539 | 0.64683 | 0.61769 | 0.61557 | 0.70504
43602.7075 | 0.82159 | 0.9111 | 0.83933 | 0.71541 | 0.64798 | 0.61862 | 0.6168 | 0.70509
43602.7077 | 0.85406 | 0.91316 | 0.84181 | 0.71639 | 0.64893 | 0.61935 | 0.61966 | 0.70516
43602.7077 | 0.83359 | 0.90904 | 0.83938 | 0.71357 | 0.64892 | 0.6196 | 0.61829 | 0.70483
43602.7077 | 0.83656 | 0.9041 | 0.83598 | 0.71032 | 0.64594 | 0.61766 | 0.6164 | 0.70463
43602.7079 | 0.85315 | 0.91182 | 0.84161 | 0.71493 | 0.64893 | 0.61968 | 0.61698 | 0.70449
43602.7079 | 0.85124 | 0.91044 | 0.84028 | 0.71402 | 0.64857 | 0.61955 | 0.61964 | 0.70458
43602.7079 | 0.85764 | 0.91167 | 0.84174 | 0.71482 | 0.64963 | 0.61999 | 0.62021 | 0.70489
43602.7081 | 0.85125 | 0.91217 | 0.84112 | 0.71491 | 0.65088 | 0.62103 | 0.61972 | 0.705
43602.7081 | 0.8603 | 0.91082 | 0.84088 | 0.71459 | 0.64867 | 0.61978 | 0.61752 | 0.70482
43602.7081 | 0.8583 | 0.91316 | 0.84267 | 0.71635 | 0.64968 | 0.62071 | 0.62015 | 0.7054
43602.7083 | 0.85293 | 0.91173 | 0.84227 | 0.71651 | 0.65147 | 0.62224 | 0.62067 | 0.70661
43602.7083 | 0.87195 | 0.91552 | 0.84535 | 0.71948 | 0.65199 | 0.6224 | 0.62108 | 0.70681
43602.7083 | 0.84614 | 0.91451 | 0.84314 | 0.71793 | 0.65263 | 0.62308 | 0.62052 | 0.70798
43602.7085 | 0.83675 | 0.90624 | 0.83713 | 0.7142 | 0.64988 | 0.62151 | 0.62185 | 0.70802
43602.7085 | 0.82527 | 0.90723 | 0.83615 | 0.71382 | 0.64897 | 0.62101 | 0.61977 | 0.70779
43602.7085 | 0.82678 | 0.90483 | 0.83532 | 0.71415 | 0.64818 | 0.61986 | 0.61959 | 0.70782
43602.7087 | 0.81222 | 0.90155 | 0.83146 | 0.7115 | 0.64631 | 0.61844 | 0.61837 | 0.70703
43602.7087 | 0.80557 | 0.90098 | 0.83106 | 0.71086 | 0.64582 | 0.61814 | 0.61871 | 0.70715
43602.7087 | 0.80962 | 0.90369 | 0.83281 | 0.7126 | 0.64614 | 0.61867 | 0.61959 | 0.70677
43602.7089 | 0.83105 | 0.90329 | 0.83364 | 0.7131 | 0.64697 | 0.61902 | 0.61991 | 0.7074
43602.7089 | 0.82547 | 0.90462 | 0.8348 | 0.71391 | 0.64804 | 0.61924 | 0.61972 | 0.70722
43602.7089 | 0.84438 | 0.9068 | 0.83752 | 0.71641 | 0.65004 | 0.62124 | 0.62195 | 0.70832
43602.7091 | 0.84075 | 0.9062 | 0.83697 | 0.71579 | 0.65053 | 0.62217 | 0.62146 | 0.70883
43602.7091 | 0.82546 | 0.9075 | 0.83675 | 0.71567 | 0.64995 | 0.62195 | 0.62149 | 0.70861
43602.7091 | 0.81907 | 0.90517 | 0.83531 | 0.71497 | 0.64981 | 0.62217 | 0.62221 | 0.70905
43602.7093 | 0.81099 | 0.9056 | 0.83467 | 0.71621 | 0.65037 | 0.62215 | 0.62326 | 0.70959
43602.7093 | 0.79151 | 0.90176 | 0.83232 | 0.71328 | 0.64916 | 0.62163 | 0.62107 | 0.7093
43602.7093 | 0.78648 | 0.89916 | 0.83004 | 0.71227 | 0.64732 | 0.62106 | 0.62062 | 0.70964
43602.7095 | 0.7874 | 0.89462 | 0.82612 | 0.70968 | 0.64508 | 0.61942 | 0.61966 | 0.70917
43602.7095 | 0.77947 | 0.89454 | 0.82578 | 0.70921 | 0.64494 | 0.61918 | 0.61869 | 0.70913
43602.7095 | 0.7785 | 0.89248 | 0.82419 | 0.70889 | 0.64385 | 0.61806 | 0.61802 | 0.70834
43602.7097 | 0.77523 | 0.88968 | 0.82244 | 0.707 | 0.64174 | 0.6164 | 0.61565 | 0.70756
43602.7098 | 0.77855 | 0.89135 | 0.82283 | 0.70761 | 0.64181 | 0.61631 | 0.61658 | 0.70751
43602.7097 | 0.77697 | 0.89285 | 0.82394 | 0.70799 | 0.64214 | 0.61584 | 0.61584 | 0.70661
43602.71 | 0.78473 | 0.89299 | 0.82406 | 0.70781 | 0.6418 | 0.61533 | 0.6148 | 0.7062
43602.71 | 0.78139 | 0.89203 | 0.82315 | 0.70582 | 0.64075 | 0.61465 | 0.61374 | 0.70588
43602.7099 | 0.79092 | 0.89122 | 0.82189 | 0.70564 | 0.64045 | 0.6145 | 0.61423 | 0.706
43602.7102 | 0.78559 | 0.88854 | 0.82046 | 0.70353 | 0.64019 | 0.61418 | 0.61352 | 0.70546
43602.7102 | 0.78466 | 0.88622 | 0.81863 | 0.70215 | 0.63904 | 0.61402 | 0.61392 | 0.70596
43602.7101 | 0.79144 | 0.8874 | 0.81973 | 0.70255 | 0.64004 | 0.61358 | 0.61353 | 0.70539
43602.7104 | 0.81782 | 0.88944 | 0.82006 | 0.7047 | 0.6404 | 0.61355 | 0.61468 | 0.70505
43602.7104 | 0.80178 | 0.88666 | 0.81878 | 0.70289 | 0.63937 | 0.61319 | 0.61341 | 0.70489
43602.7103 | 0.81424 | 0.88387 | 0.81713 | 0.70144 | 0.63879 | 0.61294 | 0.61318 | 0.70478
43602.7106 | 0.81622 | 0.88471 | 0.81753 | 0.70223 | 0.63843 | 0.6127 | 0.61208 | 0.70442
43602.7106 | 0.82834 | 0.886 | 0.81874 | 0.70351 | 0.63965 | 0.61385 | 0.61525 | 0.7048
43602.7106 | 0.82492 | 0.88044 | 0.81538 | 0.70033 | 0.63865 | 0.61311 | 0.61426 | 0.70503
43602.7108 | 0.8319 | 0.88623 | 0.82003 | 0.70285 | 0.64153 | 0.61497 | 0.61558 | 0.70522
43602.7108 | 0.83903 | 0.88625 | 0.81996 | 0.70283 | 0.63979 | 0.61442 | 0.61443 | 0.7052
43602.7108 | 0.8426 | 0.88704 | 0.8212 | 0.70343 | 0.64286 | 0.61617 | 0.61499 | 0.7052
43602.711 | 0.8409 | 0.8882 | 0.82167 | 0.70402 | 0.64322 | 0.61676 | 0.61626 | 0.70564
43602.711 | 0.83944 | 0.88813 | 0.82158 | 0.70442 | 0.64286 | 0.61669 | 0.61798 | 0.70611
43602.711 | 0.83399 | 0.8868 | 0.82033 | 0.70447 | 0.64104 | 0.61578 | 0.61574 | 0.7065
43602.7112 | 0.82528 | 0.88558 | 0.81961 | 0.70444 | 0.64314 | 0.61724 | 0.61863 | 0.70707
43602.7112 | 0.819 | 0.88401 | 0.81803 | 0.70273 | 0.64122 | 0.61594 | 0.61596 | 0.70685
43602.7112 | 0.80956 | 0.8854 | 0.81807 | 0.70378 | 0.64152 | 0.61652 | 0.61793 | 0.70746
43602.7114 | 0.80513 | 0.88427 | 0.81621 | 0.70328 | 0.64109 | 0.61624 | 0.61794 | 0.70752
43602.7114 | 0.79312 | 0.88242 | 0.81454 | 0.70141 | 0.64012 | 0.61576 | 0.61535 | 0.7073
43602.7114 | 0.79237 | 0.87987 | 0.81262 | 0.70084 | 0.63901 | 0.61477 | 0.61627 | 0.70697
43602.7116 | 0.77427 | 0.87367 | 0.80651 | 0.69702 | 0.63507 | 0.61222 | 0.61323 | 0.70644
43602.7116 | 0.77635 | 0.87164 | 0.80507 | 0.69588 | 0.63441 | 0.61213 | 0.61347 | 0.7067
43602.7116 | 0.78289 | 0.87353 | 0.80635 | 0.69707 | 0.63478 | 0.61151 | 0.61267 | 0.70569
43602.7118 | 0.78344 | 0.87227 | 0.80514 | 0.69615 | 0.6331 | 0.61016 | 0.61261 | 0.70494
43602.7118 | 0.78457 | 0.87226 | 0.8051 | 0.6961 | 0.63366 | 0.61033 | 0.61154 | 0.70504
43602.7118 | 0.78297 | 0.87175 | 0.80539 | 0.69589 | 0.63342 | 0.6099 | 0.6116 | 0.70477
43602.712 | 0.80229 | 0.87408 | 0.80783 | 0.69765 | 0.63698 | 0.61238 | 0.61299 | 0.70517
43602.712 | 0.78246 | 0.87085 | 0.80426 | 0.6945 | 0.63355 | 0.61031 | 0.61293 | 0.70519
43602.712 | 0.81304 | 0.87208 | 0.80595 | 0.69697 | 0.63503 | 0.61161 | 0.61335 | 0.70564
43602.7122 | 0.78348 | 0.86811 | 0.80261 | 0.69439 | 0.63366 | 0.61114 | 0.6139 | 0.70572
43602.7122 | 0.7932 | 0.86796 | 0.80295 | 0.69537 | 0.63349 | 0.61143 | 0.61372 | 0.70633
43602.7122 | 0.78056 | 0.86469 | 0.79931 | 0.69285 | 0.63235 | 0.61052 | 0.61252 | 0.70609
43602.7124 | 0.77908 | 0.85854 | 0.7944 | 0.68861 | 0.62917 | 0.60831 | 0.61156 | 0.70553
43602.7124 | 0.77824 | 0.85871 | 0.79482 | 0.68962 | 0.62934 | 0.60894 | 0.61118 | 0.70617
43602.7124 | 0.77304 | 0.85654 | 0.79244 | 0.6879 | 0.62831 | 0.6073 | 0.60999 | 0.70526
43602.7126 | 0.78527 | 0.86399 | 0.79789 | 0.69221 | 0.63126 | 0.60878 | 0.60998 | 0.70477
43602.7126 | 0.77762 | 0.86313 | 0.79767 | 0.69127 | 0.63047 | 0.60867 | 0.61013 | 0.70505
43602.7126 | 0.79689 | 0.86751 | 0.80195 | 0.69507 | 0.63329 | 0.61036 | 0.61304 | 0.70548
43602.7128 | 0.80127 | 0.87085 | 0.8063 | 0.698 | 0.63687 | 0.61372 | 0.61501 | 0.70713
43602.7128 | 0.79271 | 0.86872 | 0.80441 | 0.69595 | 0.6359 | 0.61338 | 0.61586 | 0.70746
43602.7128 | 0.79719 | 0.87101 | 0.80625 | 0.6987 | 0.63794 | 0.61553 | 0.6169 | 0.70888
43602.713 | 0.78443 | 0.86782 | 0.80293 | 0.69763 | 0.63734 | 0.61499 | 0.6159 | 0.70912
43602.713 | 0.78049 | 0.86467 | 0.80114 | 0.69534 | 0.63579 | 0.61405 | 0.61524 | 0.70898
43602.713 | 0.77113 | 0.85722 | 0.79362 | 0.69065 | 0.63272 | 0.61288 | 0.61461 | 0.70971
43602.7132 | 0.76379 | 0.84851 | 0.78633 | 0.68533 | 0.62745 | 0.60811 | 0.61161 | 0.70763
43602.7132 | 0.76355 | 0.849 | 0.78586 | 0.68475 | 0.62699 | 0.60767 | 0.61 | 0.70742
43602.7132 | 0.75416 | 0.85003 | 0.78692 | 0.68576 | 0.6256 | 0.60521 | 0.60868 | 0.70562
43602.7134 | 0.76511 | 0.86351 | 0.79792 | 0.69218 | 0.62843 | 0.60637 | 0.60833 | 0.7041
43602.7135 | 0.76573 | 0.86464 | 0.7986 | 0.69249 | 0.62903 | 0.60656 | 0.61035 | 0.70392
43602.7134 | 0.76888 | 0.87079 | 0.80558 | 0.69678 | 0.6317 | 0.60824 | 0.61142 | 0.70404
43602.7137 | 0.78261 | 0.88375 | 0.81633 | 0.70357 | 0.63812 | 0.61372 | 0.615 | 0.706
43602.7137 | 0.78928 | 0.88366 | 0.81646 | 0.70346 | 0.63899 | 0.61437 | 0.61462 | 0.70608
43602.7136 | 0.78721 | 0.88461 | 0.81724 | 0.70361 | 0.64002 | 0.61616 | 0.61767 | 0.70731
43602.7139 | 0.77756 | 0.87999 | 0.81361 | 0.70198 | 0.63947 | 0.61602 | 0.61816 | 0.70824
43602.7139 | 0.77684 | 0.88062 | 0.81425 | 0.70302 | 0.64007 | 0.61602 | 0.61648 | 0.70823
43602.7139 | 0.77306 | 0.87697 | 0.81113 | 0.7012 | 0.63804 | 0.61517 | 0.61603 | 0.7083
43602.7141 | 0.77295 | 0.8723 | 0.80687 | 0.69842 | 0.63679 | 0.61399 | 0.61625 | 0.70836
43602.7141 | 0.77193 | 0.87208 | 0.80594 | 0.69788 | 0.63638 | 0.61367 | 0.61616 | 0.70826
43602.7141 | 0.76769 | 0.86979 | 0.80546 | 0.69678 | 0.63529 | 0.61283 | 0.61513 | 0.70779
43602.7143 | 0.76755 | 0.87014 | 0.80502 | 0.6976 | 0.63547 | 0.61317 | 0.61475 | 0.70808
43602.7143 | 0.7627 | 0.86911 | 0.8038 | 0.69728 | 0.63519 | 0.61272 | 0.61471 | 0.708
43602.7143 | 0.76492 | 0.86836 | 0.80363 | 0.6962 | 0.63449 | 0.61242 | 0.61425 | 0.70814
43602.7145 | 0.76505 | 0.86432 | 0.79928 | 0.69272 | 0.6319 | 0.61048 | 0.6146 | 0.70713
43602.7145 | 0.7615 | 0.86326 | 0.79932 | 0.6924 | 0.6323 | 0.61076 | 0.61308 | 0.70728
43602.7145 | 0.76253 | 0.86533 | 0.80049 | 0.69338 | 0.63021 | 0.608 | 0.60939 | 0.70551
43602.7147 | 0.7629 | 0.86988 | 0.80442 | 0.695 | 0.63038 | 0.60742 | 0.60908 | 0.70383
43602.7147 | 0.76294 | 0.87099 | 0.80537 | 0.69588 | 0.63066 | 0.60745 | 0.60893 | 0.70388
43602.7147 | 0.76328 | 0.87778 | 0.81238 | 0.69972 | 0.63352 | 0.60936 | 0.61058 | 0.7037
43602.7149 | 0.7864 | 0.88884 | 0.82199 | 0.7062 | 0.63906 | 0.61271 | 0.61237 | 0.70439
43602.7149 | 0.78392 | 0.88905 | 0.82186 | 0.70508 | 0.63918 | 0.61315 | 0.61363 | 0.70434
43602.7149 | 0.79341 | 0.89267 | 0.82474 | 0.70771 | 0.6418 | 0.6156 | 0.61752 | 0.70559
43602.7151 | 0.80038 | 0.89335 | 0.82614 | 0.70833 | 0.6452 | 0.61854 | 0.61964 | 0.70721
43602.7151 | 0.80413 | 0.89005 | 0.82459 | 0.70682 | 0.64343 | 0.61798 | 0.61807 | 0.70784
43602.7151 | 0.79243 | 0.88881 | 0.82293 | 0.70764 | 0.64361 | 0.61864 | 0.61992 | 0.70896
43602.7153 | 0.77922 | 0.87951 | 0.8142 | 0.70266 | 0.64125 | 0.61782 | 0.61837 | 0.70996
43602.7153 | 0.78671 | 0.8792 | 0.81334 | 0.70194 | 0.64075 | 0.6176 | 0.6186 | 0.70963
43602.7153 | 0.77447 | 0.87336 | 0.80831 | 0.69904 | 0.63802 | 0.61505 | 0.61704 | 0.70852
43602.7155 | 0.76416 | 0.8671 | 0.80231 | 0.69506 | 0.63316 | 0.61093 | 0.61364 | 0.70661
43602.7155 | 0.76556 | 0.86611 | 0.80163 | 0.69425 | 0.63271 | 0.61092 | 0.61247 | 0.70661
43602.7155 | 0.7645 | 0.86954 | 0.8039 | 0.6949 | 0.63189 | 0.60935 | 0.61284 | 0.70494
43602.7157 | 0.76251 | 0.87789 | 0.81162 | 0.69941 | 0.63354 | 0.60984 | 0.60973 | 0.7038
43602.7158 | 0.77936 | 0.87914 | 0.81337 | 0.70064 | 0.63474 | 0.61042 | 0.61069 | 0.70379
43602.7157 | 0.79174 | 0.88546 | 0.81826 | 0.70329 | 0.63734 | 0.61161 | 0.61125 | 0.7035
43602.716 | 0.82144 | 0.89029 | 0.82378 | 0.70542 | 0.64187 | 0.6154 | 0.61471 | 0.70404
43602.716 | 0.84609 | 0.8893 | 0.82426 | 0.70538 | 0.6411 | 0.61478 | 0.61603 | 0.7044
43602.7159 | 0.8566 | 0.8986 | 0.83122 | 0.70951 | 0.64759 | 0.61929 | 0.61751 | 0.7042
43602.7162 | 0.86586 | 0.90543 | 0.83581 | 0.71224 | 0.64672 | 0.61886 | 0.61798 | 0.70421
43602.7162 | 0.86644 | 0.9088 | 0.8387 | 0.71485 | 0.64925 | 0.62064 | 0.62094 | 0.70465
43602.7161 | 0.86201 | 0.90668 | 0.83726 | 0.71299 | 0.64785 | 0.6198 | 0.61998 | 0.7047
43602.7164 | 0.85249 | 0.90547 | 0.83667 | 0.71363 | 0.64918 | 0.62149 | 0.62044 | 0.70641
43602.7164 | 0.86397 | 0.90753 | 0.83855 | 0.71573 | 0.65065 | 0.6227 | 0.62244 | 0.707
43602.7164 | 0.83684 | 0.90121 | 0.83484 | 0.71223 | 0.65049 | 0.62238 | 0.62196 | 0.70785
43602.7166 | 0.83351 | 0.90112 | 0.83387 | 0.71377 | 0.64954 | 0.62244 | 0.62174 | 0.7093
43602.7166 | 0.83038 | 0.90084 | 0.83419 | 0.7147 | 0.65023 | 0.6227 | 0.62167 | 0.70928
43602.7166 | 0.83714 | 0.90004 | 0.83391 | 0.71451 | 0.6505 | 0.62216 | 0.62386 | 0.70911
43602.7168 | 0.8149 | 0.89977 | 0.83254 | 0.71408 | 0.64877 | 0.62147 | 0.62091 | 0.70896
43602.7168 | 0.82095 | 0.89879 | 0.83193 | 0.71396 | 0.6492 | 0.62136 | 0.6211 | 0.70877
43602.7168 | 0.81614 | 0.90032 | 0.83288 | 0.71434 | 0.64866 | 0.6209 | 0.62017 | 0.70869
43602.717 | 0.79993 | 0.89791 | 0.83038 | 0.71239 | 0.64724 | 0.62099 | 0.62098 | 0.7092
43602.717 | 0.80466 | 0.89853 | 0.83183 | 0.71346 | 0.6478 | 0.62076 | 0.62045 | 0.70878
43602.717 | 0.80537 | 0.89459 | 0.82903 | 0.71093 | 0.64632 | 0.62031 | 0.62029 | 0.70885
43602.7172 | 0.78437 | 0.89691 | 0.82965 | 0.71171 | 0.64717 | 0.62088 | 0.62044 | 0.70883
43602.7172 | 0.7996 | 0.89552 | 0.82898 | 0.71176 | 0.64691 | 0.62045 | 0.61976 | 0.70871
43602.7172 | 0.80442 | 0.8965 | 0.82958 | 0.71277 | 0.64786 | 0.62087 | 0.6204 | 0.70912
43602.7174 | 0.78282 | 0.89103 | 0.82458 | 0.70969 | 0.64529 | 0.6194 | 0.62012 | 0.70854
43602.7174 | 0.78076 | 0.89099 | 0.82464 | 0.70925 | 0.64498 | 0.61947 | 0.61994 | 0.70874
43602.7174 | 0.78405 | 0.88664 | 0.82138 | 0.70728 | 0.64347 | 0.61823 | 0.61835 | 0.70842
43602.7176 | 0.78607 | 0.88737 | 0.82095 | 0.70728 | 0.64359 | 0.61771 | 0.61799 | 0.70806
43602.7176 | 0.78471 | 0.88855 | 0.82192 | 0.70694 | 0.64296 | 0.61724 | 0.61922 | 0.70799
43602.7176 | 0.78917 | 0.88698 | 0.82045 | 0.70626 | 0.64335 | 0.61689 | 0.61718 | 0.70727
43602.7178 | 0.79007 | 0.88489 | 0.8201 | 0.70546 | 0.64249 | 0.61686 | 0.61733 | 0.70804
43602.7179 | 0.78867 | 0.88685 | 0.82066 | 0.70719 | 0.64254 | 0.61693 | 0.61934 | 0.70817
43602.7178 | 0.82548 | 0.8878 | 0.82283 | 0.70933 | 0.64476 | 0.61825 | 0.61941 | 0.70836
43602.7181 | 0.7975 | 0.88798 | 0.82238 | 0.70764 | 0.64525 | 0.61884 | 0.61934 | 0.70868
43602.7181 | 0.81456 | 0.88567 | 0.82204 | 0.70834 | 0.6452 | 0.61933 | 0.61904 | 0.70922
43602.718 | 0.79715 | 0.88714 | 0.82225 | 0.7076 | 0.64618 | 0.62027 | 0.62072 | 0.70925
43602.7183 | 0.79076 | 0.88518 | 0.81909 | 0.70629 | 0.64464 | 0.61984 | 0.6196 | 0.71028
43602.7183 | 0.78719 | 0.88525 | 0.81963 | 0.707 | 0.64473 | 0.61959 | 0.62178 | 0.71044
43602.7183 | 0.78555 | 0.88279 | 0.81783 | 0.7063 | 0.64445 | 0.61924 | 0.62131 | 0.71011
43602.7185 | 0.78006 | 0.87777 | 0.8125 | 0.70286 | 0.64147 | 0.61738 | 0.61922 | 0.70964
43602.7185 | 0.77995 | 0.87707 | 0.81269 | 0.70259 | 0.64158 | 0.61733 | 0.61727 | 0.70955
43602.7185 | 0.78643 | 0.8771 | 0.81178 | 0.70174 | 0.64051 | 0.61659 | 0.61834 | 0.7092
43602.7187 | 0.77682 | 0.87476 | 0.80989 | 0.70095 | 0.63892 | 0.61509 | 0.61834 | 0.70841
43602.7187 | 0.77494 | 0.87494 | 0.81029 | 0.70104 | 0.63893 | 0.61465 | 0.61538 | 0.70807
43602.7187 | 0.77785 | 0.87581 | 0.81107 | 0.70035 | 0.63851 | 0.61431 | 0.61493 | 0.70767
43602.7189 | 0.78367 | 0.87962 | 0.814 | 0.70291 | 0.63982 | 0.61465 | 0.61523 | 0.70728
43602.7189 | 0.78195 | 0.88011 | 0.81407 | 0.70319 | 0.64037 | 0.61515 | 0.61573 | 0.70741
43602.7189 | 0.79018 | 0.88332 | 0.81683 | 0.70488 | 0.64192 | 0.61587 | 0.6185 | 0.70741
43602.7191 | 0.80721 | 0.88295 | 0.81819 | 0.7057 | 0.64384 | 0.6177 | 0.61834 | 0.70833
43602.7191 | 0.79655 | 0.88298 | 0.81814 | 0.70506 | 0.64319 | 0.6174 | 0.61759 | 0.70824
43602.7191 | 0.80913 | 0.88519 | 0.81998 | 0.70728 | 0.64505 | 0.61876 | 0.61913 | 0.70874
43602.7193 | 0.83227 | 0.89173 | 0.82604 | 0.71137 | 0.64812 | 0.62134 | 0.62145 | 0.70972
43602.7193 | 0.81324 | 0.89037 | 0.82482 | 0.7095 | 0.64776 | 0.62096 | 0.62027 | 0.70962
43602.7193 | 0.81322 | 0.88996 | 0.82519 | 0.70977 | 0.6479 | 0.62158 | 0.6217 | 0.71036
43602.7195 | 0.80612 | 0.89353 | 0.82764 | 0.71219 | 0.64866 | 0.62251 | 0.62221 | 0.71106
43602.7195 | 0.82377 | 0.89346 | 0.82856 | 0.71342 | 0.64994 | 0.62328 | 0.62319 | 0.71126
43602.7195 | 0.80981 | 0.89401 | 0.82841 | 0.71356 | 0.64973 | 0.62334 | 0.62303 | 0.71147
43602.7197 | 0.80325 | 0.89465 | 0.82812 | 0.71404 | 0.65048 | 0.62373 | 0.62388 | 0.71161
43602.7198 | 0.79351 | 0.89496 | 0.8278 | 0.71263 | 0.64963 | 0.623 | 0.6237 | 0.71155
43602.7197 | 0.78436 | 0.89161 | 0.82523 | 0.71144 | 0.64824 | 0.62289 | 0.62348 | 0.71153
43602.7199 | 0.78357 | 0.88704 | 0.82198 | 0.70819 | 0.64673 | 0.62171 | 0.62253 | 0.71178
43602.72 | 0.77962 | 0.88816 | 0.82193 | 0.70904 | 0.64649 | 0.62194 | 0.6216 | 0.71189
43602.7199 | 0.78653 | 0.88875 | 0.8222 | 0.70891 | 0.6469 | 0.62141 | 0.62371 | 0.71125
43602.7202 | 0.77963 | 0.89083 | 0.82488 | 0.71095 | 0.64769 | 0.62211 | 0.62195 | 0.71162
43602.7202 | 0.78049 | 0.89018 | 0.82373 | 0.71021 | 0.6472 | 0.62181 | 0.62095 | 0.71146
43602.7201 | 0.79014 | 0.8905 | 0.82353 | 0.70949 | 0.64733 | 0.62192 | 0.62147 | 0.71145
43602.7204 | 0.78624 | 0.89532 | 0.82875 | 0.71178 | 0.64873 | 0.62303 | 0.62459 | 0.71164
43602.7204 | 0.78353 | 0.89459 | 0.82883 | 0.71311 | 0.64953 | 0.62357 | 0.62336 | 0.71185
43602.7204 | 0.78078 | 0.89765 | 0.83216 | 0.71473 | 0.6507 | 0.62463 | 0.62392 | 0.71244
43602.7206 | 0.79385 | 0.90408 | 0.83751 | 0.71816 | 0.65369 | 0.62681 | 0.62569 | 0.71305
43602.7206 | 0.78874 | 0.90539 | 0.8374 | 0.71859 | 0.6545 | 0.62715 | 0.62814 | 0.71326
43602.7206 | 0.78711 | 0.90343 | 0.83731 | 0.71841 | 0.6543 | 0.62745 | 0.62711 | 0.71372
43602.7208 | 0.78892 | 0.89878 | 0.8331 | 0.71498 | 0.65225 | 0.62639 | 0.62623 | 0.71375
43602.7208 | 0.78188 | 0.89744 | 0.83236 | 0.7143 | 0.65219 | 0.626 | 0.62662 | 0.71381
43602.7208 | 0.78232 | 0.89685 | 0.83074 | 0.71381 | 0.65147 | 0.62581 | 0.62778 | 0.71377
43602.721 | 0.78098 | 0.89348 | 0.82868 | 0.71278 | 0.65004 | 0.62471 | 0.62555 | 0.71338
43602.721 | 0.78101 | 0.89497 | 0.82878 | 0.71227 | 0.65006 | 0.6245 | 0.62481 | 0.71318
43602.721 | 0.77824 | 0.89255 | 0.82721 | 0.71032 | 0.64809 | 0.62299 | 0.62428 | 0.71231
43602.7212 | 0.77486 | 0.89445 | 0.82928 | 0.71142 | 0.64696 | 0.62099 | 0.62184 | 0.7103
43602.7212 | 0.77355 | 0.89432 | 0.82889 | 0.7109 | 0.64675 | 0.6203 | 0.61994 | 0.71009
43602.7212 | 0.77651 | 0.89811 | 0.83242 | 0.71208 | 0.64721 | 0.62059 | 0.62012 | 0.70914
43602.7214 | 0.78165 | 0.90768 | 0.8418 | 0.71709 | 0.6503 | 0.6221 | 0.62139 | 0.70842
43602.7214 | 0.78623 | 0.90819 | 0.84164 | 0.71721 | 0.65 | 0.62179 | 0.62102 | 0.70834
43602.7214 | 0.80234 | 0.91615 | 0.84878 | 0.72262 | 0.65394 | 0.62437 | 0.62221 | 0.70881
43602.7216 | 0.79902 | 0.91495 | 0.8501 | 0.72108 | 0.65582 | 0.62661 | 0.62645 | 0.70994
43602.7216 | 0.82105 | 0.9214 | 0.85307 | 0.72553 | 0.65646 | 0.62714 | 0.62546 | 0.71048
43602.7216 | 0.8386 | 0.92258 | 0.85496 | 0.72545 | 0.65952 | 0.62864 | 0.62673 | 0.71116
43602.7218 | 0.8173 | 0.92089 | 0.85183 | 0.72496 | 0.66024 | 0.63033 | 0.62911 | 0.71315
43602.7219 | 0.81862 | 0.91865 | 0.85095 | 0.72473 | 0.65929 | 0.63043 | 0.62956 | 0.71344
43602.7218 | 0.82393 | 0.91545 | 0.84824 | 0.72415 | 0.65822 | 0.63009 | 0.62862 | 0.71389
43602.7221 | 0.79298 | 0.90287 | 0.83761 | 0.71586 | 0.65412 | 0.6276 | 0.62741 | 0.71399
43602.7221 | 0.78743 | 0.90265 | 0.83677 | 0.71602 | 0.65337 | 0.62749 | 0.6271 | 0.71406
43602.722 | 0.784 | 0.90098 | 0.83462 | 0.71511 | 0.65237 | 0.62579 | 0.62511 | 0.71265
43602.7223 | 0.79383 | 0.90419 | 0.83662 | 0.71684 | 0.65106 | 0.62392 | 0.62339 | 0.71091
43602.7223 | 0.79549 | 0.9041 | 0.83731 | 0.71845 | 0.65225 | 0.6242 | 0.6258 | 0.71108
43602.7223 | 0.78746 | 0.90614 | 0.8382 | 0.71645 | 0.65096 | 0.62325 | 0.62227 | 0.70988
43602.7225 | 0.80933 | 0.91331 | 0.84309 | 0.72085 | 0.65388 | 0.62441 | 0.62352 | 0.70969
43602.7225 | 0.79952 | 0.9099 | 0.84125 | 0.718 | 0.653 | 0.62405 | 0.62458 | 0.70944
43602.7225 | 0.86252 | 0.91386 | 0.84428 | 0.72106 | 0.65348 | 0.62455 | 0.62302 | 0.70981
43602.7227 | 0.84982 | 0.91294 | 0.84499 | 0.71945 | 0.65704 | 0.62735 | 0.62579 | 0.70995
43602.7227 | 0.84189 | 0.90816 | 0.84154 | 0.71603 | 0.65306 | 0.62459 | 0.62293 | 0.70904
43602.7227 | 0.85711 | 0.91637 | 0.84762 | 0.72144 | 0.65746 | 0.62809 | 0.62585 | 0.70999
43602.7229 | 0.87092 | 0.91845 | 0.84904 | 0.72247 | 0.65622 | 0.62696 | 0.62487 | 0.70917
43602.7229 | 0.87205 | 0.91745 | 0.84835 | 0.72137 | 0.65759 | 0.62819 | 0.62533 | 0.70934
43602.7229 | 0.86138 | 0.91388 | 0.84553 | 0.71916 | 0.6556 | 0.6267 | 0.62573 | 0.70913
43602.7231 | 0.87037 | 0.91164 | 0.84382 | 0.71883 | 0.65391 | 0.6257 | 0.6241 | 0.70926
43602.7231 | 0.86669 | 0.91625 | 0.84732 | 0.72192 | 0.65787 | 0.62858 | 0.62641 | 0.70998
43602.7231 | 0.86457 | 0.91302 | 0.8449 | 0.719 | 0.65574 | 0.62729 | 0.62519 | 0.70941
43602.7233 | 0.87639 | 0.91482 | 0.84685 | 0.7218 | 0.66004 | 0.63033 | 0.62999 | 0.71078
43602.7233 | 0.87382 | 0.91422 | 0.84646 | 0.72127 | 0.65647 | 0.6278 | 0.62618 | 0.71
43602.7233 | 0.86886 | 0.91219 | 0.84466 | 0.72106 | 0.65765 | 0.62887 | 0.62925 | 0.7114
43602.7235 | 0.86762 | 0.90902 | 0.84237 | 0.72006 | 0.65694 | 0.62882 | 0.62796 | 0.71222
43602.7235 | 0.8594 | 0.91101 | 0.84393 | 0.72155 | 0.65753 | 0.6288 | 0.62756 | 0.71222
43602.7235 | 0.86485 | 0.90803 | 0.84207 | 0.71993 | 0.65555 | 0.62784 | 0.62684 | 0.71242
43602.7237 | 0.85027 | 0.9055 | 0.83992 | 0.71895 | 0.65541 | 0.62875 | 0.62813 | 0.71302
43602.7238 | 0.8556 | 0.90694 | 0.84136 | 0.71977 | 0.65786 | 0.6297 | 0.6291 | 0.71348
43602.7237 | 0.85615 | 0.90394 | 0.83902 | 0.7192 | 0.65473 | 0.62808 | 0.62878 | 0.71362
43602.724 | 0.84532 | 0.90306 | 0.83815 | 0.71961 | 0.65744 | 0.63024 | 0.62948 | 0.71437
43602.724 | 0.84806 | 0.90065 | 0.83744 | 0.71909 | 0.65635 | 0.62941 | 0.62888 | 0.71452
43602.724 | 0.85916 | 0.90338 | 0.83841 | 0.72075 | 0.65721 | 0.63047 | 0.62963 | 0.71529
43602.7242 | 0.82618 | 0.89795 | 0.83392 | 0.71783 | 0.65565 | 0.62919 | 0.62915 | 0.71531
43602.7242 | 0.81357 | 0.89662 | 0.8326 | 0.71662 | 0.65487 | 0.62849 | 0.6287 | 0.71508
43602.7242 | 0.81472 | 0.89665 | 0.83173 | 0.7171 | 0.65436 | 0.62805 | 0.62771 | 0.71472
43602.7244 | 0.80415 | 0.88855 | 0.82357 | 0.71216 | 0.65077 | 0.62565 | 0.62771 | 0.71413
43602.7244 | 0.79494 | 0.88831 | 0.82349 | 0.71232 | 0.65021 | 0.62533 | 0.62573 | 0.71388
43602.7244 | 0.80127 | 0.88735 | 0.82223 | 0.71228 | 0.64959 | 0.62437 | 0.62599 | 0.71344
43602.7246 | 0.79126 | 0.88642 | 0.82016 | 0.70997 | 0.64714 | 0.62258 | 0.62427 | 0.71225
43602.7246 | 0.79793 | 0.88706 | 0.82074 | 0.71056 | 0.64824 | 0.62318 | 0.62372 | 0.71234
43602.7246 | 0.80195 | 0.88638 | 0.82125 | 0.7104 | 0.64803 | 0.62248 | 0.62259 | 0.71173
43602.7248 | 0.81187 | 0.88506 | 0.81972 | 0.70952 | 0.64824 | 0.62282 | 0.62325 | 0.71175
43602.7248 | 0.8051 | 0.88347 | 0.8193 | 0.70892 | 0.6477 | 0.62238 | 0.62215 | 0.71181
43602.7248 | 0.83122 | 0.88774 | 0.82218 | 0.71211 | 0.64929 | 0.62353 | 0.62345 | 0.7122
43602.725 | 0.83595 | 0.88615 | 0.82132 | 0.71115 | 0.65061 | 0.62468 | 0.62474 | 0.71251
43602.725 | 0.82034 | 0.8853 | 0.82149 | 0.71094 | 0.65047 | 0.62447 | 0.62465 | 0.71271
43602.725 | 0.81379 | 0.88128 | 0.81784 | 0.70885 | 0.64872 | 0.62416 | 0.62586 | 0.71366
43602.7252 | 0.80689 | 0.8804 | 0.81611 | 0.70931 | 0.64864 | 0.62439 | 0.62611 | 0.71413
43602.7253 | 0.80525 | 0.88105 | 0.81654 | 0.70893 | 0.64915 | 0.62441 | 0.62466 | 0.7141
43602.7252 | 0.80869 | 0.87797 | 0.81458 | 0.70792 | 0.6473 | 0.62389 | 0.62641 | 0.71454
43602.7255 | 0.79573 | 0.87311 | 0.80942 | 0.70437 | 0.64467 | 0.62234 | 0.62397 | 0.71399
43602.7255 | 0.78977 | 0.87371 | 0.81048 | 0.70541 | 0.64592 | 0.62278 | 0.62522 | 0.7143
43602.7254 | 0.7868 | 0.86898 | 0.80716 | 0.70217 | 0.64325 | 0.62066 | 0.62291 | 0.71325
43602.7257 | 0.78562 | 0.86978 | 0.80628 | 0.70238 | 0.6425 | 0.61988 | 0.62093 | 0.71264
43602.7257 | 0.78648 | 0.86961 | 0.80645 | 0.70236 | 0.64201 | 0.6194 | 0.62111 | 0.71235
43602.7257 | 0.78747 | 0.87214 | 0.80824 | 0.70351 | 0.64316 | 0.61945 | 0.62111 | 0.7119
43602.7259 | 0.82747 | 0.87869 | 0.81364 | 0.70741 | 0.64549 | 0.62089 | 0.62176 | 0.71204
43602.7259 | 0.81074 | 0.87735 | 0.81328 | 0.70697 | 0.64702 | 0.62178 | 0.62197 | 0.71181
43602.7259 | 0.79367 | 0.87393 | 0.81012 | 0.70429 | 0.64494 | 0.62109 | 0.62199 | 0.71222
43602.7261 | 0.79993 | 0.87169 | 0.80844 | 0.70329 | 0.64484 | 0.62171 | 0.62235 | 0.71307
43602.7261 | 0.79658 | 0.87107 | 0.80798 | 0.70298 | 0.64392 | 0.62092 | 0.62189 | 0.71295
43602.7261 | 0.80138 | 0.87063 | 0.80857 | 0.7043 | 0.6445 | 0.62124 | 0.62242 | 0.71316
43602.7263 | 0.79293 | 0.87048 | 0.80759 | 0.70327 | 0.64429 | 0.62131 | 0.62225 | 0.71356
43602.7263 | 0.7929 | 0.87056 | 0.80736 | 0.70347 | 0.64418 | 0.62165 | 0.62484 | 0.71372
43602.7263 | 0.7966 | 0.87226 | 0.80946 | 0.70482 | 0.64487 | 0.62166 | 0.6238 | 0.71382
43602.7265 | 0.78338 | 0.86789 | 0.80616 | 0.70236 | 0.6434 | 0.62128 | 0.62249 | 0.7141
43602.7265 | 0.79852 | 0.86915 | 0.80671 | 0.70352 | 0.64422 | 0.6215 | 0.62524 | 0.7142
43602.7265 | 0.7913 | 0.87165 | 0.8083 | 0.70422 | 0.64463 | 0.6217 | 0.62401 | 0.7138
43602.7267 | 0.78588 | 0.87022 | 0.80689 | 0.70335 | 0.64442 | 0.62172 | 0.62397 | 0.71415
43602.7267 | 0.78553 | 0.86895 | 0.80654 | 0.70306 | 0.64406 | 0.62134 | 0.62227 | 0.71382
43602.7267 | 0.78118 | 0.8673 | 0.80546 | 0.70218 | 0.64343 | 0.62155 | 0.62516 | 0.71422
43602.7269 | 0.78433 | 0.8721 | 0.81 | 0.70461 | 0.64542 | 0.62222 | 0.62354 | 0.714
43602.7269 | 0.78527 | 0.87077 | 0.80949 | 0.70491 | 0.64564 | 0.62246 | 0.62448 | 0.71424
43602.7269 | 0.789 | 0.87383 | 0.81194 | 0.70662 | 0.64638 | 0.62315 | 0.62402 | 0.7144
43602.7271 | 0.78303 | 0.87477 | 0.81205 | 0.70647 | 0.64702 | 0.62332 | 0.62457 | 0.71468
43602.7272 | 0.78039 | 0.87325 | 0.81146 | 0.70645 | 0.64668 | 0.6228 | 0.62457 | 0.71454
43602.7271 | 0.78904 | 0.87328 | 0.81072 | 0.70536 | 0.64574 | 0.62248 | 0.62389 | 0.71457
43602.7274 | 0.78419 | 0.87728 | 0.81444 | 0.70768 | 0.6474 | 0.62368 | 0.62482 | 0.71497
43602.7274 | 0.78482 | 0.87599 | 0.81417 | 0.70802 | 0.64809 | 0.62455 | 0.62615 | 0.71518
43602.7273 | 0.78097 | 0.8771 | 0.81467 | 0.70843 | 0.64753 | 0.62417 | 0.62697 | 0.71525
43602.7276 | 0.78195 | 0.87472 | 0.81205 | 0.70675 | 0.64738 | 0.62445 | 0.62594 | 0.7157
43602.7276 | 0.78794 | 0.87455 | 0.81231 | 0.70728 | 0.64723 | 0.62438 | 0.62543 | 0.7156
43602.7276 | 0.78224 | 0.87203 | 0.81077 | 0.70448 | 0.64667 | 0.62421 | 0.62633 | 0.71583
43602.7278 | 0.78079 | 0.87095 | 0.81005 | 0.70417 | 0.6463 | 0.62373 | 0.62529 | 0.71569
43602.7278 | 0.78146 | 0.87082 | 0.80921 | 0.70388 | 0.64639 | 0.62392 | 0.62603 | 0.71581
43602.7278 | 0.78012 | 0.87246 | 0.81097 | 0.7049 | 0.64572 | 0.62322 | 0.62479 | 0.71535
43602.728 | 0.7769 | 0.87147 | 0.80979 | 0.7041 | 0.64506 | 0.62232 | 0.62394 | 0.71483
43602.728 | 0.78304 | 0.87094 | 0.80932 | 0.70356 | 0.64468 | 0.62178 | 0.62512 | 0.71445
43602.728 | 0.77726 | 0.87189 | 0.80979 | 0.70359 | 0.64387 | 0.62098 | 0.62301 | 0.7138
43602.7282 | 0.77671 | 0.87601 | 0.81288 | 0.70424 | 0.64326 | 0.61989 | 0.62233 | 0.71234
43602.7282 | 0.77616 | 0.87692 | 0.81368 | 0.70499 | 0.64331 | 0.62011 | 0.6207 | 0.71226
43602.7282 | 0.77505 | 0.88078 | 0.81779 | 0.70776 | 0.64493 | 0.62038 | 0.6228 | 0.71152
43602.7284 | 0.78103 | 0.88694 | 0.82272 | 0.70976 | 0.64591 | 0.62042 | 0.62209 | 0.71068
43602.7284 | 0.78368 | 0.88753 | 0.82328 | 0.70997 | 0.64587 | 0.62085 | 0.62159 | 0.71081
43602.7284 | 0.7866 | 0.88994 | 0.82447 | 0.71072 | 0.64673 | 0.6215 | 0.62166 | 0.71096
43602.7286 | 0.79365 | 0.89026 | 0.82437 | 0.71152 | 0.64797 | 0.62218 | 0.62296 | 0.71085
43602.7286 | 0.79009 | 0.89017 | 0.82493 | 0.71104 | 0.64804 | 0.62212 | 0.62228 | 0.711
43602.7286 | 0.78871 | 0.88875 | 0.82261 | 0.71022 | 0.64713 | 0.62207 | 0.6223 | 0.7113
43602.7288 | 0.79985 | 0.88546 | 0.82083 | 0.70943 | 0.64752 | 0.62227 | 0.62494 | 0.71152
43602.7288 | 0.79517 | 0.88487 | 0.82062 | 0.70901 | 0.64744 | 0.62257 | 0.62286 | 0.71168
43602.729 | 0.80053 | 0.88147 | 0.81823 | 0.70802 | 0.64677 | 0.62247 | 0.62315 | 0.7121
43602.729 | 0.79468 | 0.88086 | 0.81688 | 0.70639 | 0.64623 | 0.62155 | 0.6234 | 0.71173
43602.729 | 0.80304 | 0.88097 | 0.81691 | 0.7077 | 0.6465 | 0.62218 | 0.62279 | 0.7121
43602.7292 | 0.79632 | 0.8784 | 0.81496 | 0.70627 | 0.64632 | 0.62214 | 0.6236 | 0.71221
43602.7292 | 0.79092 | 0.87798 | 0.81439 | 0.70573 | 0.64559 | 0.6214 | 0.62336 | 0.71223
43602.7292 | 0.80039 | 0.87554 | 0.81243 | 0.7052 | 0.64452 | 0.621 | 0.62265 | 0.7122
43602.7294 | 0.80031 | 0.87498 | 0.81144 | 0.70469 | 0.64496 | 0.62077 | 0.62179 | 0.71168
43602.7294 | 0.79096 | 0.87361 | 0.81043 | 0.70338 | 0.64404 | 0.62019 | 0.62168 | 0.71163
43602.7294 | 0.79973 | 0.87328 | 0.81029 | 0.7033 | 0.64434 | 0.6202 | 0.62213 | 0.71131
43602.7296 | 0.81827 | 0.87684 | 0.81331 | 0.70546 | 0.64501 | 0.6213 | 0.62221 | 0.71197
43602.7296 | 0.84034 | 0.88173 | 0.8171 | 0.70829 | 0.64773 | 0.6225 | 0.62272 | 0.71173
43602.7296 | 0.83437 | 0.8806 | 0.81739 | 0.70797 | 0.64825 | 0.62302 | 0.62367 | 0.71191
43602.7298 | 0.87927 | 0.91037 | 0.84238 | 0.72492 | 0.66332 | 0.63519 | 0.63416 | 0.71504
43602.7299 | 0.85872 | 0.89927 | 0.8347 | 0.71767 | 0.65968 | 0.63219 | 0.63043 | 0.71386
43602.7298 | 0.88065 | 0.92108 | 0.85272 | 0.73161 | 0.67188 | 0.64192 | 0.64085 | 0.71713
43602.7301 | 0.84581 | 0.91516 | 0.85023 | 0.73081 | 0.66922 | 0.64133 | 0.64098 | 0.72113
43602.7301 | 0.85028 | 0.91259 | 0.84973 | 0.73049 | 0.6701 | 0.6426 | 0.6414 | 0.72208
43602.73 | 0.82411 | 0.90396 | 0.84264 | 0.72603 | 0.66766 | 0.64215 | 0.64211 | 0.72429
43602.7303 | 0.80259 | 0.8905 | 0.83039 | 0.71955 | 0.66297 | 0.63922 | 0.63989 | 0.72432
43602.7303 | 0.79915 | 0.89057 | 0.82987 | 0.72011 | 0.66285 | 0.63893 | 0.64236 | 0.72423
43602.7303 | 0.78652 | 0.88434 | 0.82373 | 0.71535 | 0.65771 | 0.63464 | 0.63616 | 0.72191
43602.7305 | 0.7837 | 0.88768 | 0.82357 | 0.71272 | 0.65222 | 0.62818 | 0.62931 | 0.71693
43602.7305 | 0.77976 | 0.88829 | 0.82449 | 0.7133 | 0.65213 | 0.62774 | 0.63007 | 0.71656
43602.7305 | 0.78073 | 0.8996 | 0.83465 | 0.71928 | 0.65338 | 0.62642 | 0.6289 | 0.7141
43602.7307 | 0.78228 | 0.91221 | 0.84877 | 0.72581 | 0.65724 | 0.62876 | 0.62761 | 0.71285
43602.7307 | 0.78426 | 0.91271 | 0.85027 | 0.72657 | 0.65784 | 0.62899 | 0.62749 | 0.71272
43602.7307 | 0.78588 | 0.9225 | 0.86024 | 0.73178 | 0.66128 | 0.63096 | 0.62947 | 0.71258
43602.7309 | 0.79949 | 0.93431 | 0.87093 | 0.73833 | 0.66686 | 0.63457 | 0.63127 | 0.71277
43602.7309 | 0.80071 | 0.93444 | 0.87218 | 0.73849 | 0.66648 | 0.63475 | 0.63195 | 0.71278
43602.7309 | 0.82727 | 0.94681 | 0.88096 | 0.74466 | 0.67144 | 0.63816 | 0.636 | 0.71391
43602.7311 | 0.85693 | 0.95745 | 0.88826 | 0.75096 | 0.67856 | 0.64357 | 0.64029 | 0.71635
43602.7311 | 0.85956 | 0.95487 | 0.88631 | 0.74902 | 0.67879 | 0.64379 | 0.64053 | 0.71627
43602.7311 | 0.84152 | 0.95357 | 0.88538 | 0.74915 | 0.67865 | 0.64515 | 0.64436 | 0.71813
43602.7313 | 0.82559 | 0.94098 | 0.877 | 0.74384 | 0.67836 | 0.64621 | 0.64345 | 0.72014
43602.7313 | 0.81961 | 0.93712 | 0.87451 | 0.74209 | 0.67581 | 0.64534 | 0.64459 | 0.72045
43602.7313 | 0.81432 | 0.9328 | 0.86801 | 0.74017 | 0.6735 | 0.6437 | 0.64234 | 0.72067
43602.7315 | 0.80298 | 0.92297 | 0.85893 | 0.73369 | 0.66854 | 0.63905 | 0.63668 | 0.71872
43602.7316 | 0.80268 | 0.92293 | 0.85875 | 0.73404 | 0.66822 | 0.6385 | 0.63755 | 0.71839
43602.7315 | 0.79628 | 0.91881 | 0.85517 | 0.73079 | 0.66457 | 0.63551 | 0.63636 | 0.71675
43602.7318 | 0.79327 | 0.9203 | 0.85569 | 0.73037 | 0.66236 | 0.63243 | 0.62962 | 0.71401
43602.7318 | 0.79112 | 0.91893 | 0.85582 | 0.73048 | 0.66261 | 0.63224 | 0.63196 | 0.71383
43602.7318 | 0.80674 | 0.9238 | 0.8587 | 0.73178 | 0.66257 | 0.63166 | 0.62916 | 0.71244
43602.732 | 0.84788 | 0.93439 | 0.86328 | 0.73521 | 0.66469 | 0.6321 | 0.62943 | 0.71144
43602.732 | 0.82246 | 0.92663 | 0.85928 | 0.73013 | 0.66395 | 0.63177 | 0.62877 | 0.71086
43602.732 | 0.89043 | 0.93696 | 0.86688 | 0.73641 | 0.66828 | 0.63472 | 0.63245 | 0.71139
43602.7322 | 0.87449 | 0.92754 | 0.85856 | 0.72909 | 0.66502 | 0.63311 | 0.62995 | 0.71
43602.7322 | 0.88711 | 0.927 | 0.85757 | 0.72927 | 0.6639 | 0.63237 | 0.6304 | 0.70993
43602.7322 | 0.87053 | 0.92548 | 0.85542 | 0.72821 | 0.66382 | 0.6328 | 0.62991 | 0.71007
43602.7324 | 0.88466 | 0.92661 | 0.8574 | 0.73203 | 0.66628 | 0.63545 | 0.63161 | 0.71216
43602.7324 | 0.88212 | 0.9207 | 0.85236 | 0.72672 | 0.66672 | 0.63575 | 0.63241 | 0.71201
43602.7324 | 0.8719 | 0.91236 | 0.84526 | 0.72273 | 0.66253 | 0.63252 | 0.63161 | 0.71188
43602.7326 | 0.86069 | 0.90636 | 0.83934 | 0.71999 | 0.65969 | 0.63087 | 0.63069 | 0.71211
43602.7326 | 0.87438 | 0.90609 | 0.83925 | 0.72071 | 0.65838 | 0.62995 | 0.62813 | 0.71225
43602.7326 | 0.8653 | 0.90085 | 0.83429 | 0.71759 | 0.6574 | 0.62948 | 0.62792 | 0.71232
43602.7328 | 0.85454 | 0.89176 | 0.82654 | 0.71128 | 0.65608 | 0.62868 | 0.62645 | 0.71114
43602.7328 | 0.84376 | 0.88925 | 0.82456 | 0.7101 | 0.65091 | 0.62477 | 0.62467 | 0.71109
43602.7328 | 0.87145 | 0.8912 | 0.82595 | 0.71212 | 0.65151 | 0.62554 | 0.62433 | 0.71057
43602.733 | 0.86156 | 0.88797 | 0.82258 | 0.71047 | 0.65415 | 0.62781 | 0.62733 | 0.71082
43602.733 | 0.86388 | 0.88596 | 0.82009 | 0.70844 | 0.65015 | 0.6244 | 0.62357 | 0.70965
43602.733 | 0.83445 | 0.87618 | 0.81141 | 0.70179 | 0.6497 | 0.62447 | 0.6227 | 0.70951
43602.7333 | 0.87618 | 0.88413 | 0.817 | 0.70704 | 0.65149 | 0.6258 | 0.62369 | 0.70967
43602.7333 | 0.89006 | 0.88878 | 0.82133 | 0.71083 | 0.64913 | 0.62387 | 0.62337 | 0.70925
43602.7332 | 0.90704 | 0.89717 | 0.82779 | 0.71723 | 0.66265 | 0.63322 | 0.63063 | 0.71051
43602.7335 | 0.9122 | 0.89486 | 0.82638 | 0.71847 | 0.65248 | 0.62667 | 0.62398 | 0.70963
43602.7335 | 0.89692 | 0.88597 | 0.81719 | 0.70994 | 0.65423 | 0.62801 | 0.62491 | 0.70995
43602.7335 | 0.89489 | 0.88058 | 0.81366 | 0.70815 | 0.64827 | 0.62392 | 0.62373 | 0.70909
43602.7337 | 0.87657 | 0.8695 | 0.80389 | 0.70119 | 0.65142 | 0.62636 | 0.62367 | 0.71042
43602.7337 | 0.87797 | 0.87029 | 0.80511 | 0.7014 | 0.64451 | 0.62138 | 0.61959 | 0.70913
43602.7337 | 0.87858 | 0.86876 | 0.80364 | 0.70212 | 0.64838 | 0.62425 | 0.62311 | 0.71028
43602.7339 | 0.86754 | 0.86096 | 0.79642 | 0.69739 | 0.6494 | 0.62523 | 0.62314 | 0.71077
43602.7339 | 0.86538 | 0.858 | 0.79377 | 0.69491 | 0.63943 | 0.61778 | 0.6172 | 0.70922
43602.7339 | 0.86382 | 0.85604 | 0.79209 | 0.6946 | 0.63892 | 0.61785 | 0.61999 | 0.70943
43602.7341 | 0.8652 | 0.85359 | 0.79075 | 0.6949 | 0.64102 | 0.61951 | 0.61916 | 0.71007
43602.7341 | 0.86659 | 0.85394 | 0.79095 | 0.69543 | 0.64513 | 0.62234 | 0.62142 | 0.71063
43602.7341 | 0.84921 | 0.84303 | 0.78228 | 0.68833 | 0.64024 | 0.61926 | 0.61763 | 0.71018
43602.7343 | 0.84271 | 0.83843 | 0.77817 | 0.68608 | 0.63976 | 0.61873 | 0.61848 | 0.71008
43602.7343 | 0.85419 | 0.84352 | 0.78183 | 0.6904 | 0.63296 | 0.61388 | 0.61599 | 0.70935
43602.7343 | 0.85684 | 0.845 | 0.78368 | 0.69202 | 0.64086 | 0.61959 | 0.61881 | 0.71065
43602.7345 | 0.84164 | 0.83298 | 0.77283 | 0.68413 | 0.63342 | 0.61451 | 0.61548 | 0.70997
43602.7346 | 0.83799 | 0.83006 | 0.77092 | 0.68264 | 0.63624 | 0.61648 | 0.61769 | 0.71057
43602.7345 | 0.84135 | 0.8323 | 0.77279 | 0.68522 | 0.63685 | 0.61687 | 0.61813 | 0.71069
43602.7348 | 0.82482 | 0.82072 | 0.76301 | 0.67797 | 0.63303 | 0.61428 | 0.61574 | 0.71024
43602.7348 | 0.81507 | 0.81462 | 0.75775 | 0.67354 | 0.62801 | 0.61024 | 0.61191 | 0.70946
43602.7347 | 0.82062 | 0.81383 | 0.75705 | 0.6742 | 0.62645 | 0.60952 | 0.61112 | 0.7096
43602.735 | 0.81472 | 0.80953 | 0.75292 | 0.67191 | 0.62434 | 0.60805 | 0.61162 | 0.7101
43602.735 | 0.82298 | 0.81455 | 0.75738 | 0.67605 | 0.62598 | 0.60911 | 0.61221 | 0.71007
43602.735 | 0.81601 | 0.80881 | 0.7529 | 0.67288 | 0.62633 | 0.60968 | 0.61273 | 0.71087
43602.7352 | 0.80563 | 0.80173 | 0.74729 | 0.67036 | 0.62612 | 0.6095 | 0.61207 | 0.71114
43602.7352 | 0.81156 | 0.8052 | 0.74989 | 0.67299 | 0.62515 | 0.60863 | 0.61202 | 0.71111
43602.7352 | 0.79946 | 0.79661 | 0.74318 | 0.66799 | 0.6233 | 0.6074 | 0.61156 | 0.7111
43602.7354 | 0.80097 | 0.79574 | 0.74184 | 0.66823 | 0.62372 | 0.60766 | 0.61077 | 0.71191
43602.7354 | 0.79797 | 0.79278 | 0.73994 | 0.66773 | 0.62165 | 0.60604 | 0.61162 | 0.71195
43602.7356 | 0.79287 | 0.78849 | 0.7369 | 0.66651 | 0.62083 | 0.60561 | 0.61012 | 0.71214
43602.7356 | 0.79607 | 0.7895 | 0.73788 | 0.66729 | 0.62075 | 0.60532 | 0.60975 | 0.71242
43602.7356 | 0.79117 | 0.78607 | 0.73488 | 0.66577 | 0.62084 | 0.60516 | 0.61106 | 0.71264
43602.7358 | 0.77999 | 0.77766 | 0.72731 | 0.66018 | 0.61815 | 0.60352 | 0.61025 | 0.71344
43602.7358 | 0.77591 | 0.77642 | 0.72576 | 0.65946 | 0.61394 | 0.60079 | 0.60707 | 0.71313
43602.7358 | 0.77989 | 0.77754 | 0.72785 | 0.66171 | 0.61914 | 0.60463 | 0.61159 | 0.71384
43602.736 | 0.78674 | 0.78034 | 0.72973 | 0.66507 | 0.61771 | 0.60313 | 0.6101 | 0.7138
43602.736 | 0.78035 | 0.77639 | 0.7264 | 0.66181 | 0.61852 | 0.60368 | 0.61012 | 0.7137
43602.736 | 0.77615 | 0.77443 | 0.72476 | 0.66088 | 0.61778 | 0.60324 | 0.61026 | 0.71395
43602.7362 | 0.77807 | 0.77342 | 0.72324 | 0.66053 | 0.61431 | 0.601 | 0.60761 | 0.7139
43602.7362 | 0.77652 | 0.77228 | 0.72327 | 0.66101 | 0.61804 | 0.60305 | 0.61158 | 0.71426
43602.7362 | 0.77377 | 0.76944 | 0.72062 | 0.65915 | 0.616 | 0.60179 | 0.60957 | 0.71444
43602.7364 | 0.7748 | 0.77063 | 0.72138 | 0.66042 | 0.61609 | 0.60112 | 0.60986 | 0.71431
43602.7364 | 0.76905 | 0.76612 | 0.71758 | 0.65781 | 0.6145 | 0.60041 | 0.60838 | 0.71417
43602.7364 | 0.77217 | 0.76714 | 0.71888 | 0.6592 | 0.61275 | 0.59908 | 0.60693 | 0.71419
43602.7367 | 0.76638 | 0.76299 | 0.71485 | 0.65646 | 0.61324 | 0.59888 | 0.60683 | 0.71407
43602.7367 | 0.76398 | 0.76129 | 0.71358 | 0.65556 | 0.61201 | 0.59821 | 0.60627 | 0.71404
43602.7366 | 0.76894 | 0.76518 | 0.71692 | 0.6587 | 0.61523 | 0.60036 | 0.60879 | 0.71462
43602.7369 | 0.77491 | 0.77013 | 0.72085 | 0.66273 | 0.61931 | 0.60314 | 0.61086 | 0.71521
43602.7369 | 0.76879 | 0.76536 | 0.71734 | 0.65997 | 0.61787 | 0.60218 | 0.61048 | 0.71537
43602.7369 | 0.76657 | 0.76267 | 0.71512 | 0.65848 | 0.6146 | 0.59925 | 0.60797 | 0.71467
43602.7371 | 0.76592 | 0.76387 | 0.71543 | 0.65938 | 0.61408 | 0.59921 | 0.60869 | 0.71483
43602.7371 | 0.76186 | 0.76073 | 0.71328 | 0.65714 | 0.61394 | 0.59913 | 0.60768 | 0.71481
43602.7371 | 0.762 | 0.75964 | 0.71236 | 0.65681 | 0.61242 | 0.59803 | 0.60756 | 0.71454
43602.7373 | 0.75333 | 0.75464 | 0.70679 | 0.65198 | 0.60671 | 0.59413 | 0.60347 | 0.71388
43602.7373 | 0.76297 | 0.75966 | 0.71256 | 0.6579 | 0.61421 | 0.59869 | 0.60762 | 0.71466
43602.7373 | 0.75522 | 0.75479 | 0.70796 | 0.65357 | 0.61204 | 0.59786 | 0.60768 | 0.71465
43602.7375 | 0.75807 | 0.75665 | 0.7097 | 0.65561 | 0.61041 | 0.59642 | 0.60797 | 0.71445
43602.7375 | 0.76274 | 0.75914 | 0.71204 | 0.65765 | 0.61327 | 0.59837 | 0.60699 | 0.71476
43602.7375 | 0.75974 | 0.7579 | 0.7108 | 0.65669 | 0.61486 | 0.59938 | 0.60767 | 0.71505
43602.7378 | 0.75256 | 0.75142 | 0.70512 | 0.65282 | 0.60966 | 0.59605 | 0.60624 | 0.71466
43602.7378 | 0.76142 | 0.75946 | 0.71209 | 0.65815 | 0.61456 | 0.59916 | 0.60809 | 0.71507
43602.738 | 0.7504 | 0.75123 | 0.70473 | 0.65254 | 0.61008 | 0.59608 | 0.60547 | 0.71434
43602.738 | 0.7468 | 0.74723 | 0.70219 | 0.65099 | 0.60964 | 0.59607 | 0.6064 | 0.71469
43602.7382 | 0.74796 | 0.74905 | 0.70342 | 0.65201 | 0.6095 | 0.59563 | 0.6052 | 0.71439
43602.7382 | 0.74286 | 0.74404 | 0.69953 | 0.64861 | 0.60991 | 0.59623 | 0.60604 | 0.7146
43602.7382 | 0.74315 | 0.745 | 0.69989 | 0.6491 | 0.60864 | 0.59577 | 0.60665 | 0.71437
43602.7384 | 0.74549 | 0.74701 | 0.70127 | 0.65046 | 0.608 | 0.59464 | 0.60516 | 0.71411
43602.7384 | 0.74811 | 0.74895 | 0.70314 | 0.65219 | 0.6105 | 0.59661 | 0.60562 | 0.71435
43602.7384 | 0.7421 | 0.74372 | 0.69883 | 0.64916 | 0.60791 | 0.59498 | 0.60505 | 0.71441
43602.7386 | 0.74344 | 0.74526 | 0.69974 | 0.6501 | 0.60676 | 0.59356 | 0.60341 | 0.71406
43602.7387 | 0.74713 | 0.7487 | 0.70271 | 0.65209 | 0.61139 | 0.59707 | 0.60844 | 0.71442
43602.7386 | 0.74408 | 0.74509 | 0.69968 | 0.6496 | 0.60905 | 0.5954 | 0.60678 | 0.71423
43602.7389 | 0.73892 | 0.73939 | 0.69605 | 0.64726 | 0.60818 | 0.59516 | 0.60595 | 0.71466
43602.7389 | 0.73771 | 0.73997 | 0.69566 | 0.64728 | 0.60611 | 0.59361 | 0.60368 | 0.71433
43602.7389 | 0.73959 | 0.7409 | 0.69679 | 0.64811 | 0.60993 | 0.5964 | 0.60705 | 0.71444
43602.7391 | 0.74013 | 0.74065 | 0.69658 | 0.64772 | 0.60652 | 0.59352 | 0.60359 | 0.7139
43602.7391 | 0.73959 | 0.74053 | 0.69653 | 0.64756 | 0.60859 | 0.59515 | 0.60669 | 0.71387
43602.7391 | 0.73837 | 0.74076 | 0.6963 | 0.64747 | 0.6083 | 0.59501 | 0.60667 | 0.71438
43602.7393 | 0.73406 | 0.73585 | 0.69269 | 0.64509 | 0.60617 | 0.59358 | 0.60528 | 0.71421
43602.7393 | 0.73225 | 0.73439 | 0.69124 | 0.64389 | 0.60399 | 0.59182 | 0.60166 | 0.71369
43602.7393 | 0.73375 | 0.73536 | 0.69156 | 0.64422 | 0.60546 | 0.59305 | 0.60253 | 0.71358
43602.7395 | 0.73777 | 0.73613 | 0.69301 | 0.64521 | 0.60745 | 0.59504 | 0.60396 | 0.7125
43602.7395 | 0.73179 | 0.73464 | 0.691 | 0.64393 | 0.60547 | 0.59348 | 0.60488 | 0.71391
43602.7395 | 0.73753 | 0.73509 | 0.6917 | 0.64432 | 0.6061 | 0.59344 | 0.60318 | 0.71247
43602.7397 | 0.73628 | 0.73289 | 0.69042 | 0.64229 | 0.60499 | 0.59268 | 0.60262 | 0.71258
43602.7397 | 0.73285 | 0.73302 | 0.69066 | 0.64296 | 0.60486 | 0.59272 | 0.60298 | 0.71277
43602.7397 | 0.73133 | 0.7328 | 0.68995 | 0.64291 | 0.60433 | 0.59225 | 0.6024 | 0.71315
43602.7399 | 0.73284 | 0.73116 | 0.68846 | 0.64115 | 0.60359 | 0.59169 | 0.60212 | 0.71185
43602.74 | 0.73267 | 0.73054 | 0.68778 | 0.64057 | 0.60351 | 0.59187 | 0.6014 | 0.7123
43602.7399 | 0.72564 | 0.72807 | 0.68541 | 0.63934 | 0.60105 | 0.58926 | 0.60074 | 0.71205
43602.7402 | 0.73042 | 0.72794 | 0.68614 | 0.63945 | 0.60176 | 0.59004 | 0.6012 | 0.71159
43602.7402 | 0.72616 | 0.7272 | 0.6847 | 0.63875 | 0.60155 | 0.58975 | 0.59969 | 0.71202
43602.7401 | 0.59523 | 0.64078 | 0.60998 | 0.57714 | 0.54766 | 0.56376 | 0.57561 | 0.70531
43602.7404 | 0.56465 | 0.60241 | 0.5745 | 0.56806 | 0.5373 | 0.55918 | 0.57458 | 0.71043
43602.7404 | 0.56424 | 0.60283 | 0.57534 | 0.56864 | 0.53754 | 0.55953 | 0.57402 | 0.71048
43602.7404 | 0.56025 | 0.59809 | 0.57115 | 0.56375 | 0.53359 | 0.55583 | 0.57152 | 0.70788
43602.7406 | 0.57679 | 0.61404 | 0.58228 | 0.57486 | 0.54121 | 0.56228 | 0.57508 | 0.71095
43602.7406 | 0.57709 | 0.61478 | 0.58365 | 0.57576 | 0.54268 | 0.56378 | 0.57767 | 0.71215
43602.7406 | 0.57948 | 0.61485 | 0.58616 | 0.57907 | 0.54866 | 0.56963 | 0.58532 | 0.7156
43602.7408 | 0.58008 | 0.61175 | 0.58304 | 0.57744 | 0.54725 | 0.56872 | 0.58452 | 0.71681
43602.7408 | 0.5809 | 0.61253 | 0.58348 | 0.57767 | 0.54653 | 0.56794 | 0.58332 | 0.71655
43602.7408 | 0.58112 | 0.61305 | 0.58274 | 0.57834 | 0.54668 | 0.56795 | 0.58285 | 0.71632
43602.741 | 0.5802 | 0.60964 | 0.58086 | 0.57683 | 0.54509 | 0.56645 | 0.58051 | 0.7151
43602.741 | 0.57916 | 0.6098 | 0.5806 | 0.57619 | 0.54501 | 0.56658 | 0.58174 | 0.7151
43602.741 | 0.57812 | 0.60858 | 0.57884 | 0.57517 | 0.5432 | 0.56466 | 0.5797 | 0.71396
43602.7412 | 0.57798 | 0.60778 | 0.57767 | 0.57438 | 0.54221 | 0.56383 | 0.57975 | 0.71335
43602.7412 | 0.57791 | 0.60815 | 0.57794 | 0.57446 | 0.54201 | 0.56361 | 0.57803 | 0.71307
43602.7412 | 0.57649 | 0.607 | 0.57713 | 0.57322 | 0.54109 | 0.56273 | 0.57825 | 0.71244
43602.7415 | 0.57418 | 0.60389 | 0.57475 | 0.57135 | 0.53928 | 0.5612 | 0.57463 | 0.7113
43602.7415 | 0.57452 | 0.60471 | 0.57408 | 0.57122 | 0.5392 | 0.56111 | 0.57834 | 0.71112
43602.7414 | 0.57383 | 0.6034 | 0.57353 | 0.57051 | 0.53793 | 0.56005 | 0.57449 | 0.71035
43602.7417 | 0.57215 | 0.60138 | 0.57203 | 0.56937 | 0.537 | 0.55877 | 0.57246 | 0.70973
43602.7417 | 0.57097 | 0.60089 | 0.57144 | 0.5683 | 0.53659 | 0.55842 | 0.57208 | 0.70918
43602.7419 | 0.57187 | 0.59892 | 0.56977 | 0.56709 | 0.53399 | 0.55605 | 0.57192 | 0.70793
43602.7419 | 0.57017 | 0.59849 | 0.5691 | 0.56645 | 0.53392 | 0.55579 | 0.57062 | 0.70751
43602.7422 | 0.56981 | 0.59752 | 0.56835 | 0.56613 | 0.53306 | 0.55478 | 0.57037 | 0.70707
43602.7422 | 0.5701 | 0.59654 | 0.56801 | 0.56586 | 0.53198 | 0.55387 | 0.568 | 0.70649
43602.7424 | 0.56797 | 0.59537 | 0.56673 | 0.56482 | 0.53145 | 0.55385 | 0.56851 | 0.70613
43602.7424 | 0.56853 | 0.5954 | 0.56698 | 0.56476 | 0.53122 | 0.55334 | 0.56822 | 0.70607
43602.7424 | 0.56759 | 0.59451 | 0.56599 | 0.56405 | 0.53093 | 0.55298 | 0.56824 | 0.70549
43602.7426 | 0.56625 | 0.59361 | 0.56531 | 0.56343 | 0.53012 | 0.55229 | 0.56759 | 0.70512
43602.7426 | 0.56689 | 0.59351 | 0.56512 | 0.56324 | 0.52966 | 0.55207 | 0.56773 | 0.70484
43602.7428 | 0.56581 | 0.59178 | 0.56353 | 0.56194 | 0.52892 | 0.55096 | 0.56563 | 0.70412
43602.7428 | 0.56529 | 0.5918 | 0.56382 | 0.56217 | 0.5287 | 0.55082 | 0.56768 | 0.7039
43602.7428 | 0.56602 | 0.59135 | 0.56352 | 0.56152 | 0.52817 | 0.55039 | 0.5663 | 0.7036
43602.743 | 0.56536 | 0.5901 | 0.56231 | 0.56091 | 0.52705 | 0.54939 | 0.56392 | 0.70276
43602.743 | 0.56474 | 0.59034 | 0.56261 | 0.56098 | 0.52705 | 0.54927 | 0.56635 | 0.7027
43602.743 | 0.56474 | 0.58991 | 0.5618 | 0.56042 | 0.52702 | 0.54915 | 0.56617 | 0.70273
43602.7432 | 0.56344 | 0.58932 | 0.56126 | 0.55981 | 0.52641 | 0.54877 | 0.56491 | 0.70253
43602.7433 | 0.5643 | 0.58945 | 0.5615 | 0.55994 | 0.52661 | 0.5488 | 0.56445 | 0.70242
43602.7432 | 0.56454 | 0.58919 | 0.56131 | 0.56007 | 0.5267 | 0.54872 | 0.56422 | 0.70223
43602.7435 | 0.56425 | 0.58872 | 0.56068 | 0.55982 | 0.52605 | 0.54831 | 0.56413 | 0.70193
43602.7435 | 0.56388 | 0.58881 | 0.56103 | 0.55982 | 0.52615 | 0.54842 | 0.56205 | 0.70178
43602.7435 | 0.56416 | 0.5886 | 0.56118 | 0.55982 | 0.52602 | 0.54821 | 0.56255 | 0.70175
43602.7437 | 0.56342 | 0.58813 | 0.56025 | 0.55961 | 0.5259 | 0.54808 | 0.56383 | 0.70155
43602.7437 | 0.56291 | 0.58822 | 0.56016 | 0.55946 | 0.52564 | 0.54797 | 0.56233 | 0.70157
43602.7437 | 0.56329 | 0.58825 | 0.56004 | 0.55938 | 0.52547 | 0.54774 | 0.56305 | 0.70125
43602.7439 | 0.56282 | 0.58746 | 0.55968 | 0.55927 | 0.5253 | 0.54751 | 0.56323 | 0.70112
43602.7439 | 0.5627 | 0.58734 | 0.55982 | 0.55934 | 0.52539 | 0.54757 | 0.56365 | 0.70108
43602.7439 | 0.56358 | 0.58764 | 0.56016 | 0.55968 | 0.52546 | 0.54759 | 0.56229 | 0.70126
43602.7441 | 0.56331 | 0.5874 | 0.56009 | 0.55924 | 0.52532 | 0.54722 | 0.56374 | 0.70096
43602.7441 | 0.56281 | 0.58737 | 0.55971 | 0.55914 | 0.52538 | 0.54752 | 0.56291 | 0.70094
43602.7441 | 0.56365 | 0.58736 | 0.55997 | 0.55942 | 0.52502 | 0.54709 | 0.56282 | 0.70088
43602.7444 | 0.56348 | 0.58733 | 0.56005 | 0.55948 | 0.52511 | 0.54716 | 0.56243 | 0.70066
43602.7444 | 0.56385 | 0.58753 | 0.56003 | 0.55963 | 0.52521 | 0.54713 | 0.56296 | 0.70081
43602.7443 | 0.56323 | 0.58715 | 0.5602 | 0.55948 | 0.52551 | 0.54749 | 0.56181 | 0.70091
43602.7446 | 0.56262 | 0.58669 | 0.55988 | 0.55913 | 0.52521 | 0.54732 | 0.56126 | 0.70064
43602.7446 | 0.56341 | 0.58682 | 0.55975 | 0.55906 | 0.52517 | 0.54719 | 0.56418 | 0.70068
43602.7446 | 0.56362 | 0.58683 | 0.55982 | 0.55949 | 0.52506 | 0.54725 | 0.56284 | 0.70047
43602.7448 | 0.56245 | 0.58625 | 0.55897 | 0.55896 | 0.52487 | 0.54693 | 0.56093 | 0.70035
43602.7448 | 0.56249 | 0.58653 | 0.55919 | 0.55904 | 0.52477 | 0.54682 | 0.56116 | 0.70022
43602.7448 | 0.56338 | 0.58678 | 0.55976 | 0.55926 | 0.52519 | 0.54663 | 0.5608 | 0.70022
43602.745 | 0.56292 | 0.58584 | 0.55905 | 0.55895 | 0.52501 | 0.54652 | 0.56279 | 0.69992
43602.745 | 0.5633 | 0.58611 | 0.55919 | 0.55881 | 0.52441 | 0.5463 | 0.56276 | 0.6998
43602.745 | 0.56337 | 0.58605 | 0.55964 | 0.55924 | 0.52493 | 0.54649 | 0.56141 | 0.69985
43602.7452 | 0.56297 | 0.58573 | 0.5589 | 0.55867 | 0.52449 | 0.54618 | 0.56204 | 0.69969
43602.7453 | 0.56284 | 0.58602 | 0.55914 | 0.55888 | 0.5246 | 0.54625 | 0.56093 | 0.69961
43602.7452 | 0.5621 | 0.58534 | 0.5585 | 0.55826 | 0.52468 | 0.54626 | 0.56213 | 0.69941
43602.7455 | 0.56226 | 0.58501 | 0.5578 | 0.55817 | 0.52392 | 0.54563 | 0.56244 | 0.69934
43602.7455 | 0.56308 | 0.58546 | 0.55852 | 0.55882 | 0.52411 | 0.54578 | 0.56175 | 0.69912
43602.7455 | 0.56264 | 0.5855 | 0.55878 | 0.5589 | 0.52472 | 0.54602 | 0.56112 | 0.69921
43602.7457 | 0.56218 | 0.58508 | 0.55859 | 0.55885 | 0.52441 | 0.54596 | 0.56132 | 0.69897
43602.7457 | 0.56203 | 0.58511 | 0.55825 | 0.55861 | 0.52448 | 0.54597 | 0.56071 | 0.69898
43602.7457 | 0.56245 | 0.58483 | 0.55822 | 0.55864 | 0.52437 | 0.5456 | 0.56032 | 0.69863
43602.7459 | 0.56146 | 0.58448 | 0.55781 | 0.55811 | 0.52413 | 0.5454 | 0.56025 | 0.69878
43602.7459 | 0.56198 | 0.58464 | 0.55796 | 0.55814 | 0.52373 | 0.54527 | 0.559 | 0.69861
43602.7459 | 0.56288 | 0.58461 | 0.55825 | 0.55875 | 0.52356 | 0.54507 | 0.55996 | 0.69834
43602.7461 | 0.56107 | 0.5841 | 0.55795 | 0.55834 | 0.52399 | 0.54553 | 0.56183 | 0.69838
43602.7462 | 0.56119 | 0.58385 | 0.55747 | 0.55807 | 0.52371 | 0.54511 | 0.56219 | 0.69837
43602.7461 | 0.56265 | 0.58483 | 0.55869 | 0.55923 | 0.52409 | 0.54532 | 0.55973 | 0.69814
43602.7464 | 0.562 | 0.58482 | 0.55869 | 0.55925 | 0.52399 | 0.54522 | 0.5591 | 0.6981
43602.7464 | 0.5612 | 0.58463 | 0.55882 | 0.55902 | 0.52366 | 0.5453 | 0.56003 | 0.69803
43602.7464 | 0.56246 | 0.58475 | 0.55909 | 0.55935 | 0.52386 | 0.54503 | 0.55934 | 0.69788
43602.7466 | 0.56187 | 0.58423 | 0.55828 | 0.55853 | 0.52345 | 0.54464 | 0.56304 | 0.69786
43602.7466 | 0.56235 | 0.58422 | 0.55853 | 0.55887 | 0.52358 | 0.54454 | 0.55971 | 0.69786
43602.7466 | 0.56168 | 0.58407 | 0.55844 | 0.55833 | 0.52408 | 0.54491 | 0.55995 | 0.6979
43602.7468 | 0.56245 | 0.58424 | 0.55884 | 0.55907 | 0.52398 | 0.54498 | 0.56005 | 0.69784
43602.7468 | 0.56212 | 0.58436 | 0.55903 | 0.55927 | 0.52385 | 0.54498 | 0.56019 | 0.69774
43602.7468 | 0.56293 | 0.58454 | 0.55936 | 0.55984 | 0.52436 | 0.54543 | 0.55989 | 0.6978
43602.747 | 0.56246 | 0.58458 | 0.55908 | 0.55976 | 0.52436 | 0.54525 | 0.55972 | 0.69775
43602.7471 | 0.56212 | 0.58434 | 0.55908 | 0.55928 | 0.52447 | 0.54521 | 0.55951 | 0.69781
43602.747 | 0.56235 | 0.5844 | 0.55892 | 0.55931 | 0.52434 | 0.54523 | 0.56011 | 0.69743
43602.7473 | 0.56272 | 0.58465 | 0.559 | 0.55985 | 0.52413 | 0.54515 | 0.55887 | 0.69725
43602.7473 | 0.56158 | 0.58374 | 0.55833 | 0.55942 | 0.52367 | 0.5446 | 0.56009 | 0.6971
43602.7476 | 0.56196 | 0.5837 | 0.55846 | 0.55961 | 0.52353 | 0.54425 | 0.55923 | 0.69672
43602.7476 | 0.56251 | 0.58379 | 0.55837 | 0.55959 | 0.52393 | 0.54472 | 0.56148 | 0.69666
43602.7476 | 0.55966 | 0.58257 | 0.55744 | 0.55828 | 0.52331 | 0.54432 | 0.5608 | 0.69679
43602.7479 | 0.56122 | 0.58285 | 0.5576 | 0.55871 | 0.5228 | 0.54421 | 0.56209 | 0.69657
43602.7479 | 0.56145 | 0.58322 | 0.55795 | 0.55893 | 0.52314 | 0.54453 | 0.55933 | 0.69622
43602.7478 | 0.56138 | 0.58347 | 0.55822 | 0.55929 | 0.52336 | 0.5443 | 0.55811 | 0.69634
43602.7481 | 0.56106 | 0.5829 | 0.55783 | 0.55881 | 0.52305 | 0.54386 | 0.55822 | 0.69627
43602.7481 | 0.56106 | 0.58305 | 0.55798 | 0.55883 | 0.52297 | 0.54399 | 0.55993 | 0.69622
43602.7481 | 0.56147 | 0.58287 | 0.55793 | 0.55913 | 0.52345 | 0.54426 | 0.55842 | 0.69611
43602.7483 | 0.56096 | 0.58291 | 0.55796 | 0.55925 | 0.52343 | 0.54424 | 0.56016 | 0.69617
43602.7483 | 0.56116 | 0.58308 | 0.55802 | 0.55925 | 0.52353 | 0.54429 | 0.56011 | 0.69616
43602.7483 | 0.56052 | 0.58286 | 0.55817 | 0.55921 | 0.52372 | 0.54458 | 0.56015 | 0.69622
43602.7485 | 0.56013 | 0.58227 | 0.55707 | 0.55838 | 0.52327 | 0.54428 | 0.5587 | 0.69613
43602.7485 | 0.56066 | 0.58219 | 0.55733 | 0.55892 | 0.52292 | 0.54375 | 0.56032 | 0.69588
43602.7485 | 0.56153 | 0.5831 | 0.55837 | 0.55974 | 0.52342 | 0.54451 | 0.55739 | 0.6958
43602.7488 | 0.56191 | 0.58287 | 0.55832 | 0.55946 | 0.52356 | 0.54427 | 0.55922 | 0.69577
43602.7488 | 0.56187 | 0.58302 | 0.55847 | 0.55981 | 0.52373 | 0.54454 | 0.55817 | 0.69581
43602.7487 | 0.56171 | 0.5823 | 0.55801 | 0.55916 | 0.52349 | 0.54422 | 0.55975 | 0.69569
43602.749 | 0.56075 | 0.58218 | 0.55785 | 0.55907 | 0.52344 | 0.54407 | 0.56127 | 0.69548
43602.749 | 0.56061 | 0.58181 | 0.5575 | 0.55871 | 0.52368 | 0.54414 | 0.55868 | 0.69564
43602.749 | 0.5617 | 0.58238 | 0.55815 | 0.55949 | 0.52363 | 0.5443 | 0.55795 | 0.69548
43602.7492 | 0.5606 | 0.58167 | 0.55752 | 0.55911 | 0.52291 | 0.54397 | 0.55995 | 0.69521
43602.7492 | 0.56074 | 0.58182 | 0.55738 | 0.55882 | 0.5232 | 0.54395 | 0.55908 | 0.69531
43602.7492 | 0.56122 | 0.58207 | 0.55749 | 0.55887 | 0.52315 | 0.54392 | 0.55803 | 0.69516
43602.7494 | 0.56129 | 0.58187 | 0.55747 | 0.55915 | 0.52336 | 0.544 | 0.55663 | 0.695
43602.7494 | 0.56073 | 0.58166 | 0.5573 | 0.55887 | 0.52338 | 0.54404 | 0.55782 | 0.69505
43602.7494 | 0.55992 | 0.58073 | 0.5568 | 0.55859 | 0.52234 | 0.54316 | 0.55799 | 0.69472
43602.7497 | 0.56064 | 0.58145 | 0.55736 | 0.55907 | 0.5228 | 0.54349 | 0.55727 | 0.69472
43602.7497 | 0.56064 | 0.58119 | 0.55692 | 0.55866 | 0.52277 | 0.54359 | 0.55707 | 0.69459
43602.7497 | 0.56 | 0.58049 | 0.55634 | 0.55824 | 0.52225 | 0.54288 | 0.55723 | 0.69439
43602.7499 | 0.5605 | 0.58116 | 0.55717 | 0.55892 | 0.52237 | 0.54321 | 0.56134 | 0.69443
43602.7499 | 0.56028 | 0.58103 | 0.55675 | 0.55836 | 0.52235 | 0.54312 | 0.55763 | 0.69441
43602.7499 | 0.55964 | 0.58085 | 0.5569 | 0.55844 | 0.52273 | 0.54332 | 0.55657 | 0.69432
43602.7501 | 0.56058 | 0.581 | 0.55737 | 0.55878 | 0.52242 | 0.54327 | 0.55939 | 0.69436
43602.7501 | 0.5604 | 0.58081 | 0.55704 | 0.55877 | 0.52253 | 0.54336 | 0.55825 | 0.69427
43602.7501 | 0.56052 | 0.58114 | 0.55726 | 0.55923 | 0.52297 | 0.54339 | 0.55654 | 0.69411
43602.7503 | 0.56062 | 0.58113 | 0.55702 | 0.55914 | 0.52305 | 0.54342 | 0.55606 | 0.69426
43602.7504 | 0.56096 | 0.58144 | 0.55739 | 0.55948 | 0.52299 | 0.54335 | 0.55695 | 0.69425
43602.7503 | 0.56046 | 0.5812 | 0.5574 | 0.55912 | 0.52279 | 0.54375 | 0.55794 | 0.69435
43602.7506 | 0.56076 | 0.58143 | 0.55764 | 0.55945 | 0.52348 | 0.54406 | 0.55733 | 0.69423
43602.7506 | 0.56041 | 0.58112 | 0.55724 | 0.55933 | 0.52343 | 0.54421 | 0.55898 | 0.69447
43602.7506 | 0.5614 | 0.58156 | 0.55795 | 0.5596 | 0.52309 | 0.54379 | 0.55728 | 0.6943
43602.7508 | 0.56136 | 0.58192 | 0.55823 | 0.55991 | 0.5239 | 0.54406 | 0.55817 | 0.69411
43602.7508 | 0.56104 | 0.58159 | 0.55792 | 0.55992 | 0.52382 | 0.54452 | 0.56099 | 0.69428
43602.7508 | 0.56139 | 0.58169 | 0.558 | 0.55967 | 0.52324 | 0.54355 | 0.55802 | 0.69418
43602.751 | 0.56095 | 0.58125 | 0.5577 | 0.55944 | 0.52369 | 0.54388 | 0.55773 | 0.69407
43602.751 | 0.56144 | 0.5815 | 0.55813 | 0.55973 | 0.52294 | 0.54342 | 0.55771 | 0.69416
43602.751 | 0.56083 | 0.58078 | 0.55774 | 0.55955 | 0.52283 | 0.54339 | 0.5595 | 0.69396
43602.7512 | 0.56037 | 0.58094 | 0.55783 | 0.55977 | 0.52304 | 0.54352 | 0.55896 | 0.69396
43602.7513 | 0.56084 | 0.58099 | 0.55766 | 0.55981 | 0.5232 | 0.5434 | 0.55708 | 0.69401
43602.7512 | 0.56108 | 0.58155 | 0.55807 | 0.56028 | 0.52364 | 0.54403 | 0.5581 | 0.69404
43602.7515 | 0.5611 | 0.58113 | 0.55805 | 0.56007 | 0.52332 | 0.54363 | 0.55798 | 0.69375
43602.7515 | 0.56049 | 0.58061 | 0.55792 | 0.55967 | 0.52333 | 0.54388 | 0.55811 | 0.69384
43602.7515 | 0.56135 | 0.58147 | 0.55832 | 0.56014 | 0.52306 | 0.54332 | 0.55723 | 0.69343
43602.7517 | 0.56056 | 0.58106 | 0.55766 | 0.55976 | 0.52314 | 0.54337 | 0.56056 | 0.69355
43602.7517 | 0.5607 | 0.58108 | 0.55781 | 0.56007 | 0.52303 | 0.54352 | 0.55738 | 0.69352
43602.7517 | 0.56041 | 0.58047 | 0.5575 | 0.55948 | 0.52292 | 0.54334 | 0.55588 | 0.69332
43602.7519 | 0.56024 | 0.58024 | 0.55708 | 0.55951 | 0.52271 | 0.54278 | 0.55729 | 0.69315
43602.7519 | 0.56139 | 0.58139 | 0.55781 | 0.56016 | 0.52305 | 0.54318 | 0.55749 | 0.69337
43602.7519 | 0.56064 | 0.5808 | 0.55754 | 0.55951 | 0.52238 | 0.54287 | 0.5584 | 0.693
43602.7522 | 0.56044 | 0.58073 | 0.55713 | 0.55955 | 0.52266 | 0.54265 | 0.55721 | 0.6931
43602.7522 | 0.56011 | 0.58057 | 0.557 | 0.5594 | 0.52263 | 0.54296 | 0.55627 | 0.69293
43602.7522 | 0.5615 | 0.58143 | 0.55771 | 0.56017 | 0.52295 | 0.5429 | 0.55693 | 0.69274
43602.7524 | 0.561 | 0.58098 | 0.55779 | 0.56049 | 0.52278 | 0.54285 | 0.55626 | 0.69264
43602.7524 | 0.56014 | 0.58005 | 0.55691 | 0.5598 | 0.52288 | 0.54299 | 0.55595 | 0.69271
43602.7524 | 0.55975 | 0.58014 | 0.55676 | 0.55944 | 0.52216 | 0.54239 | 0.55597 | 0.69241
43602.7526 | 0.5591 | 0.57939 | 0.55574 | 0.55883 | 0.52204 | 0.54208 | 0.55618 | 0.69222
43602.7526 | 0.55944 | 0.57966 | 0.55611 | 0.55925 | 0.52159 | 0.54167 | 0.55604 | 0.69206
43602.7526 | 0.55981 | 0.57989 | 0.55634 | 0.55891 | 0.52186 | 0.54214 | 0.55456 | 0.69236
43602.7528 | 0.55922 | 0.5795 | 0.55586 | 0.5588 | 0.52177 | 0.54213 | 0.55662 | 0.69188
43602.7529 | 0.55945 | 0.57972 | 0.55645 | 0.55919 | 0.52147 | 0.5414 | 0.55568 | 0.69188
43602.7528 | 0.56038 | 0.58054 | 0.55697 | 0.55964 | 0.52215 | 0.54209 | 0.55558 | 0.69199
43602.7531 | 0.5588 | 0.57923 | 0.55626 | 0.55909 | 0.52162 | 0.54197 | 0.55597 | 0.69216
43602.7531 | 0.55969 | 0.57983 | 0.55662 | 0.55929 | 0.52216 | 0.54217 | 0.55502 | 0.6921
43602.7531 | 0.56033 | 0.58061 | 0.5575 | 0.55988 | 0.52212 | 0.54242 | 0.55807 | 0.69213
43602.7533 | 0.56019 | 0.58052 | 0.55744 | 0.55994 | 0.52244 | 0.54277 | 0.55566 | 0.69218
43602.7533 | 0.56092 | 0.581 | 0.55744 | 0.56035 | 0.52267 | 0.54295 | 0.55707 | 0.6923
43602.7533 | 0.56048 | 0.58054 | 0.5576 | 0.56011 | 0.52301 | 0.54327 | 0.5554 | 0.6922
43602.7535 | 0.56069 | 0.58102 | 0.55783 | 0.56064 | 0.52278 | 0.54303 | 0.55699 | 0.6924
43602.7535 | 0.56016 | 0.58064 | 0.55735 | 0.56041 | 0.52299 | 0.54314 | 0.55643 | 0.69236
43602.7535 | 0.56021 | 0.58076 | 0.55812 | 0.56061 | 0.52332 | 0.54307 | 0.556 | 0.69236
43602.7538 | 0.56201 | 0.58192 | 0.55848 | 0.56105 | 0.5236 | 0.54318 | 0.55614 | 0.69212
43602.7538 | 0.56114 | 0.58145 | 0.55844 | 0.56089 | 0.52407 | 0.54339 | 0.55582 | 0.69229
43602.7539 | 0.56132 | 0.58162 | 0.5581 | 0.56123 | 0.5231 | 0.54295 | 0.55785 | 0.69222
43602.7539 | 0.56205 | 0.58208 | 0.55837 | 0.56137 | 0.52369 | 0.54349 | 0.55666 | 0.69215
43602.7539 | 0.56117 | 0.58162 | 0.55825 | 0.5609 | 0.52352 | 0.54312 | 0.55615 | 0.69219
43602.7542 | 0.56065 | 0.5807 | 0.55828 | 0.56069 | 0.52327 | 0.54356 | 0.55844 | 0.69235
43602.7542 | 0.56077 | 0.58086 | 0.55835 | 0.56082 | 0.52346 | 0.5436 | 0.55646 | 0.69227
43602.7541 | 0.56215 | 0.58151 | 0.55828 | 0.56103 | 0.52341 | 0.54319 | 0.55824 | 0.69201
43602.7544 | 0.56109 | 0.58115 | 0.55818 | 0.56127 | 0.52391 | 0.54403 | 0.55644 | 0.69214
43602.7544 | 0.56134 | 0.58113 | 0.55809 | 0.56109 | 0.52341 | 0.54346 | 0.55497 | 0.6919
43602.7544 | 0.5618 | 0.58171 | 0.55841 | 0.56183 | 0.52409 | 0.54394 | 0.5582 | 0.6919
43602.7546 | 0.56232 | 0.58204 | 0.55864 | 0.56183 | 0.52394 | 0.54367 | 0.55625 | 0.69186
43602.7546 | 0.56196 | 0.58192 | 0.559 | 0.56191 | 0.52421 | 0.54389 | 0.55735 | 0.69193
43602.7546 | 0.56215 | 0.58235 | 0.55904 | 0.56224 | 0.52421 | 0.54424 | 0.55795 | 0.69205
43602.7548 | 0.56298 | 0.58298 | 0.56007 | 0.56343 | 0.52543 | 0.545 | 0.5579 | 0.69226
43602.7549 | 0.56282 | 0.58287 | 0.56013 | 0.56351 | 0.52564 | 0.54517 | 0.55752 | 0.69225
43602.7548 | 0.56315 | 0.58291 | 0.55966 | 0.56346 | 0.52536 | 0.54485 | 0.55914 | 0.69211
43602.7551 | 0.56486 | 0.58506 | 0.56172 | 0.56527 | 0.52711 | 0.54612 | 0.55787 | 0.69281
43602.7551 | 0.5638 | 0.58401 | 0.56097 | 0.56473 | 0.52701 | 0.54658 | 0.5587 | 0.69295
43602.7552 | 0.5651 | 0.58517 | 0.56213 | 0.56591 | 0.52813 | 0.54732 | 0.558 | 0.69334
43602.7553 | 0.56485 | 0.58482 | 0.56229 | 0.56557 | 0.52759 | 0.54717 | 0.5622 | 0.69326
43602.7552 | 0.56526 | 0.58501 | 0.56261 | 0.56577 | 0.52869 | 0.54795 | 0.56174 | 0.69341
43602.7555 | 0.56613 | 0.58598 | 0.56379 | 0.56756 | 0.52965 | 0.5487 | 0.55964 | 0.69399
43602.7555 | 0.56671 | 0.58692 | 0.56449 | 0.56806 | 0.5299 | 0.54874 | 0.55878 | 0.69409
43602.7555 | 0.56752 | 0.58732 | 0.56451 | 0.5681 | 0.53069 | 0.54952 | 0.56158 | 0.69441
43602.7557 | 0.56865 | 0.58832 | 0.56585 | 0.56992 | 0.53137 | 0.55053 | 0.56222 | 0.69503
43602.7557 | 0.56839 | 0.58848 | 0.56615 | 0.56987 | 0.53228 | 0.55141 | 0.56259 | 0.69544
43602.7557 | 0.56885 | 0.58899 | 0.56625 | 0.57027 | 0.53224 | 0.55116 | 0.56114 | 0.69546
43602.7559 | 0.56995 | 0.58986 | 0.56807 | 0.57178 | 0.53449 | 0.55332 | 0.56271 | 0.6963
43602.7559 | 0.57021 | 0.5903 | 0.56803 | 0.5719 | 0.53395 | 0.55288 | 0.56396 | 0.69647
43602.7561 | 0.57098 | 0.59071 | 0.56875 | 0.57272 | 0.53506 | 0.55409 | 0.56482 | 0.69717
43602.7561 | 0.57173 | 0.59152 | 0.5697 | 0.57356 | 0.53588 | 0.55473 | 0.56495 | 0.69729
43602.7561 | 0.57177 | 0.59154 | 0.56984 | 0.57392 | 0.53626 | 0.55524 | 0.56517 | 0.69762
43602.7563 | 0.57318 | 0.59256 | 0.5708 | 0.5753 | 0.53789 | 0.55673 | 0.56846 | 0.6981
43602.7563 | 0.57334 | 0.59306 | 0.57134 | 0.57554 | 0.5384 | 0.55686 | 0.56805 | 0.69831
43602.7563 | 0.57337 | 0.59268 | 0.57116 | 0.57539 | 0.53829 | 0.55727 | 0.56652 | 0.69839
43602.7566 | 0.57373 | 0.5932 | 0.57185 | 0.57588 | 0.53903 | 0.55774 | 0.56969 | 0.69892
43602.7566 | 0.57398 | 0.5934 | 0.57184 | 0.57625 | 0.53917 | 0.55794 | 0.56764 | 0.69895
43602.7566 | 0.57444 | 0.59362 | 0.57235 | 0.57645 | 0.53956 | 0.55814 | 0.56814 | 0.69932
43602.7568 | 0.5751 | 0.5943 | 0.573 | 0.57759 | 0.54034 | 0.55876 | 0.5683 | 0.6995
43602.7568 | 0.57521 | 0.5943 | 0.57305 | 0.57754 | 0.54 | 0.55853 | 0.56804 | 0.69938
43602.7568 | 0.57561 | 0.59467 | 0.57342 | 0.57798 | 0.54057 | 0.55895 | 0.57054 | 0.69949
43602.757 | 0.57542 | 0.59436 | 0.57341 | 0.57766 | 0.5406 | 0.55925 | 0.56924 | 0.69966
43602.7571 | 0.57535 | 0.59446 | 0.57353 | 0.57802 | 0.54112 | 0.5594 | 0.56919 | 0.69966
43602.757 | 0.57528 | 0.59442 | 0.57356 | 0.57794 | 0.54076 | 0.55912 | 0.56863 | 0.69996
43602.7573 | 0.57551 | 0.59494 | 0.57362 | 0.57859 | 0.54129 | 0.55964 | 0.5697 | 0.6999
43602.7573 | 0.57527 | 0.59516 | 0.57358 | 0.57855 | 0.54117 | 0.55965 | 0.56832 | 0.69972
43602.7573 | 0.57508 | 0.59456 | 0.57358 | 0.57847 | 0.541 | 0.55977 | 0.57089 | 0.69982
43602.7575 | 0.57531 | 0.59493 | 0.57358 | 0.57873 | 0.5414 | 0.55973 | 0.56943 | 0.69971
43602.7575 | 0.57527 | 0.595 | 0.57357 | 0.57903 | 0.54132 | 0.55981 | 0.56843 | 0.69968
43602.7575 | 0.57478 | 0.59467 | 0.57347 | 0.57859 | 0.54122 | 0.55963 | 0.56869 | 0.69941
43602.7578 | 0.57454 | 0.59419 | 0.57336 | 0.57848 | 0.54083 | 0.55905 | 0.56884 | 0.69917
43602.7578 | 0.57445 | 0.59393 | 0.57305 | 0.57834 | 0.54108 | 0.5592 | 0.56908 | 0.69923
43602.7577 | 0.57513 | 0.59462 | 0.57363 | 0.57859 | 0.54079 | 0.55923 | 0.57298 | 0.6995
43602.758 | 0.57422 | 0.59366 | 0.57297 | 0.57807 | 0.54045 | 0.55914 | 0.56776 | 0.69894
43602.758 | 0.57386 | 0.59318 | 0.5725 | 0.57778 | 0.54039 | 0.55884 | 0.56981 | 0.69901
43602.758 | 0.57393 | 0.59347 | 0.57263 | 0.57801 | 0.54044 | 0.55851 | 0.56848 | 0.69866
43602.7582 | 0.5737 | 0.59343 | 0.57271 | 0.57812 | 0.54057 | 0.55884 | 0.56911 | 0.69851
43602.7582 | 0.57343 | 0.59325 | 0.57232 | 0.57774 | 0.54019 | 0.55839 | 0.56776 | 0.69847
43602.7582 | 0.57338 | 0.593 | 0.57178 | 0.57733 | 0.53984 | 0.55785 | 0.56805 | 0.69828
43602.7585 | 0.57342 | 0.5933 | 0.57224 | 0.57763 | 0.5397 | 0.5578 | 0.56807 | 0.69795
43602.7585 | 0.57313 | 0.59278 | 0.57161 | 0.57724 | 0.53971 | 0.55788 | 0.56736 | 0.69824
43602.7585 | 0.57245 | 0.59186 | 0.57116 | 0.57659 | 0.53898 | 0.55723 | 0.5668 | 0.69785
43602.7587 | 0.57191 | 0.59133 | 0.5707 | 0.57603 | 0.5384 | 0.55626 | 0.56565 | 0.69751
43602.7587 | 0.572 | 0.59142 | 0.57087 | 0.57625 | 0.53833 | 0.55664 | 0.5672 | 0.69736
43602.7587 | 0.57157 | 0.59079 | 0.57029 | 0.57594 | 0.53844 | 0.55655 | 0.56636 | 0.69727
43602.7589 | 0.57076 | 0.59069 | 0.56993 | 0.57539 | 0.53792 | 0.55628 | 0.56559 | 0.69697
43602.7589 | 0.57048 | 0.59017 | 0.56938 | 0.57513 | 0.53704 | 0.55561 | 0.56663 | 0.69675
43602.7589 | 0.57094 | 0.59051 | 0.56978 | 0.57502 | 0.53767 | 0.55574 | 0.56679 | 0.69667
43602.7592 | 0.5704 | 0.58964 | 0.56941 | 0.57454 | 0.53716 | 0.55536 | 0.56424 | 0.69617
43602.7592 | 0.57047 | 0.59001 | 0.56938 | 0.57454 | 0.53696 | 0.55508 | 0.56437 | 0.69613
43602.7592 | 0.57083 | 0.59052 | 0.56992 | 0.57482 | 0.53687 | 0.55499 | 0.56476 | 0.69594
43602.7594 | 0.56993 | 0.58996 | 0.56925 | 0.57453 | 0.53677 | 0.55499 | 0.56513 | 0.69571
43602.7594 | 0.57016 | 0.5897 | 0.56891 | 0.57427 | 0.5368 | 0.55498 | 0.56432 | 0.69581
43602.7594 | 0.56872 | 0.58825 | 0.56823 | 0.57349 | 0.53587 | 0.55422 | 0.5639 | 0.69531
43602.7596 | 0.56939 | 0.58916 | 0.56844 | 0.57385 | 0.53638 | 0.5546 | 0.56361 | 0.69541
43602.7597 | 0.56892 | 0.58828 | 0.56781 | 0.57318 | 0.53555 | 0.55389 | 0.56569 | 0.69532
43602.7596 | 0.56882 | 0.58854 | 0.56794 | 0.57344 | 0.53567 | 0.55364 | 0.56448 | 0.69494
43602.7599 | 0.56812 | 0.58785 | 0.56766 | 0.57303 | 0.53537 | 0.55381 | 0.56285 | 0.69464
43602.7599 | 0.56834 | 0.58788 | 0.56764 | 0.57278 | 0.53502 | 0.55334 | 0.56422 | 0.69463
43602.7599 | 0.56871 | 0.5883 | 0.56797 | 0.57344 | 0.53521 | 0.55341 | 0.56159 | 0.69452
43602.7601 | 0.5683 | 0.58766 | 0.56745 | 0.57284 | 0.53474 | 0.55283 | 0.56302 | 0.69479
43602.7601 | 0.56878 | 0.58846 | 0.56785 | 0.57346 | 0.53547 | 0.55361 | 0.56406 | 0.69478
43602.7601 | 0.56905 | 0.58853 | 0.56834 | 0.57398 | 0.53597 | 0.5543 | 0.56493 | 0.69486
43602.7604 | 0.5688 | 0.58883 | 0.56835 | 0.57383 | 0.53641 | 0.55461 | 0.56344 | 0.69517
43602.7604 | 0.56868 | 0.58882 | 0.56817 | 0.5737 | 0.53579 | 0.55393 | 0.5646 | 0.69461
43602.7603 | 0.56878 | 0.58839 | 0.56809 | 0.57381 | 0.53578 | 0.55385 | 0.56263 | 0.69461
43602.7606 | 0.56843 | 0.58807 | 0.56747 | 0.57323 | 0.53546 | 0.55338 | 0.56625 | 0.69447
43602.7606 | 0.56896 | 0.58866 | 0.56836 | 0.57403 | 0.53583 | 0.55388 | 0.56366 | 0.69438
43602.7606 | 0.5676 | 0.58743 | 0.56795 | 0.57339 | 0.53587 | 0.55379 | 0.56372 | 0.69444
43602.7608 | 0.56903 | 0.58916 | 0.56841 | 0.57445 | 0.53692 | 0.5549 | 0.56659 | 0.69501
43602.7608 | 0.56897 | 0.58874 | 0.56783 | 0.57399 | 0.53635 | 0.55412 | 0.56519 | 0.69472
43602.7608 | 0.56807 | 0.58816 | 0.56844 | 0.57377 | 0.53616 | 0.55412 | 0.56352 | 0.69455
43602.7611 | 0.56923 | 0.5889 | 0.56866 | 0.57432 | 0.53658 | 0.55458 | 0.56462 | 0.69504
43602.7611 | 0.56838 | 0.58818 | 0.56813 | 0.57358 | 0.53638 | 0.55454 | 0.5632 | 0.69464
43602.761 | 0.56827 | 0.58823 | 0.56814 | 0.57389 | 0.53681 | 0.55459 | 0.56354 | 0.69477
43602.7613 | 0.56944 | 0.58909 | 0.56879 | 0.57459 | 0.53715 | 0.55497 | 0.56489 | 0.69497
43602.7613 | 0.56948 | 0.5893 | 0.5692 | 0.57502 | 0.53771 | 0.5555 | 0.56487 | 0.69508
43602.7613 | 0.56915 | 0.58905 | 0.56939 | 0.57518 | 0.53758 | 0.55554 | 0.56422 | 0.69518
43602.7615 | 0.56876 | 0.58904 | 0.56868 | 0.57497 | 0.53719 | 0.55539 | 0.56541 | 0.69507
43602.7615 | 0.56853 | 0.58855 | 0.5682 | 0.57427 | 0.53708 | 0.55524 | 0.56451 | 0.69505
43602.7615 | 0.56912 | 0.58898 | 0.56896 | 0.57498 | 0.5372 | 0.55508 | 0.56663 | 0.69485
43602.7618 | 0.56939 | 0.58935 | 0.5688 | 0.57485 | 0.53789 | 0.55592 | 0.56418 | 0.69507
43602.7618 | 0.56829 | 0.58834 | 0.56828 | 0.57416 | 0.53732 | 0.55516 | 0.56652 | 0.69477
43602.7618 | 0.56909 | 0.58884 | 0.56917 | 0.57502 | 0.53761 | 0.55563 | 0.56615 | 0.69515
43602.762 | 0.56913 | 0.589 | 0.56844 | 0.57499 | 0.5371 | 0.55509 | 0.56331 | 0.69471
43602.762 | 0.56886 | 0.58895 | 0.5687 | 0.57512 | 0.53763 | 0.55568 | 0.56378 | 0.69491
43602.762 | 0.56874 | 0.58878 | 0.56914 | 0.57507 | 0.53817 | 0.55622 | 0.56536 | 0.69529
43602.7622 | 0.56907 | 0.58896 | 0.56992 | 0.57524 | 0.53827 | 0.55581 | 0.56422 | 0.69489
43602.7623 | 0.56857 | 0.58836 | 0.569 | 0.57484 | 0.53782 | 0.55567 | 0.56434 | 0.69496
43602.7622 | 0.56857 | 0.5884 | 0.56898 | 0.57492 | 0.53769 | 0.55542 | 0.56486 | 0.69461
43602.7625 | 0.56952 | 0.58892 | 0.56844 | 0.57493 | 0.53781 | 0.55569 | 0.56389 | 0.69477
43602.7625 | 0.56907 | 0.58848 | 0.568 | 0.57422 | 0.53736 | 0.55513 | 0.56728 | 0.69448
43602.7625 | 0.56923 | 0.58845 | 0.56833 | 0.57477 | 0.53773 | 0.55534 | 0.56698 | 0.69451
43602.7627 | 0.56803 | 0.58787 | 0.56803 | 0.57476 | 0.5379 | 0.55552 | 0.56429 | 0.69466
43602.7627 | 0.56814 | 0.5881 | 0.56832 | 0.57459 | 0.53778 | 0.55569 | 0.56437 | 0.69461
43602.7627 | 0.56826 | 0.58807 | 0.56829 | 0.5743 | 0.53717 | 0.5551 | 0.56412 | 0.69441
43602.7629 | 0.56836 | 0.58788 | 0.56686 | 0.574 | 0.53713 | 0.55506 | 0.5659 | 0.6941
43602.763 | 0.56829 | 0.58835 | 0.56827 | 0.57467 | 0.53713 | 0.55525 | 0.56439 | 0.69415
43602.7629 | 0.56865 | 0.58849 | 0.56837 | 0.57466 | 0.53731 | 0.55512 | 0.56343 | 0.6942
43602.7632 | 0.56849 | 0.58785 | 0.56853 | 0.57487 | 0.53747 | 0.55526 | 0.56444 | 0.69401
43602.7632 | 0.56793 | 0.58751 | 0.56796 | 0.57449 | 0.5373 | 0.55522 | 0.56362 | 0.69415
43602.7632 | 0.56763 | 0.58722 | 0.56781 | 0.5741 | 0.53716 | 0.55533 | 0.56326 | 0.69402
43602.7634 | 0.56799 | 0.58758 | 0.56796 | 0.57428 | 0.53718 | 0.555 | 0.5635 | 0.6941
43602.7634 | 0.56823 | 0.58774 | 0.56869 | 0.57498 | 0.53747 | 0.55536 | 0.56356 | 0.69413
43602.7634 | 0.56785 | 0.58726 | 0.56832 | 0.57454 | 0.53743 | 0.55518 | 0.56544 | 0.69424
43602.7637 | 0.56686 | 0.58692 | 0.5667 | 0.57394 | 0.53702 | 0.55501 | 0.56269 | 0.69401
43602.7637 | 0.56735 | 0.58755 | 0.56821 | 0.57464 | 0.53719 | 0.55484 | 0.56688 | 0.6938
43602.7636 | 0.56691 | 0.58716 | 0.56814 | 0.57456 | 0.53701 | 0.55476 | 0.56356 | 0.69384
43602.7639 | 0.56756 | 0.58687 | 0.56747 | 0.57438 | 0.53765 | 0.55521 | 0.56571 | 0.69404
43602.7639 | 0.56783 | 0.5867 | 0.567 | 0.57406 | 0.53713 | 0.55506 | 0.56402 | 0.69388
43602.7639 | 0.5666 | 0.58622 | 0.56744 | 0.57397 | 0.53734 | 0.55512 | 0.56329 | 0.69383
43602.7641 | 0.56655 | 0.58738 | 0.56844 | 0.57451 | 0.53721 | 0.55488 | 0.56376 | 0.6936
43602.7641 | 0.56675 | 0.58724 | 0.56835 | 0.57457 | 0.53758 | 0.55536 | 0.56533 | 0.69373
43602.7641 | 0.56803 | 0.58734 | 0.567 | 0.57431 | 0.53738 | 0.55501 | 0.56587 | 0.69391
43602.7644 | 0.56703 | 0.58678 | 0.56817 | 0.57469 | 0.53772 | 0.55546 | 0.56308 | 0.69376
43602.7644 | 0.56794 | 0.58743 | 0.56898 | 0.575 | 0.53806 | 0.55559 | 0.56732 | 0.69395
43602.7643 | 0.56767 | 0.58737 | 0.5684 | 0.57469 | 0.53729 | 0.55504 | 0.56478 | 0.6936
43602.7646 | 0.56768 | 0.58698 | 0.56824 | 0.57487 | 0.5379 | 0.5555 | 0.56444 | 0.69398
43602.7646 | 0.56759 | 0.58685 | 0.56817 | 0.57494 | 0.53819 | 0.55568 | 0.56379 | 0.69394
43602.7646 | 0.56693 | 0.58731 | 0.5692 | 0.57495 | 0.53813 | 0.5555 | 0.56639 | 0.69383
43602.7648 | 0.56667 | 0.58642 | 0.56768 | 0.57467 | 0.53749 | 0.55506 | 0.56402 | 0.69346
43602.7648 | 0.56667 | 0.58626 | 0.56792 | 0.5745 | 0.53734 | 0.55516 | 0.56612 | 0.69357
43602.7648 | 0.56671 | 0.58615 | 0.56773 | 0.57457 | 0.53763 | 0.5556 | 0.56495 | 0.69377
43602.7651 | 0.56661 | 0.58677 | 0.56837 | 0.57516 | 0.53754 | 0.55512 | 0.56625 | 0.69345
43602.7651 | 0.56766 | 0.5872 | 0.56874 | 0.57529 | 0.53761 | 0.55527 | 0.5654 | 0.69371
43602.765 | 0.56688 | 0.58667 | 0.56764 | 0.57447 | 0.53761 | 0.55497 | 0.56367 | 0.69355
43602.7653 | 0.56677 | 0.58628 | 0.56769 | 0.57483 | 0.53763 | 0.55543 | 0.56692 | 0.69355
43602.7653 | 0.56615 | 0.5854 | 0.56722 | 0.57444 | 0.53735 | 0.55512 | 0.56473 | 0.69354
43602.7653 | 0.56715 | 0.58667 | 0.56819 | 0.57505 | 0.53782 | 0.55539 | 0.56322 | 0.69378
43602.7655 | 0.56672 | 0.58613 | 0.56749 | 0.5746 | 0.5379 | 0.55514 | 0.56324 | 0.69351
43602.7655 | 0.56658 | 0.5864 | 0.56749 | 0.57467 | 0.53746 | 0.55505 | 0.56284 | 0.69329
43602.7655 | 0.56725 | 0.58667 | 0.56872 | 0.57522 | 0.5382 | 0.55559 | 0.56396 | 0.69377
43602.7658 | 0.5658 | 0.58565 | 0.56797 | 0.57448 | 0.53726 | 0.55483 | 0.56354 | 0.69319
43602.7658 | 0.56666 | 0.58601 | 0.5678 | 0.57448 | 0.53732 | 0.55497 | 0.56492 | 0.69317
43602.7658 | 0.56685 | 0.58652 | 0.56847 | 0.57485 | 0.5374 | 0.55498 | 0.56644 | 0.69306
43602.766 | 0.56647 | 0.58616 | 0.56806 | 0.57487 | 0.53811 | 0.55543 | 0.56414 | 0.69337
43602.766 | 0.56612 | 0.58544 | 0.56677 | 0.57428 | 0.53751 | 0.55478 | 0.56232 | 0.69306
43602.766 | 0.56648 | 0.58577 | 0.56721 | 0.57494 | 0.53803 | 0.55539 | 0.569 | 0.69334
43602.7662 | 0.56651 | 0.58621 | 0.56818 | 0.57509 | 0.53743 | 0.55497 | 0.564 | 0.69311
43602.7662 | 0.56661 | 0.58625 | 0.56815 | 0.57485 | 0.53765 | 0.55532 | 0.56297 | 0.69327
43602.7662 | 0.56654 | 0.58614 | 0.56849 | 0.57541 | 0.53786 | 0.55512 | 0.56374 | 0.69315
43602.7665 | 0.566 | 0.5854 | 0.56695 | 0.57437 | 0.53713 | 0.55492 | 0.56425 | 0.69302
43602.7665 | 0.56637 | 0.58533 | 0.56687 | 0.57463 | 0.53691 | 0.55462 | 0.56288 | 0.69273
43602.7665 | 0.56604 | 0.58528 | 0.56644 | 0.57444 | 0.53687 | 0.55449 | 0.5656 | 0.69282
43602.7667 | 0.56585 | 0.58529 | 0.56763 | 0.57495 | 0.53719 | 0.5547 | 0.56676 | 0.69268
43602.7667 | 0.56617 | 0.58603 | 0.56811 | 0.57511 | 0.53777 | 0.5552 | 0.56509 | 0.69307
43602.7669 | 0.56614 | 0.58643 | 0.56864 | 0.57518 | 0.53771 | 0.55501 | 0.56494 | 0.69307
43602.7669 | 0.56596 | 0.58611 | 0.56839 | 0.57507 | 0.53788 | 0.55545 | 0.56366 | 0.693
43602.7669 | 0.56577 | 0.58489 | 0.56742 | 0.57456 | 0.53726 | 0.55447 | 0.56335 | 0.69272
43602.7671 | 0.56557 | 0.58477 | 0.56683 | 0.57436 | 0.53715 | 0.5545 | 0.56285 | 0.69254
43602.7671 | 0.56554 | 0.58498 | 0.56692 | 0.57436 | 0.53704 | 0.55438 | 0.56583 | 0.69248
43602.7671 | 0.56507 | 0.58493 | 0.56742 | 0.57458 | 0.53702 | 0.55444 | 0.56324 | 0.69244
43602.7674 | 0.56566 | 0.58489 | 0.56746 | 0.5746 | 0.53743 | 0.55496 | 0.56413 | 0.69272
43602.7674 | 0.56614 | 0.58518 | 0.56722 | 0.57448 | 0.53716 | 0.55466 | 0.56357 | 0.69263
43602.7673 | 0.56547 | 0.5854 | 0.5681 | 0.57496 | 0.53727 | 0.55472 | 0.5629 | 0.69256
43602.7676 | 0.56618 | 0.5858 | 0.56828 | 0.57555 | 0.53804 | 0.55545 | 0.56425 | 0.69307
43602.7676 | 0.56588 | 0.58553 | 0.56771 | 0.57492 | 0.53799 | 0.55532 | 0.56338 | 0.69281
43602.7676 | 0.56558 | 0.58512 | 0.56698 | 0.57405 | 0.53719 | 0.55463 | 0.56332 | 0.69251
43602.7678 | 0.5664 | 0.586 | 0.56831 | 0.57571 | 0.53801 | 0.55543 | 0.56522 | 0.69285
43602.7678 | 0.56613 | 0.58603 | 0.56827 | 0.57539 | 0.53833 | 0.55569 | 0.56525 | 0.69317
43602.7678 | 0.56643 | 0.58586 | 0.56757 | 0.57492 | 0.53749 | 0.55495 | 0.56326 | 0.69282
43602.7681 | 0.56621 | 0.58612 | 0.56893 | 0.57581 | 0.53834 | 0.55568 | 0.56735 | 0.69294
43602.7681 | 0.56613 | 0.58585 | 0.56882 | 0.57561 | 0.53829 | 0.55563 | 0.56417 | 0.6929
43602.768 | 0.56561 | 0.58543 | 0.56787 | 0.57505 | 0.53717 | 0.55478 | 0.56314 | 0.69235
43602.7683 | 0.56637 | 0.58552 | 0.56826 | 0.5754 | 0.53775 | 0.55502 | 0.56437 | 0.69287
43602.7683 | 0.56608 | 0.58557 | 0.56833 | 0.57544 | 0.53817 | 0.55529 | 0.5634 | 0.69308
43602.7683 | 0.56554 | 0.58553 | 0.56802 | 0.57509 | 0.53808 | 0.55508 | 0.56375 | 0.69298
43602.7685 | 0.56578 | 0.58546 | 0.56822 | 0.57523 | 0.538 | 0.55532 | 0.56471 | 0.69283
43602.7685 | 0.56564 | 0.58542 | 0.56824 | 0.57527 | 0.53802 | 0.55513 | 0.56333 | 0.69268
43602.7685 | 0.56532 | 0.58523 | 0.56795 | 0.57508 | 0.53777 | 0.55503 | 0.56463 | 0.69249
43602.7688 | 0.56626 | 0.58575 | 0.56861 | 0.57612 | 0.53845 | 0.55555 | 0.56351 | 0.69289
43602.7688 | 0.56631 | 0.58556 | 0.56849 | 0.576 | 0.53873 | 0.55589 | 0.56397 | 0.69295
43602.7687 | 0.56568 | 0.58552 | 0.56864 | 0.57549 | 0.53826 | 0.55524 | 0.56376 | 0.69245
43602.769 | 0.56497 | 0.58508 | 0.56815 | 0.57511 | 0.53846 | 0.55528 | 0.56591 | 0.69265
43602.769 | 0.56564 | 0.58529 | 0.56849 | 0.57577 | 0.53842 | 0.55514 | 0.5638 | 0.69273
43602.769 | 0.5653 | 0.58553 | 0.56859 | 0.57568 | 0.53887 | 0.55542 | 0.56338 | 0.69271
43602.7692 | 0.56555 | 0.58529 | 0.56841 | 0.57564 | 0.53875 | 0.55564 | 0.56355 | 0.69292
43602.7692 | 0.56526 | 0.58493 | 0.5675 | 0.57503 | 0.53794 | 0.55489 | 0.5628 | 0.69236
43602.7692 | 0.56509 | 0.58512 | 0.56828 | 0.57537 | 0.53846 | 0.55536 | 0.56372 | 0.69247
43602.7695 | 0.56523 | 0.58484 | 0.56791 | 0.5754 | 0.53848 | 0.55549 | 0.5636 | 0.69246
43602.7695 | 0.56596 | 0.58579 | 0.56872 | 0.57583 | 0.53856 | 0.55553 | 0.56378 | 0.6925
43602.7694 | 0.56583 | 0.58542 | 0.56818 | 0.57537 | 0.539 | 0.5555 | 0.56306 | 0.69272
43602.7697 | 0.56571 | 0.58541 | 0.56833 | 0.5755 | 0.53824 | 0.55512 | 0.56649 | 0.69248
43602.7697 | 0.56596 | 0.5855 | 0.56851 | 0.57554 | 0.53846 | 0.55527 | 0.5642 | 0.69245
43602.7697 | 0.56575 | 0.58508 | 0.5681 | 0.57572 | 0.53818 | 0.55476 | 0.56305 | 0.69242
43602.7699 | 0.56547 | 0.58495 | 0.56799 | 0.57515 | 0.53796 | 0.55485 | 0.56362 | 0.69228
43602.7699 | 0.5657 | 0.58531 | 0.56848 | 0.57551 | 0.53816 | 0.55511 | 0.56259 | 0.69237
43602.7699 | 0.56571 | 0.5854 | 0.56822 | 0.5755 | 0.53834 | 0.55517 | 0.56348 | 0.69247
43602.7702 | 0.5664 | 0.58564 | 0.56902 | 0.57605 | 0.5389 | 0.55536 | 0.56266 | 0.69264
43602.7702 | 0.56599 | 0.58538 | 0.56858 | 0.57564 | 0.53892 | 0.5552 | 0.56632 | 0.69281
43602.7702 | 0.56625 | 0.5856 | 0.56842 | 0.57614 | 0.53943 | 0.55585 | 0.5656 | 0.69298
43602.7704 | 0.56729 | 0.58735 | 0.57018 | 0.57752 | 0.53989 | 0.55648 | 0.56486 | 0.69324
43602.7704 | 0.56678 | 0.58657 | 0.5693 | 0.57664 | 0.5402 | 0.55668 | 0.56464 | 0.69333
43602.7704 | 0.56681 | 0.58671 | 0.56945 | 0.57663 | 0.53918 | 0.5557 | 0.56522 | 0.69308
43602.7707 | 0.56627 | 0.58581 | 0.56872 | 0.57598 | 0.53921 | 0.55573 | 0.56356 | 0.69303
43602.7707 | 0.56673 | 0.58619 | 0.56928 | 0.57648 | 0.53886 | 0.55546 | 0.56698 | 0.69261
43602.7706 | 0.56632 | 0.58571 | 0.5685 | 0.57607 | 0.5393 | 0.55567 | 0.56447 | 0.6929
43602.7709 | 0.5664 | 0.58569 | 0.56827 | 0.57595 | 0.53929 | 0.55585 | 0.56375 | 0.69307
43602.7709 | 0.56615 | 0.58551 | 0.56844 | 0.57604 | 0.53902 | 0.55585 | 0.56445 | 0.69292
43602.7709 | 0.56658 | 0.58608 | 0.56883 | 0.57596 | 0.53939 | 0.55598 | 0.56402 | 0.69299
43602.7711 | 0.56674 | 0.58654 | 0.56931 | 0.57663 | 0.54016 | 0.55641 | 0.56705 | 0.69317
43602.7711 | 0.56653 | 0.58663 | 0.56951 | 0.57659 | 0.53972 | 0.55645 | 0.56464 | 0.69314
43602.7711 | 0.56619 | 0.58605 | 0.56886 | 0.57581 | 0.53963 | 0.55599 | 0.5636 | 0.69311
43602.7714 | 0.56641 | 0.58627 | 0.56907 | 0.57609 | 0.53982 | 0.55623 | 0.56465 | 0.69334
43602.7714 | 0.56628 | 0.58601 | 0.56889 | 0.57578 | 0.53956 | 0.55598 | 0.56462 | 0.69325
43602.7714 | 0.56742 | 0.58704 | 0.57026 | 0.57713 | 0.54073 | 0.55712 | 0.56739 | 0.69375
43602.7716 | 0.56711 | 0.5872 | 0.56968 | 0.57704 | 0.54023 | 0.55655 | 0.56541 | 0.69336
43602.7716 | 0.56688 | 0.58679 | 0.56942 | 0.57691 | 0.54057 | 0.55666 | 0.56535 | 0.69341
43602.7716 | 0.56728 | 0.58654 | 0.5694 | 0.57665 | 0.54036 | 0.55663 | 0.56895 | 0.69358
43602.7718 | 0.56701 | 0.58668 | 0.56966 | 0.57688 | 0.54036 | 0.55681 | 0.56625 | 0.69348
43602.7718 | 0.56653 | 0.5865 | 0.5693 | 0.57669 | 0.5403 | 0.55679 | 0.56595 | 0.69362
43602.7718 | 0.56624 | 0.58592 | 0.56886 | 0.57608 | 0.5397 | 0.55599 | 0.56854 | 0.69312
43602.7721 | 0.56675 | 0.58621 | 0.56907 | 0.57639 | 0.53971 | 0.55604 | 0.56513 | 0.69309
43602.7721 | 0.56718 | 0.58644 | 0.56951 | 0.57672 | 0.53999 | 0.55648 | 0.5647 | 0.69332
43602.7721 | 0.56622 | 0.58566 | 0.56866 | 0.57569 | 0.53927 | 0.55576 | 0.56365 | 0.69291
43602.7723 | 0.5658 | 0.58567 | 0.56826 | 0.57561 | 0.53872 | 0.55506 | 0.5633 | 0.69259
43602.7723 | 0.56601 | 0.5862 | 0.56883 | 0.57585 | 0.53916 | 0.55553 | 0.56351 | 0.69278
43602.7723 | 0.56576 | 0.58576 | 0.5685 | 0.57559 | 0.53912 | 0.55539 | 0.56766 | 0.693
43602.7725 | 0.56557 | 0.58575 | 0.56857 | 0.57548 | 0.53893 | 0.55534 | 0.56444 | 0.69267
43602.7726 | 0.56571 | 0.5858 | 0.56853 | 0.57552 | 0.539 | 0.55558 | 0.56374 | 0.69276
43602.7725 | 0.56568 | 0.58562 | 0.56844 | 0.57519 | 0.53895 | 0.55519 | 0.56553 | 0.69292
43602.7728 | 0.5659 | 0.5859 | 0.56898 | 0.57608 | 0.53948 | 0.55577 | 0.56362 | 0.69301
43602.7728 | 0.56552 | 0.58579 | 0.56866 | 0.57548 | 0.53919 | 0.55563 | 0.5658 | 0.6929
43602.7728 | 0.56627 | 0.58625 | 0.56948 | 0.57601 | 0.53936 | 0.5558 | 0.56373 | 0.69312
43602.773 | 0.56699 | 0.58691 | 0.5701 | 0.57698 | 0.54025 | 0.55664 | 0.56448 | 0.69345
43602.773 | 0.56699 | 0.58685 | 0.56994 | 0.57707 | 0.54068 | 0.5568 | 0.5687 | 0.69357
43602.773 | 0.56641 | 0.58657 | 0.56929 | 0.57631 | 0.5399 | 0.55612 | 0.56553 | 0.69325
43602.7733 | 0.56691 | 0.58676 | 0.56971 | 0.57666 | 0.54012 | 0.55649 | 0.56767 | 0.69336
43602.7733 | 0.56656 | 0.58675 | 0.56943 | 0.57663 | 0.54009 | 0.55647 | 0.56546 | 0.69357
43602.7733 | 0.56648 | 0.58607 | 0.56896 | 0.57632 | 0.5398 | 0.5562 | 0.56388 | 0.69322
43602.7735 | 0.56689 | 0.58668 | 0.56944 | 0.57638 | 0.53981 | 0.5562 | 0.56388 | 0.69335
43602.7735 | 0.5665 | 0.58619 | 0.56896 | 0.57583 | 0.53999 | 0.55637 | 0.56706 | 0.69337
43602.7735 | 0.56657 | 0.58627 | 0.56913 | 0.57624 | 0.53981 | 0.55613 | 0.56436 | 0.6934
43602.7737 | 0.56617 | 0.58587 | 0.56865 | 0.57554 | 0.53935 | 0.55577 | 0.56568 | 0.69315
43602.7738 | 0.56598 | 0.58591 | 0.56829 | 0.5754 | 0.53878 | 0.55544 | 0.56419 | 0.69292
43602.7737 | 0.56558 | 0.58517 | 0.56769 | 0.57489 | 0.53887 | 0.55488 | 0.56273 | 0.69272
43602.774 | 0.5662 | 0.58591 | 0.56877 | 0.57566 | 0.5392 | 0.55551 | 0.56392 | 0.69289
43602.774 | 0.56599 | 0.58558 | 0.56872 | 0.57557 | 0.53917 | 0.55538 | 0.56318 | 0.6929
43602.774 | 0.56604 | 0.58559 | 0.56842 | 0.57545 | 0.53918 | 0.5555 | 0.56449 | 0.69275
43602.7742 | 0.566 | 0.58618 | 0.56877 | 0.57564 | 0.53931 | 0.55534 | 0.56579 | 0.69276
43602.7742 | 0.56602 | 0.58606 | 0.56889 | 0.57565 | 0.5398 | 0.55588 | 0.56512 | 0.69297
43602.7742 | 0.56559 | 0.58566 | 0.56859 | 0.57552 | 0.53891 | 0.55553 | 0.56431 | 0.69265
43602.7745 | 0.56524 | 0.58516 | 0.5682 | 0.575 | 0.53896 | 0.55498 | 0.56466 | 0.69247
43602.7745 | 0.56516 | 0.58515 | 0.5679 | 0.57501 | 0.53862 | 0.55494 | 0.56324 | 0.69249
43602.7745 | 0.56529 | 0.5853 | 0.56786 | 0.57486 | 0.53846 | 0.55476 | 0.56394 | 0.69235
43602.7747 | 0.56457 | 0.58445 | 0.56725 | 0.57404 | 0.53794 | 0.55387 | 0.56229 | 0.692
43602.7747 | 0.56538 | 0.58545 | 0.56813 | 0.5751 | 0.53841 | 0.55473 | 0.5637 | 0.69245
43602.7747 | 0.56462 | 0.58499 | 0.56755 | 0.57454 | 0.53818 | 0.55456 | 0.56592 | 0.69226
43602.7749 | 0.5645 | 0.58453 | 0.56711 | 0.5743 | 0.53804 | 0.55443 | 0.56242 | 0.69217
43602.775 | 0.56478 | 0.58454 | 0.56719 | 0.5742 | 0.53793 | 0.55417 | 0.56216 | 0.69212
43602.7749 | 0.56449 | 0.58471 | 0.56706 | 0.57456 | 0.53801 | 0.55466 | 0.56312 | 0.69236
43602.7752 | 0.56508 | 0.58492 | 0.56775 | 0.57454 | 0.53861 | 0.5549 | 0.56334 | 0.6926
43602.7752 | 0.56521 | 0.58505 | 0.56784 | 0.57474 | 0.53832 | 0.55473 | 0.56268 | 0.69248
43602.7752 | 0.56487 | 0.58515 | 0.56767 | 0.57481 | 0.53847 | 0.55471 | 0.56567 | 0.69251
43602.7754 | 0.56387 | 0.58368 | 0.56627 | 0.57365 | 0.53706 | 0.55375 | 0.56226 | 0.69191
43602.7754 | 0.56452 | 0.58449 | 0.56696 | 0.57423 | 0.53705 | 0.5536 | 0.56374 | 0.69178
43602.7754 | 0.56495 | 0.58509 | 0.56758 | 0.57465 | 0.53777 | 0.55428 | 0.56402 | 0.69221
43602.7757 | 0.56448 | 0.58472 | 0.56715 | 0.57407 | 0.53744 | 0.5538 | 0.56218 | 0.69202
43602.7757 | 0.56437 | 0.58434 | 0.56666 | 0.57379 | 0.53747 | 0.55371 | 0.56408 | 0.69191
43602.7757 | 0.56492 | 0.58429 | 0.5669 | 0.57402 | 0.53762 | 0.55406 | 0.5619 | 0.69201
43602.7759 | 0.56379 | 0.58407 | 0.5668 | 0.57347 | 0.53721 | 0.5533 | 0.562 | 0.69165
43602.7759 | 0.56389 | 0.58415 | 0.56649 | 0.57367 | 0.53738 | 0.55354 | 0.56222 | 0.69174
43602.7759 | 0.56417 | 0.5842 | 0.56674 | 0.57362 | 0.53706 | 0.55352 | 0.56193 | 0.69165
43602.7761 | 0.56471 | 0.58462 | 0.56739 | 0.57386 | 0.53758 | 0.55405 | 0.567 | 0.69199
43602.7762 | 0.56438 | 0.58432 | 0.56686 | 0.57341 | 0.53749 | 0.55393 | 0.56374 | 0.692
43602.7761 | 0.56515 | 0.58498 | 0.56763 | 0.57423 | 0.53769 | 0.55417 | 0.56215 | 0.69223
43602.7764 | 0.56536 | 0.58553 | 0.56803 | 0.57453 | 0.53805 | 0.55427 | 0.56338 | 0.69222
43602.7764 | 0.56522 | 0.58531 | 0.56779 | 0.57451 | 0.53836 | 0.55463 | 0.56297 | 0.69237
43602.7764 | 0.56508 | 0.58485 | 0.56718 | 0.57394 | 0.5379 | 0.55412 | 0.56271 | 0.69219
43602.7766 | 0.56518 | 0.5853 | 0.56766 | 0.57464 | 0.53795 | 0.55401 | 0.56368 | 0.69211
43602.7766 | 0.56529 | 0.58524 | 0.56776 | 0.57452 | 0.53825 | 0.5544 | 0.56267 | 0.69248
43602.7766 | 0.56488 | 0.58467 | 0.56743 | 0.57403 | 0.53789 | 0.55421 | 0.56511 | 0.69225
43602.7769 | 0.56467 | 0.58438 | 0.56695 | 0.5737 | 0.53751 | 0.55385 | 0.56181 | 0.69211
43602.7769 | 0.56448 | 0.58432 | 0.5671 | 0.57333 | 0.53726 | 0.55353 | 0.56414 | 0.69201
43602.777 | 0.56468 | 0.58469 | 0.56737 | 0.57376 | 0.53797 | 0.55403 | 0.56234 | 0.69227
43602.7771 | 0.56454 | 0.58463 | 0.56735 | 0.57367 | 0.5379 | 0.5541 | 0.56178 | 0.69214
43602.777 | 0.56438 | 0.58453 | 0.56672 | 0.57346 | 0.53762 | 0.55388 | 0.56341 | 0.6921
43602.7773 | 0.56481 | 0.58477 | 0.56737 | 0.574 | 0.53798 | 0.55397 | 0.56224 | 0.69223
43602.7773 | 0.56455 | 0.58453 | 0.56739 | 0.57411 | 0.53794 | 0.55398 | 0.56268 | 0.69209
43602.7773 | 0.56391 | 0.58396 | 0.56667 | 0.57334 | 0.53791 | 0.55393 | 0.56422 | 0.69214
43602.7775 | 0.56439 | 0.58442 | 0.56708 | 0.57397 | 0.53771 | 0.55381 | 0.56459 | 0.69227
43602.7775 | 0.56468 | 0.58446 | 0.56733 | 0.5742 | 0.53804 | 0.55419 | 0.56352 | 0.69232
43602.7777 | 0.56432 | 0.58438 | 0.56684 | 0.57361 | 0.53757 | 0.55389 | 0.56278 | 0.69221
43602.7777 | 0.56418 | 0.58438 | 0.56673 | 0.57358 | 0.53755 | 0.55394 | 0.56192 | 0.69222
43602.7777 | 0.5652 | 0.58512 | 0.56752 | 0.57442 | 0.53826 | 0.55449 | 0.56403 | 0.69235
43602.7779 | 0.56482 | 0.58498 | 0.5674 | 0.57412 | 0.53823 | 0.5541 | 0.56348 | 0.69259
43602.7779 | 0.5651 | 0.58491 | 0.56756 | 0.57425 | 0.53812 | 0.55441 | 0.56265 | 0.69237
43602.7779 | 0.56434 | 0.58474 | 0.56718 | 0.57369 | 0.53741 | 0.5537 | 0.56229 | 0.69202
43602.7782 | 0.564 | 0.58445 | 0.56646 | 0.57339 | 0.53748 | 0.55352 | 0.56285 | 0.69206
43602.7782 | 0.56418 | 0.58451 | 0.56683 | 0.57352 | 0.53717 | 0.55333 | 0.56215 | 0.69193
43602.7782 | 0.56401 | 0.58431 | 0.56668 | 0.57309 | 0.53724 | 0.55365 | 0.56627 | 0.69212
43602.7784 | 0.56459 | 0.58432 | 0.56678 | 0.57379 | 0.53773 | 0.55383 | 0.56166 | 0.69216
43602.7784 | 0.56435 | 0.5846 | 0.56653 | 0.57359 | 0.53761 | 0.55374 | 0.56252 | 0.69212
43602.7784 | 0.56446 | 0.58433 | 0.56631 | 0.57303 | 0.53705 | 0.55331 | 0.56428 | 0.69184
43602.7787 | 0.56491 | 0.58453 | 0.56657 | 0.5739 | 0.53773 | 0.55362 | 0.56561 | 0.69206
43602.7786 | 0.5641 | 0.58401 | 0.56628 | 0.57331 | 0.53768 | 0.55372 | 0.56273 | 0.6921
43602.7788 | 0.56523 | 0.58548 | 0.56791 | 0.57478 | 0.53844 | 0.55448 | 0.56284 | 0.69261
43602.7788 | 0.56509 | 0.58523 | 0.5674 | 0.57437 | 0.53855 | 0.55476 | 0.56283 | 0.69256
43602.779 | 0.56532 | 0.58537 | 0.56783 | 0.57454 | 0.53875 | 0.55497 | 0.56637 | 0.69268
43602.779 | 0.56541 | 0.5851 | 0.56757 | 0.57446 | 0.53851 | 0.55466 | 0.5631 | 0.69256
43602.779 | 0.56534 | 0.58528 | 0.56785 | 0.57455 | 0.53814 | 0.5545 | 0.56405 | 0.69252
43602.7792 | 0.56421 | 0.58452 | 0.56663 | 0.57342 | 0.53756 | 0.55393 | 0.56303 | 0.69224
43602.7792 | 0.56432 | 0.58477 | 0.56694 | 0.57388 | 0.53745 | 0.55366 | 0.56162 | 0.69215
43602.7792 | 0.56432 | 0.58486 | 0.56694 | 0.57375 | 0.53753 | 0.55374 | 0.56342 | 0.69206
43602.7795 | 0.56484 | 0.58493 | 0.56728 | 0.57393 | 0.53771 | 0.55399 | 0.56354 | 0.69237
43602.7795 | 0.56505 | 0.58509 | 0.56747 | 0.574 | 0.53825 | 0.55435 | 0.56242 | 0.69246
43602.7797 | 0.56482 | 0.58493 | 0.56719 | 0.57381 | 0.5376 | 0.55362 | 0.56392 | 0.6922
43602.7796 | 0.56508 | 0.58492 | 0.56731 | 0.57392 | 0.5382 | 0.55426 | 0.56349 | 0.69245
43602.7798 | 0.56442 | 0.58457 | 0.56675 | 0.57358 | 0.53794 | 0.55424 | 0.56245 | 0.69226
43602.7798 | 0.56426 | 0.58454 | 0.56664 | 0.57348 | 0.53761 | 0.55392 | 0.5617 | 0.69229
43602.7798 | 0.56403 | 0.584 | 0.56658 | 0.5732 | 0.53744 | 0.55375 | 0.56241 | 0.69221
43602.7801 | 0.56374 | 0.5842 | 0.56615 | 0.57342 | 0.53705 | 0.55326 | 0.5619 | 0.69189
43602.7801 | 0.56414 | 0.58422 | 0.56656 | 0.57352 | 0.53717 | 0.55367 | 0.56167 | 0.69207
43602.7801 | 0.56535 | 0.58502 | 0.56748 | 0.57449 | 0.53838 | 0.55469 | 0.56286 | 0.69254
43602.7803 | 0.56606 | 0.58591 | 0.56836 | 0.57513 | 0.53894 | 0.55507 | 0.56405 | 0.69276
43602.7803 | 0.56588 | 0.58577 | 0.56834 | 0.57558 | 0.53919 | 0.55542 | 0.56344 | 0.69295
43602.7803 | 0.56584 | 0.5859 | 0.56795 | 0.57535 | 0.53946 | 0.55546 | 0.564 | 0.69308
43602.7806 | 0.56569 | 0.58569 | 0.56815 | 0.57525 | 0.53875 | 0.55471 | 0.56282 | 0.69284
43602.7806 | 0.56502 | 0.58499 | 0.56762 | 0.57479 | 0.53863 | 0.5548 | 0.5632 | 0.6928
43602.7805 | 0.5661 | 0.58612 | 0.56845 | 0.57545 | 0.53895 | 0.55517 | 0.56306 | 0.69313
43602.7808 | 0.56573 | 0.58591 | 0.5684 | 0.57532 | 0.53948 | 0.5553 | 0.56723 | 0.69302
43602.7808 | 0.5655 | 0.58593 | 0.56817 | 0.57518 | 0.53918 | 0.55516 | 0.56517 | 0.69296
43602.7808 | 0.56549 | 0.58571 | 0.56807 | 0.57504 | 0.53899 | 0.55534 | 0.56411 | 0.69308
43602.781 | 0.5658 | 0.58644 | 0.56871 | 0.57557 | 0.53896 | 0.55539 | 0.56355 | 0.69292
43602.781 | 0.56581 | 0.58625 | 0.56834 | 0.57529 | 0.53911 | 0.55569 | 0.56358 | 0.69313
43602.781 | 0.56497 | 0.58556 | 0.56809 | 0.57473 | 0.53877 | 0.55498 | 0.56277 | 0.69281
43602.7813 | 0.56451 | 0.58504 | 0.56712 | 0.57404 | 0.53777 | 0.55403 | 0.56279 | 0.69221
43602.7813 | 0.565 | 0.58572 | 0.56784 | 0.57466 | 0.53837 | 0.55454 | 0.56604 | 0.69264
43602.7813 | 0.56457 | 0.58475 | 0.56722 | 0.57412 | 0.5378 | 0.55419 | 0.56248 | 0.69233
43602.7815 | 0.56415 | 0.58467 | 0.56664 | 0.57393 | 0.53749 | 0.55358 | 0.56261 | 0.692
43602.7815 | 0.56374 | 0.58426 | 0.56652 | 0.57371 | 0.53769 | 0.55387 | 0.56145 | 0.69199
43602.7815 | 0.56435 | 0.58459 | 0.56674 | 0.57374 | 0.53801 | 0.554 | 0.56401 | 0.6923
43602.7818 | 0.56352 | 0.58391 | 0.56616 | 0.57307 | 0.53672 | 0.55309 | 0.56484 | 0.69165
43602.7818 | 0.56428 | 0.58438 | 0.5665 | 0.57353 | 0.53695 | 0.55344 | 0.56268 | 0.69163
43602.7818 | 0.56412 | 0.58432 | 0.56642 | 0.5733 | 0.53714 | 0.55331 | 0.56397 | 0.69188
43602.782 | 0.56344 | 0.58391 | 0.56615 | 0.57298 | 0.5369 | 0.55317 | 0.56165 | 0.69167
43602.782 | 0.56395 | 0.58427 | 0.56662 | 0.57364 | 0.53709 | 0.55314 | 0.56181 | 0.69174
43602.782 | 0.56261 | 0.58318 | 0.56535 | 0.57246 | 0.53606 | 0.55258 | 0.56134 | 0.69131
43602.7822 | 0.56277 | 0.58311 | 0.5651 | 0.57226 | 0.53628 | 0.55246 | 0.56097 | 0.69112
43602.7823 | 0.56154 | 0.5822 | 0.5642 | 0.57111 | 0.5357 | 0.55189 | 0.5611 | 0.69102
43602.7822 | 0.56248 | 0.58264 | 0.56458 | 0.5718 | 0.53572 | 0.55211 | 0.56096 | 0.69102
43602.7825 | 0.56093 | 0.58182 | 0.56369 | 0.57105 | 0.53478 | 0.55118 | 0.56076 | 0.69022
43602.7825 | 0.56081 | 0.5815 | 0.56352 | 0.57077 | 0.53437 | 0.55063 | 0.56012 | 0.68998
43602.7825 | 0.56034 | 0.58076 | 0.56261 | 0.57 | 0.53377 | 0.55002 | 0.5589 | 0.68954
43602.7827 | 0.55992 | 0.58074 | 0.56229 | 0.56922 | 0.53255 | 0.54918 | 0.55816 | 0.68922
43602.7827 | 0.56005 | 0.58078 | 0.5625 | 0.56935 | 0.53307 | 0.54959 | 0.55785 | 0.68916
43602.7827 | 0.55914 | 0.58035 | 0.56224 | 0.56939 | 0.5326 | 0.54858 | 0.55685 | 0.68882
43602.783 | 0.559 | 0.57952 | 0.56172 | 0.56858 | 0.53227 | 0.54895 | 0.55825 | 0.6887
43602.783 | 0.55889 | 0.57953 | 0.56172 | 0.56879 | 0.53226 | 0.54861 | 0.56013 | 0.68867
43602.783 | 0.5584 | 0.57887 | 0.56106 | 0.56778 | 0.53157 | 0.54804 | 0.55697 | 0.68833
43602.7832 | 0.55719 | 0.578 | 0.55973 | 0.56707 | 0.53087 | 0.54716 | 0.55588 | 0.68787
43602.7832 | 0.55811 | 0.57869 | 0.56049 | 0.56752 | 0.53042 | 0.54714 | 0.55821 | 0.68771
43602.7832 | 0.55767 | 0.57828 | 0.56021 | 0.56715 | 0.53071 | 0.54734 | 0.55657 | 0.6877
43602.7835 | 0.55617 | 0.5772 | 0.55875 | 0.56613 | 0.52957 | 0.54589 | 0.55399 | 0.68692
43602.7835 | 0.55605 | 0.57693 | 0.55847 | 0.56588 | 0.52907 | 0.54553 | 0.55739 | 0.68681
43602.7835 | 0.55555 | 0.57659 | 0.5583 | 0.56542 | 0.52851 | 0.54509 | 0.5561 | 0.68636
43602.7837 | 0.55623 | 0.57676 | 0.55878 | 0.56581 | 0.52896 | 0.5457 | 0.55535 | 0.68663
43602.7837 | 0.55573 | 0.57628 | 0.55796 | 0.56522 | 0.52852 | 0.5454 | 0.55412 | 0.6865
43602.7837 | 0.55658 | 0.57676 | 0.55852 | 0.56582 | 0.52943 | 0.54613 | 0.5542 | 0.687
43602.784 | 0.5577 | 0.57834 | 0.56011 | 0.56704 | 0.53045 | 0.54681 | 0.55606 | 0.68756
43602.784 | 0.55709 | 0.57766 | 0.55932 | 0.56637 | 0.53017 | 0.5468 | 0.55621 | 0.68746
43602.784 | 0.55845 | 0.57882 | 0.56078 | 0.56752 | 0.53124 | 0.54765 | 0.56024 | 0.68808
43602.7842 | 0.55941 | 0.57981 | 0.56186 | 0.5687 | 0.53204 | 0.5489 | 0.55705 | 0.68866
43602.7842 | 0.55906 | 0.57936 | 0.56139 | 0.56838 | 0.53209 | 0.54885 | 0.55706 | 0.68864
43602.7842 | 0.56034 | 0.58096 | 0.56285 | 0.56964 | 0.53283 | 0.54958 | 0.55941 | 0.68899
43602.7845 | 0.56041 | 0.58107 | 0.56318 | 0.57004 | 0.53362 | 0.55 | 0.55861 | 0.6896
43602.7845 | 0.56106 | 0.58205 | 0.5641 | 0.57073 | 0.534 | 0.55034 | 0.55831 | 0.68972
43602.7846 | 0.56269 | 0.58282 | 0.56498 | 0.57201 | 0.53562 | 0.55218 | 0.5608 | 0.69086
43602.7846 | 0.56281 | 0.5832 | 0.56537 | 0.57214 | 0.53569 | 0.55195 | 0.56022 | 0.69074
43602.7846 | 0.56345 | 0.58337 | 0.5657 | 0.57227 | 0.53652 | 0.5528 | 0.56155 | 0.69139
43602.7849 | 0.5647 | 0.58455 | 0.567 | 0.57362 | 0.53728 | 0.5539 | 0.5632 | 0.69207
43602.7849 | 0.56471 | 0.58482 | 0.56705 | 0.57374 | 0.53766 | 0.55412 | 0.56352 | 0.69225
43602.7849 | 0.56437 | 0.5841 | 0.56636 | 0.57319 | 0.53782 | 0.55439 | 0.5641 | 0.69236
43602.7851 | 0.5652 | 0.58491 | 0.56707 | 0.57405 | 0.53818 | 0.55457 | 0.56364 | 0.69261
43602.7851 | 0.56574 | 0.58545 | 0.56765 | 0.57459 | 0.53816 | 0.55432 | 0.56305 | 0.69261
43602.7853 | 0.56622 | 0.58588 | 0.56793 | 0.57505 | 0.53919 | 0.55546 | 0.56389 | 0.69329
43602.7853 | 0.56571 | 0.58537 | 0.56756 | 0.57458 | 0.5387 | 0.55503 | 0.56316 | 0.69299
43602.7855 | 0.56624 | 0.58597 | 0.56821 | 0.57491 | 0.53936 | 0.55542 | 0.56583 | 0.69328
43602.7855 | 0.56569 | 0.5853 | 0.56752 | 0.57412 | 0.53874 | 0.55492 | 0.56406 | 0.69309
43602.7855 | 0.56602 | 0.58546 | 0.56751 | 0.57436 | 0.53859 | 0.55478 | 0.56272 | 0.69274
43602.7857 | 0.56499 | 0.58479 | 0.56711 | 0.57381 | 0.53769 | 0.55394 | 0.56334 | 0.69229
43602.7857 | 0.56478 | 0.58464 | 0.56674 | 0.57332 | 0.53803 | 0.55394 | 0.56232 | 0.6925
43602.7859 | 0.56436 | 0.58438 | 0.56633 | 0.57308 | 0.53685 | 0.55319 | 0.56285 | 0.69178
43602.7859 | 0.56444 | 0.58471 | 0.56684 | 0.57382 | 0.53745 | 0.5536 | 0.56227 | 0.692
43602.7859 | 0.56421 | 0.58429 | 0.56668 | 0.573 | 0.5377 | 0.55386 | 0.56192 | 0.69225
43602.7861 | 0.56222 | 0.58245 | 0.5646 | 0.57132 | 0.5357 | 0.55202 | 0.56051 | 0.69101
43602.7861 | 0.563 | 0.58304 | 0.56518 | 0.57196 | 0.53639 | 0.55244 | 0.56135 | 0.69112
43602.7864 | 0.56293 | 0.58268 | 0.56479 | 0.57157 | 0.53583 | 0.55199 | 0.56182 | 0.691
43602.7864 | 0.56246 | 0.58243 | 0.56426 | 0.57106 | 0.53524 | 0.55147 | 0.55963 | 0.69073
43602.7866 | 0.56205 | 0.58201 | 0.56413 | 0.57086 | 0.5353 | 0.5514 | 0.55967 | 0.69064
43602.7866 | 0.56209 | 0.58241 | 0.56447 | 0.5712 | 0.53479 | 0.55104 | 0.56192 | 0.69059
43602.7868 | 0.5617 | 0.58164 | 0.5636 | 0.57065 | 0.53431 | 0.55078 | 0.55946 | 0.69013
43602.7867 | 0.56183 | 0.58179 | 0.56385 | 0.57071 | 0.53488 | 0.55122 | 0.56012 | 0.69045
43602.7869 | 0.56136 | 0.58165 | 0.56356 | 0.57048 | 0.53432 | 0.55051 | 0.55915 | 0.69006
43602.7869 | 0.56165 | 0.58181 | 0.56398 | 0.57061 | 0.53458 | 0.5509 | 0.56048 | 0.69015
43602.7871 | 0.56091 | 0.5814 | 0.56316 | 0.57018 | 0.5339 | 0.55044 | 0.55863 | 0.68998
43602.7871 | 0.56103 | 0.5814 | 0.56372 | 0.57047 | 0.53421 | 0.55051 | 0.56163 | 0.68995
43602.7871 | 0.56062 | 0.58061 | 0.56242 | 0.56948 | 0.53368 | 0.54992 | 0.55832 | 0.68976
43602.7874 | 0.56117 | 0.5814 | 0.56372 | 0.57021 | 0.53401 | 0.55028 | 0.55943 | 0.69007
43602.7873 | 0.5615 | 0.58144 | 0.56353 | 0.57025 | 0.53418 | 0.55057 | 0.55936 | 0.69022
43602.7875 | 0.56127 | 0.58162 | 0.56361 | 0.5705 | 0.53445 | 0.55069 | 0.55945 | 0.69034
43602.7875 | 0.56144 | 0.58176 | 0.56377 | 0.57051 | 0.53426 | 0.55056 | 0.56005 | 0.69024
43602.7877 | 0.56139 | 0.58167 | 0.5636 | 0.57075 | 0.53434 | 0.55066 | 0.55918 | 0.69024
43602.7877 | 0.56112 | 0.5817 | 0.5638 | 0.57063 | 0.53459 | 0.55098 | 0.56017 | 0.69038
43602.7879 | 0.56815 | 0.58773 | 0.57015 | 0.5771 | 0.54122 | 0.55708 | 0.56874 | 0.69454
43602.7879 | 0.56958 | 0.58948 | 0.57223 | 0.57899 | 0.54257 | 0.55829 | 0.56866 | 0.69544
43602.7881 | 0.57966 | 0.59887 | 0.58142 | 0.58876 | 0.55279 | 0.56852 | 0.57691 | 0.70214
43602.7881 | 0.58139 | 0.60032 | 0.58321 | 0.5903 | 0.55487 | 0.57067 | 0.57947 | 0.70357
43602.7882 | 0.58687 | 0.60516 | 0.58837 | 0.59555 | 0.56111 | 0.57638 | 0.58643 | 0.70756
43602.7882 | 0.58713 | 0.60541 | 0.58861 | 0.59581 | 0.56126 | 0.57654 | 0.58571 | 0.70785
43602.7884 | 0.58908 | 0.60745 | 0.59041 | 0.5978 | 0.56351 | 0.57875 | 0.59 | 0.70944
43602.7884 | 0.58939 | 0.60751 | 0.59061 | 0.59795 | 0.56378 | 0.57878 | 0.5874 | 0.70949
43602.7886 | 0.58935 | 0.60767 | 0.59076 | 0.59838 | 0.5638 | 0.57913 | 0.58806 | 0.70984
43602.7886 | 0.58941 | 0.60758 | 0.59079 | 0.59832 | 0.56385 | 0.57928 | 0.58797 | 0.70981
43602.7886 | 0.58973 | 0.60798 | 0.59119 | 0.59827 | 0.564 | 0.5794 | 0.58771 | 0.70991
43602.7888 | 0.59121 | 0.60956 | 0.59261 | 0.59972 | 0.56546 | 0.58066 | 0.59167 | 0.71086
43602.7888 | 0.5913 | 0.60949 | 0.59255 | 0.59992 | 0.56553 | 0.58083 | 0.59095 | 0.71088
43602.789 | 0.59364 | 0.61184 | 0.59524 | 0.60242 | 0.56807 | 0.58321 | 0.59174 | 0.71277
43602.789 | 0.59376 | 0.61188 | 0.59525 | 0.60249 | 0.56836 | 0.58347 | 0.59379 | 0.71279
43602.7892 | 0.59881 | 0.61705 | 0.6005 | 0.60755 | 0.57287 | 0.58756 | 0.59638 | 0.71557
43602.7892 | 0.59961 | 0.61766 | 0.60129 | 0.6084 | 0.57507 | 0.58946 | 0.60056 | 0.71685
43602.7894 | 0.60183 | 0.61996 | 0.60356 | 0.61087 | 0.57778 | 0.59229 | 0.60132 | 0.71857
43602.7894 | 0.60171 | 0.6199 | 0.60356 | 0.6107 | 0.57761 | 0.59213 | 0.60075 | 0.71847
43602.7895 | 0.60657 | 0.62472 | 0.60856 | 0.61585 | 0.58173 | 0.5964 | 0.60342 | 0.72075
43602.7895 | 0.60788 | 0.6257 | 0.60969 | 0.61658 | 0.58333 | 0.5977 | 0.60499 | 0.72173
43602.7897 | 0.61488 | 0.63266 | 0.61727 | 0.6244 | 0.5918 | 0.60552 | 0.61222 | 0.72678
43602.7897 | 0.61679 | 0.63422 | 0.61874 | 0.62591 | 0.59287 | 0.60686 | 0.61622 | 0.72742
43602.7899 | 0.62558 | 0.64278 | 0.62791 | 0.63501 | 0.60258 | 0.61594 | 0.62338 | 0.73355
43602.7899 | 0.62744 | 0.64443 | 0.62941 | 0.63657 | 0.60398 | 0.61714 | 0.6247 | 0.73445
43602.7901 | 0.63271 | 0.6494 | 0.63438 | 0.64199 | 0.60993 | 0.62301 | 0.63019 | 0.73857
43602.7901 | 0.63201 | 0.64849 | 0.6335 | 0.64087 | 0.60955 | 0.62242 | 0.62895 | 0.73828
43602.7902 | 0.61872 | 0.63574 | 0.6201 | 0.62759 | 0.59559 | 0.60972 | 0.61714 | 0.72959
43602.7902 | 0.61701 | 0.634 | 0.61847 | 0.62574 | 0.59348 | 0.60745 | 0.61523 | 0.72817
43602.7904 | 0.60587 | 0.6237 | 0.60779 | 0.61477 | 0.58216 | 0.59629 | 0.60566 | 0.7207
43602.7904 | 0.60454 | 0.62269 | 0.60685 | 0.61383 | 0.58046 | 0.59493 | 0.60303 | 0.71988
43602.7906 | 0.59833 | 0.61691 | 0.60046 | 0.60719 | 0.57388 | 0.58886 | 0.59691 | 0.71535
43602.7906 | 0.59808 | 0.61656 | 0.59998 | 0.60684 | 0.57311 | 0.58817 | 0.59603 | 0.71496
43602.7908 | 0.59496 | 0.61368 | 0.59693 | 0.60388 | 0.57007 | 0.58516 | 0.59237 | 0.71294
43602.7908 | 0.59477 | 0.61341 | 0.59665 | 0.60362 | 0.56951 | 0.58448 | 0.5929 | 0.71264
43602.7909 | 0.59013 | 0.6096 | 0.59279 | 0.59957 | 0.5652 | 0.58037 | 0.58769 | 0.70975
43602.7909 | 0.5896 | 0.6089 | 0.59207 | 0.59893 | 0.56452 | 0.57979 | 0.59022 | 0.70943
43602.7911 | 0.58285 | 0.60237 | 0.58519 | 0.59189 | 0.55706 | 0.57252 | 0.58024 | 0.70464
43602.7911 | 0.58282 | 0.60225 | 0.58517 | 0.5918 | 0.55721 | 0.57257 | 0.58302 | 0.70463
43602.7913 | 0.58081 | 0.6003 | 0.58316 | 0.5899 | 0.55479 | 0.57039 | 0.58145 | 0.70327
43602.7913 | 0.58112 | 0.60045 | 0.58351 | 0.5902 | 0.55516 | 0.57093 | 0.57946 | 0.70351
43602.7915 | 0.58258 | 0.60216 | 0.58503 | 0.59186 | 0.55629 | 0.57146 | 0.57974 | 0.70415
43602.7915 | 0.58481 | 0.60437 | 0.58738 | 0.59396 | 0.55912 | 0.57432 | 0.5824 | 0.70589
43602.7916 | 0.59864 | 0.61751 | 0.60101 | 0.60805 | 0.57407 | 0.58862 | 0.59667 | 0.71558
43602.7916 | 0.5999 | 0.61826 | 0.60179 | 0.60902 | 0.57516 | 0.58956 | 0.59678 | 0.71627
43602.7918 | 0.60773 | 0.62586 | 0.60955 | 0.61654 | 0.5836 | 0.59789 | 0.60546 | 0.72189
43602.7918 | 0.60826 | 0.6263 | 0.61001 | 0.61697 | 0.58406 | 0.59828 | 0.60737 | 0.72215
43602.792 | 0.61204 | 0.62951 | 0.61352 | 0.62047 | 0.58792 | 0.6022 | 0.60944 | 0.72494
43602.792 | 0.61213 | 0.62967 | 0.61385 | 0.62096 | 0.58796 | 0.60221 | 0.61147 | 0.72509
43602.7922 | 0.61353 | 0.6309 | 0.61506 | 0.6226 | 0.5896 | 0.60385 | 0.61145 | 0.72615
43602.7922 | 0.61348 | 0.63092 | 0.61497 | 0.62252 | 0.58983 | 0.60395 | 0.61438 | 0.72622
43602.7924 | 0.61498 | 0.63247 | 0.61665 | 0.62404 | 0.59102 | 0.605 | 0.61249 | 0.72709
43602.7923 | 0.61628 | 0.63355 | 0.61753 | 0.62525 | 0.59195 | 0.60621 | 0.61424 | 0.72763
43602.7925 | 0.61835 | 0.63544 | 0.61999 | 0.62734 | 0.59465 | 0.60837 | 0.61872 | 0.72929
43602.7925 | 0.62008 | 0.63695 | 0.62181 | 0.62913 | 0.5961 | 0.60963 | 0.61779 | 0.73016
43602.7927 | 0.62387 | 0.64043 | 0.62539 | 0.63273 | 0.60076 | 0.61429 | 0.62148 | 0.7328
43602.7927 | 0.62391 | 0.64059 | 0.6255 | 0.63278 | 0.60058 | 0.61425 | 0.62099 | 0.73266
43602.7929 | 0.62732 | 0.64399 | 0.62889 | 0.63617 | 0.60425 | 0.61779 | 0.62759 | 0.7353
43602.7929 | 0.62725 | 0.64392 | 0.62879 | 0.63615 | 0.60401 | 0.61776 | 0.62556 | 0.73511
43602.7929 | 0.6293 | 0.64611 | 0.63103 | 0.63831 | 0.60641 | 0.61972 | 0.62856 | 0.73643
43602.7931 | 0.63242 | 0.64895 | 0.63398 | 0.64128 | 0.60942 | 0.62275 | 0.62891 | 0.73857
43602.7931 | 0.63259 | 0.64927 | 0.63455 | 0.64147 | 0.60988 | 0.62332 | 0.63045 | 0.7389
43602.7933 | 0.63547 | 0.65197 | 0.63671 | 0.64414 | 0.61277 | 0.62602 | 0.63403 | 0.74083
43602.7933 | 0.6357 | 0.65205 | 0.63696 | 0.64445 | 0.61291 | 0.6262 | 0.63358 | 0.74099
43602.7935 | 0.63741 | 0.65385 | 0.63857 | 0.64616 | 0.61531 | 0.6284 | 0.63595 | 0.74232
43602.7935 | 0.63845 | 0.65462 | 0.63974 | 0.64727 | 0.61574 | 0.62898 | 0.6372 | 0.74266
43602.7937 | 0.64106 | 0.65755 | 0.64262 | 0.64972 | 0.61902 | 0.63205 | 0.64297 | 0.74494
43602.7936 | 0.64138 | 0.65751 | 0.64276 | 0.65006 | 0.61936 | 0.63231 | 0.6408 | 0.74504
43602.7938 | 0.64373 | 0.65987 | 0.64487 | 0.6525 | 0.62135 | 0.63455 | 0.64086 | 0.74654
43602.7938 | 0.64366 | 0.6598 | 0.64525 | 0.65244 | 0.62144 | 0.63467 | 0.6437 | 0.74661
43602.794 | 0.64515 | 0.66104 | 0.64664 | 0.65392 | 0.62314 | 0.63618 | 0.64309 | 0.74733
43602.794 | 0.64552 | 0.6614 | 0.64714 | 0.65428 | 0.62339 | 0.6363 | 0.6435 | 0.74754
43602.7942 | 0.64774 | 0.66332 | 0.64894 | 0.65608 | 0.62559 | 0.6385 | 0.64497 | 0.74904
43602.7942 | 0.64812 | 0.6636 | 0.64952 | 0.65658 | 0.62605 | 0.6389 | 0.64587 | 0.74921
43602.7944 | 0.64946 | 0.66519 | 0.65096 | 0.65814 | 0.62769 | 0.64038 | 0.64821 | 0.75035
43602.7944 | 0.64971 | 0.66538 | 0.65112 | 0.6581 | 0.62784 | 0.64052 | 0.64793 | 0.75042
43602.7945 | 0.65167 | 0.66712 | 0.65305 | 0.65993 | 0.62923 | 0.64155 | 0.64806 | 0.75112
43602.7945 | 0.6526 | 0.66822 | 0.65421 | 0.66099 | 0.63075 | 0.64288 | 0.64951 | 0.75217
43602.7947 | 0.6541 | 0.6697 | 0.65612 | 0.66277 | 0.63252 | 0.64458 | 0.65067 | 0.75329
43602.7947 | 0.65469 | 0.67024 | 0.65645 | 0.66321 | 0.63301 | 0.64523 | 0.65355 | 0.75369
43602.7949 | 0.65677 | 0.6724 | 0.65831 | 0.66539 | 0.63492 | 0.64728 | 0.65357 | 0.75474
43602.7949 | 0.65816 | 0.67332 | 0.65941 | 0.66655 | 0.63621 | 0.6485 | 0.65473 | 0.7555
43602.7951 | 0.66116 | 0.67672 | 0.66301 | 0.67002 | 0.6408 | 0.6527 | 0.65837 | 0.75833
43602.7951 | 0.66097 | 0.67651 | 0.66303 | 0.66986 | 0.64054 | 0.65255 | 0.66124 | 0.75804
43602.7952 | 0.6671 | 0.68222 | 0.66884 | 0.6758 | 0.64703 | 0.65851 | 0.66678 | 0.7619
43602.7952 | 0.6671 | 0.6821 | 0.6684 | 0.67592 | 0.64679 | 0.65843 | 0.66408 | 0.76196
43602.7954 | 0.67125 | 0.68609 | 0.67258 | 0.67992 | 0.65088 | 0.66258 | 0.66898 | 0.76493
43602.7954 | 0.67128 | 0.68608 | 0.67264 | 0.67971 | 0.65086 | 0.66266 | 0.67145 | 0.76481
43602.7956 | 0.67434 | 0.68918 | 0.67596 | 0.68323 | 0.65452 | 0.66607 | 0.67263 | 0.76752
43602.7956 | 0.67453 | 0.68916 | 0.6759 | 0.6831 | 0.65438 | 0.66603 | 0.67219 | 0.7675
43602.7958 | 0.67859 | 0.69294 | 0.67999 | 0.68719 | 0.65825 | 0.6696 | 0.67735 | 0.76966
43602.7958 | 0.67885 | 0.69298 | 0.68022 | 0.68719 | 0.65897 | 0.67008 | 0.67672 | 0.77005
43602.7959 | 0.67978 | 0.69395 | 0.68109 | 0.68821 | 0.65958 | 0.6709 | 0.67671 | 0.77058
43602.7959 | 0.68113 | 0.69531 | 0.68276 | 0.68982 | 0.66099 | 0.67216 | 0.67799 | 0.77153
43602.7961 | 0.68384 | 0.6978 | 0.68502 | 0.69228 | 0.66412 | 0.67492 | 0.68295 | 0.77319
43602.7961 | 0.68515 | 0.69909 | 0.68658 | 0.69365 | 0.66497 | 0.67605 | 0.68193 | 0.77388
43602.7963 | 0.68816 | 0.70232 | 0.68985 | 0.6966 | 0.66864 | 0.67924 | 0.68546 | 0.77613
43602.7963 | 0.68848 | 0.70251 | 0.6901 | 0.69685 | 0.66913 | 0.67992 | 0.6878 | 0.77644
43602.7965 | 0.69166 | 0.70555 | 0.69326 | 0.70042 | 0.672 | 0.68252 | 0.68807 | 0.77817
43602.7965 | 0.69213 | 0.70594 | 0.69372 | 0.7006 | 0.67298 | 0.68376 | 0.68922 | 0.77893
43602.7966 | 0.69358 | 0.70754 | 0.69527 | 0.70215 | 0.67452 | 0.68536 | 0.69205 | 0.78004
43602.7966 | 0.69492 | 0.70871 | 0.69637 | 0.70342 | 0.67535 | 0.68606 | 0.69239 | 0.7805
43602.7968 | 0.69714 | 0.71085 | 0.6987 | 0.70566 | 0.67877 | 0.68889 | 0.69533 | 0.78248
43602.7968 | 0.6987 | 0.71236 | 0.70029 | 0.70721 | 0.68008 | 0.69033 | 0.69569 | 0.78327
43602.797 | 0.69947 | 0.71295 | 0.70129 | 0.70803 | 0.68191 | 0.69227 | 0.69755 | 0.78461
43602.797 | 0.69778 | 0.71135 | 0.69904 | 0.70616 | 0.67973 | 0.69017 | 0.69699 | 0.78325
43602.7972 | 0.68642 | 0.70108 | 0.6882 | 0.69529 | 0.66799 | 0.67902 | 0.68447 | 0.77537
43602.7972 | 0.68479 | 0.69928 | 0.68665 | 0.69362 | 0.66601 | 0.67719 | 0.68274 | 0.77416
43602.7974 | 0.67342 | 0.68862 | 0.67539 | 0.68231 | 0.65414 | 0.66575 | 0.67149 | 0.76657
43602.7974 | 0.67349 | 0.68871 | 0.67565 | 0.68231 | 0.65312 | 0.66457 | 0.67175 | 0.76584
43602.7976 | 0.66513 | 0.68062 | 0.66697 | 0.67387 | 0.64457 | 0.65663 | 0.66182 | 0.76033
43602.7975 | 0.66397 | 0.67969 | 0.66581 | 0.67283 | 0.6436 | 0.65571 | 0.66266 | 0.75963
43602.7977 | 0.65806 | 0.67645 | 0.66251 | 0.66813 | 0.63699 | 0.64901 | 0.65788 | 0.75477
43602.7977 | 0.66972 | 0.68586 | 0.67256 | 0.67869 | 0.64957 | 0.66122 | 0.66703 | 0.76306
43602.7979 | 0.66989 | 0.68535 | 0.67188 | 0.67884 | 0.65011 | 0.66168 | 0.66762 | 0.76384
43602.7979 | 0.66873 | 0.68414 | 0.67072 | 0.67776 | 0.64875 | 0.66021 | 0.66645 | 0.76303
43602.7981 | 0.65918 | 0.67551 | 0.66136 | 0.66846 | 0.63914 | 0.65101 | 0.65993 | 0.75673
43602.7981 | 0.65792 | 0.67433 | 0.65992 | 0.66707 | 0.6376 | 0.64971 | 0.65568 | 0.75584
43602.7983 | 0.65312 | 0.66967 | 0.6554 | 0.66229 | 0.63224 | 0.64458 | 0.65036 | 0.75248
43602.7983 | 0.65227 | 0.6689 | 0.65458 | 0.66175 | 0.63133 | 0.64365 | 0.64942 | 0.75191
43602.7985 | 0.66146 | 0.67749 | 0.66354 | 0.67009 | 0.63941 | 0.65197 | 0.6581 | 0.75713
43602.7985 | 0.66415 | 0.67994 | 0.66633 | 0.67275 | 0.64299 | 0.65498 | 0.66089 | 0.75914
43602.7986 | 0.68253 | 0.6974 | 0.68446 | 0.69148 | 0.66157 | 0.67287 | 0.67882 | 0.7712
43602.7986 | 0.68442 | 0.69886 | 0.68585 | 0.69313 | 0.66477 | 0.6758 | 0.68095 | 0.77321
43602.7988 | 0.6914 | 0.70548 | 0.69311 | 0.69989 | 0.67249 | 0.68329 | 0.68793 | 0.77832
43602.7988 | 0.69146 | 0.7055 | 0.69325 | 0.70013 | 0.67263 | 0.68356 | 0.68814 | 0.77842
43602.799 | 0.69665 | 0.71052 | 0.69819 | 0.70517 | 0.67741 | 0.68797 | 0.69557 | 0.78174
43602.799 | 0.6975 | 0.71134 | 0.69906 | 0.70581 | 0.67894 | 0.68937 | 0.69429 | 0.78256
43602.7992 | 0.69921 | 0.71317 | 0.7009 | 0.70745 | 0.68078 | 0.6911 | 0.69803 | 0.78357
43602.7992 | 0.69993 | 0.71383 | 0.7016 | 0.70836 | 0.68136 | 0.69176 | 0.69683 | 0.78408
43602.7994 | 0.70175 | 0.71539 | 0.70352 | 0.71009 | 0.68361 | 0.69404 | 0.70015 | 0.78598
43602.7994 | 0.7018 | 0.71535 | 0.70351 | 0.71009 | 0.68372 | 0.69408 | 0.69935 | 0.7859
43602.7996 | 0.70448 | 0.71784 | 0.70602 | 0.71293 | 0.68673 | 0.69642 | 0.7027 | 0.78765
43602.7995 | 0.70483 | 0.71789 | 0.70612 | 0.71296 | 0.68668 | 0.69662 | 0.70221 | 0.78764
43602.7997 | 0.70804 | 0.72156 | 0.70977 | 0.71644 | 0.6907 | 0.70065 | 0.70781 | 0.78987
43602.7997 | 0.7082 | 0.72169 | 0.70985 | 0.71635 | 0.69056 | 0.7008 | 0.70604 | 0.78989
43602.7999 | 0.71135 | 0.72488 | 0.71313 | 0.72004 | 0.69427 | 0.70395 | 0.70919 | 0.79219
43602.7999 | 0.71262 | 0.72577 | 0.71429 | 0.72099 | 0.69454 | 0.70428 | 0.70868 | 0.79256
43602.8001 | 0.71628 | 0.72925 | 0.71769 | 0.72476 | 0.69913 | 0.70885 | 0.7132 | 0.79545
43602.8001 | 0.71627 | 0.72927 | 0.71794 | 0.72484 | 0.69939 | 0.70888 | 0.71347 | 0.79554
43602.8003 | 0.71807 | 0.73119 | 0.71994 | 0.72698 | 0.70156 | 0.71098 | 0.71583 | 0.79686
43602.8003 | 0.7194 | 0.73232 | 0.7212 | 0.72818 | 0.70195 | 0.71162 | 0.71597 | 0.79735
43602.8005 | 0.72287 | 0.73551 | 0.72446 | 0.73163 | 0.70622 | 0.71562 | 0.71989 | 0.79999
43602.8005 | 0.72391 | 0.73646 | 0.72555 | 0.73228 | 0.70728 | 0.71678 | 0.72198 | 0.80062
43602.8007 | 0.72621 | 0.73888 | 0.72785 | 0.73512 | 0.7093 | 0.71861 | 0.72316 | 0.80207
43602.8006 | 0.72696 | 0.73916 | 0.72829 | 0.73526 | 0.7102 | 0.71957 | 0.72471 | 0.80274
43602.8008 | 0.72831 | 0.74101 | 0.73024 | 0.73719 | 0.71225 | 0.7213 | 0.72572 | 0.80396
43602.8008 | 0.7286 | 0.74121 | 0.73033 | 0.73732 | 0.71227 | 0.72132 | 0.72672 | 0.80385
43602.801 | 0.73155 | 0.74395 | 0.73295 | 0.74021 | 0.71556 | 0.72458 | 0.72869 | 0.80597
43602.801 | 0.73149 | 0.744 | 0.73326 | 0.74027 | 0.71569 | 0.72467 | 0.73137 | 0.80616
43602.8012 | 0.73512 | 0.74731 | 0.73672 | 0.74385 | 0.71946 | 0.72829 | 0.73315 | 0.80851
43602.8012 | 0.73524 | 0.74764 | 0.73715 | 0.74405 | 0.71984 | 0.72848 | 0.73328 | 0.80865
43602.8014 | 0.73842 | 0.75056 | 0.73997 | 0.74724 | 0.72282 | 0.73138 | 0.73587 | 0.81059
43602.8014 | 0.73923 | 0.75123 | 0.74086 | 0.74777 | 0.72329 | 0.73198 | 0.73606 | 0.81089
43602.8016 | 0.74068 | 0.7527 | 0.74272 | 0.74949 | 0.72568 | 0.73422 | 0.73872 | 0.81228
43602.8016 | 0.74111 | 0.75303 | 0.74289 | 0.74987 | 0.7256 | 0.73426 | 0.73789 | 0.8125
43602.8018 | 0.74527 | 0.75699 | 0.74676 | 0.75365 | 0.73006 | 0.73843 | 0.74331 | 0.81519
43602.8017 | 0.7452 | 0.75697 | 0.74689 | 0.75363 | 0.73012 | 0.73876 | 0.74289 | 0.81542
43602.8019 | 0.74803 | 0.75943 | 0.74954 | 0.7566 | 0.73338 | 0.74148 | 0.74729 | 0.81713
43602.8019 | 0.74827 | 0.75963 | 0.74982 | 0.75698 | 0.73343 | 0.74168 | 0.74688 | 0.8172
43602.8021 | 0.75009 | 0.76175 | 0.75207 | 0.75891 | 0.73528 | 0.74363 | 0.74722 | 0.81861
43602.8021 | 0.75124 | 0.76272 | 0.75315 | 0.75979 | 0.73622 | 0.74441 | 0.74916 | 0.81919
43602.8023 | 0.75865 | 0.7695 | 0.76032 | 0.76757 | 0.7442 | 0.75196 | 0.75557 | 0.82379
43602.8023 | 0.76021 | 0.77099 | 0.76165 | 0.76887 | 0.74612 | 0.75389 | 0.75733 | 0.8249
43602.8025 | 0.76256 | 0.77303 | 0.76355 | 0.7709 | 0.74832 | 0.75595 | 0.75894 | 0.82651
43602.8025 | 0.763 | 0.77363 | 0.76424 | 0.77104 | 0.74865 | 0.75646 | 0.75942 | 0.82679
43602.8027 | 0.76475 | 0.77539 | 0.7662 | 0.77311 | 0.75053 | 0.75798 | 0.76201 | 0.82815
43602.8027 | 0.76547 | 0.77616 | 0.76685 | 0.77387 | 0.75103 | 0.75858 | 0.76375 | 0.82864
43602.8029 | 0.76832 | 0.77904 | 0.76997 | 0.77676 | 0.75432 | 0.762 | 0.7657 | 0.83069
43602.8028 | 0.76865 | 0.77907 | 0.76986 | 0.7766 | 0.7545 | 0.76214 | 0.76833 | 0.83079
43602.803 | 0.77029 | 0.7808 | 0.77186 | 0.77864 | 0.75628 | 0.76359 | 0.76703 | 0.83199
43602.803 | 0.77081 | 0.78115 | 0.77215 | 0.77899 | 0.75688 | 0.76432 | 0.76861 | 0.83232
43602.8032 | 0.77287 | 0.78315 | 0.77442 | 0.78124 | 0.75887 | 0.76611 | 0.76984 | 0.8338
43602.8032 | 0.77284 | 0.78323 | 0.77439 | 0.78122 | 0.75902 | 0.76635 | 0.77201 | 0.8339
43602.8034 | 0.77458 | 0.78503 | 0.7763 | 0.78316 | 0.76101 | 0.76828 | 0.77206 | 0.83515
43602.8034 | 0.77509 | 0.78529 | 0.77624 | 0.78324 | 0.76131 | 0.76855 | 0.77167 | 0.83529
43602.8036 | 0.77658 | 0.78665 | 0.7781 | 0.78478 | 0.7627 | 0.77003 | 0.77526 | 0.83628
43602.8036 | 0.77681 | 0.78676 | 0.77864 | 0.78502 | 0.76316 | 0.77027 | 0.77371 | 0.83649
43602.8038 | 0.77831 | 0.78859 | 0.7804 | 0.78709 | 0.76533 | 0.77236 | 0.77618 | 0.83777
43602.8038 | 0.77851 | 0.78874 | 0.7805 | 0.7872 | 0.76529 | 0.77244 | 0.77617 | 0.83786
43602.804 | 0.7784 | 0.78842 | 0.78001 | 0.78684 | 0.7661 | 0.77309 | 0.77842 | 0.83843
43602.8039 | 0.77581 | 0.786 | 0.7775 | 0.78426 | 0.76335 | 0.77047 | 0.77425 | 0.83652
43602.8041 | 0.75774 | 0.76888 | 0.75958 | 0.76609 | 0.74445 | 0.75231 | 0.75709 | 0.82465
43602.8041 | 0.7545 | 0.76613 | 0.75648 | 0.7631 | 0.74085 | 0.74895 | 0.75403 | 0.82218
43602.8043 | 0.73752 | 0.74986 | 0.7401 | 0.7461 | 0.72255 | 0.73148 | 0.73568 | 0.80997
43602.8043 | 0.73629 | 0.74913 | 0.7388 | 0.74522 | 0.72133 | 0.73015 | 0.73411 | 0.80904
43602.8045 | 0.72973 | 0.74266 | 0.73207 | 0.73887 | 0.71441 | 0.72361 | 0.72723 | 0.80481
43602.8045 | 0.72542 | 0.73857 | 0.72724 | 0.73412 | 0.70984 | 0.71908 | 0.72688 | 0.8021
43602.8047 | 0.71542 | 0.7288 | 0.71743 | 0.72447 | 0.69941 | 0.70946 | 0.71397 | 0.79584
43602.8047 | 0.71315 | 0.72663 | 0.71515 | 0.72214 | 0.69669 | 0.70648 | 0.71166 | 0.79392
43602.8049 | 0.69497 | 0.70956 | 0.69728 | 0.70413 | 0.67748 | 0.68815 | 0.69627 | 0.78184
43602.8049 | 0.69279 | 0.70755 | 0.6954 | 0.70202 | 0.6753 | 0.686 | 0.6923 | 0.7805
43602.8051 | 0.68016 | 0.69591 | 0.683 | 0.68941 | 0.66235 | 0.67338 | 0.67871 | 0.77124
43602.8051 | 0.67895 | 0.69441 | 0.68156 | 0.6881 | 0.66038 | 0.67179 | 0.67642 | 0.77029
43602.8053 | 0.67122 | 0.68782 | 0.67428 | 0.6804 | 0.65266 | 0.66418 | 0.67003 | 0.76534
43602.8052 | 0.67157 | 0.68793 | 0.67484 | 0.68046 | 0.65173 | 0.66337 | 0.66811 | 0.76461
43602.8054 | 0.68779 | 0.70312 | 0.69057 | 0.6968 | 0.66793 | 0.6788 | 0.68405 | 0.77514
43602.8054 | 0.69767 | 0.71246 | 0.70032 | 0.70659 | 0.6792 | 0.68939 | 0.69559 | 0.78206
43602.8056 | 0.71031 | 0.72386 | 0.71234 | 0.7188 | 0.69237 | 0.70238 | 0.70635 | 0.79087
43602.8056 | 0.71359 | 0.72714 | 0.71552 | 0.72208 | 0.69642 | 0.70646 | 0.71342 | 0.79338
43602.8058 | 0.7188 | 0.73188 | 0.7206 | 0.72773 | 0.70188 | 0.71131 | 0.71588 | 0.79685
43602.8058 | 0.7207 | 0.73369 | 0.72269 | 0.72937 | 0.70331 | 0.71263 | 0.71707 | 0.7977
43602.806 | 0.7284 | 0.74131 | 0.73062 | 0.73743 | 0.71247 | 0.7216 | 0.72466 | 0.80352
43602.806 | 0.72987 | 0.74294 | 0.73211 | 0.73862 | 0.71391 | 0.72302 | 0.72598 | 0.80465
43602.8062 | 0.73218 | 0.74508 | 0.73433 | 0.74085 | 0.71655 | 0.72567 | 0.7293 | 0.80643
43602.8062 | 0.73323 | 0.74591 | 0.73518 | 0.74162 | 0.71751 | 0.72647 | 0.73135 | 0.80703
43602.8064 | 0.73423 | 0.74676 | 0.73616 | 0.74259 | 0.71848 | 0.72751 | 0.73147 | 0.80783
43602.8064 | 0.73414 | 0.74674 | 0.73633 | 0.74274 | 0.71853 | 0.72752 | 0.73144 | 0.80797
43602.8066 | 0.73512 | 0.74768 | 0.73708 | 0.74364 | 0.71964 | 0.72831 | 0.7327 | 0.8087
43602.8066 | 0.73532 | 0.74764 | 0.73702 | 0.7437 | 0.71946 | 0.7282 | 0.73223 | 0.80868
43602.8068 | 0.73552 | 0.74796 | 0.7376 | 0.7441 | 0.71949 | 0.7286 | 0.73275 | 0.80874
43602.8068 | 0.73563 | 0.74834 | 0.73768 | 0.74417 | 0.7201 | 0.72875 | 0.73314 | 0.80916
43602.8069 | 0.73564 | 0.74827 | 0.73761 | 0.74413 | 0.72037 | 0.72884 | 0.73427 | 0.80924
43602.8069 | 0.73578 | 0.74825 | 0.73764 | 0.74414 | 0.72026 | 0.72907 | 0.73502 | 0.80912
43602.8071 | 0.73767 | 0.75008 | 0.73949 | 0.74598 | 0.72179 | 0.73055 | 0.73519 | 0.81014
43602.8071 | 0.73844 | 0.7507 | 0.74014 | 0.74674 | 0.72265 | 0.73147 | 0.73631 | 0.81085
43602.8073 | 0.74878 | 0.76116 | 0.75121 | 0.75807 | 0.73443 | 0.74256 | 0.74547 | 0.81717
43602.8073 | 0.75122 | 0.76337 | 0.75335 | 0.75979 | 0.7361 | 0.74427 | 0.7474 | 0.81863
43602.8075 | 0.75316 | 0.76504 | 0.75523 | 0.76175 | 0.73871 | 0.74668 | 0.7502 | 0.82082
43602.8075 | 0.75347 | 0.76525 | 0.75553 | 0.76184 | 0.73898 | 0.74696 | 0.75028 | 0.82085
43602.8077 | 0.75695 | 0.76824 | 0.75876 | 0.76499 | 0.74232 | 0.75021 | 0.75436 | 0.8231
43602.8077 | 0.75709 | 0.76857 | 0.75893 | 0.76535 | 0.74263 | 0.75058 | 0.75417 | 0.82341
43602.8079 | 0.75769 | 0.76905 | 0.7596 | 0.76629 | 0.74354 | 0.75113 | 0.75546 | 0.82394
43602.8079 | 0.75783 | 0.76929 | 0.75964 | 0.76632 | 0.74368 | 0.75141 | 0.75564 | 0.82406
43602.8081 | 0.75903 | 0.77022 | 0.76074 | 0.76759 | 0.74474 | 0.75274 | 0.75859 | 0.82478
43602.8081 | 0.75907 | 0.77032 | 0.76074 | 0.76753 | 0.74476 | 0.75267 | 0.7572 | 0.82465
43602.8083 | 0.75985 | 0.77134 | 0.76185 | 0.76838 | 0.74588 | 0.75351 | 0.75819 | 0.82559
43602.8082 | 0.7605 | 0.77174 | 0.76243 | 0.76867 | 0.74644 | 0.75411 | 0.75801 | 0.82582
43602.8084 | 0.76167 | 0.77274 | 0.76357 | 0.7701 | 0.74747 | 0.75519 | 0.75861 | 0.82639
43602.8084 | 0.76199 | 0.7731 | 0.7635 | 0.77036 | 0.74788 | 0.75565 | 0.75859 | 0.82677
43602.8086 | 0.76306 | 0.77393 | 0.76439 | 0.77125 | 0.749 | 0.7564 | 0.75967 | 0.82745
43602.8086 | 0.76336 | 0.77428 | 0.76492 | 0.77171 | 0.7491 | 0.75664 | 0.75997 | 0.8274
43602.8088 | 0.76522 | 0.77599 | 0.76689 | 0.77341 | 0.75144 | 0.75873 | 0.76242 | 0.82903
43602.8088 | 0.76532 | 0.77619 | 0.76712 | 0.7737 | 0.75144 | 0.75893 | 0.76261 | 0.82903
43602.809 | 0.76653 | 0.77761 | 0.76831 | 0.77499 | 0.75269 | 0.76048 | 0.76497 | 0.82999
43602.809 | 0.76765 | 0.77825 | 0.76921 | 0.77568 | 0.75361 | 0.76134 | 0.76513 | 0.83047
43602.8092 | 0.76873 | 0.77942 | 0.77034 | 0.77696 | 0.7552 | 0.76268 | 0.76858 | 0.83142
43602.8092 | 0.76913 | 0.77983 | 0.77062 | 0.77738 | 0.75549 | 0.76303 | 0.76648 | 0.83169
43602.8094 | 0.76954 | 0.78042 | 0.77106 | 0.77778 | 0.75599 | 0.76371 | 0.76761 | 0.83214
43602.8094 | 0.76973 | 0.78055 | 0.77138 | 0.77783 | 0.75632 | 0.76373 | 0.76977 | 0.83212
43602.8096 | 0.77058 | 0.78143 | 0.7726 | 0.77885 | 0.75729 | 0.76484 | 0.7678 | 0.83288
43602.8096 | 0.77076 | 0.78158 | 0.77251 | 0.77898 | 0.75729 | 0.76489 | 0.77094 | 0.83283
43602.8097 | 0.77153 | 0.78225 | 0.77349 | 0.78017 | 0.7581 | 0.76548 | 0.76908 | 0.83332
43602.8097 | 0.77214 | 0.78299 | 0.77407 | 0.78049 | 0.7589 | 0.76611 | 0.77033 | 0.83375
43602.8099 | 0.77273 | 0.78344 | 0.77467 | 0.78102 | 0.75933 | 0.76629 | 0.76973 | 0.83409
43602.8099 | 0.77277 | 0.78355 | 0.77482 | 0.78148 | 0.75933 | 0.76672 | 0.77042 | 0.83422
43602.8101 | 0.77339 | 0.78439 | 0.77535 | 0.78204 | 0.75999 | 0.76744 | 0.77251 | 0.83459
43602.8101 | 0.77355 | 0.78434 | 0.77563 | 0.78199 | 0.76014 | 0.76719 | 0.77109 | 0.83464
43602.8103 | 0.77415 | 0.78481 | 0.7759 | 0.78278 | 0.76098 | 0.76783 | 0.77138 | 0.83509
43602.8103 | 0.77394 | 0.78492 | 0.77586 | 0.78272 | 0.76094 | 0.76791 | 0.77119 | 0.83513
43602.8105 | 0.7754 | 0.78607 | 0.77706 | 0.7839 | 0.76196 | 0.76915 | 0.77434 | 0.83598
43602.8105 | 0.775 | 0.78573 | 0.77652 | 0.78377 | 0.76168 | 0.76858 | 0.77249 | 0.83562
43602.8107 | 0.77567 | 0.78647 | 0.7779 | 0.78441 | 0.76247 | 0.76955 | 0.77469 | 0.83615
43602.8107 | 0.77613 | 0.78675 | 0.77781 | 0.78439 | 0.76312 | 0.76994 | 0.77368 | 0.83644
43602.8109 | 0.7776 | 0.78783 | 0.77904 | 0.78539 | 0.76426 | 0.77112 | 0.77479 | 0.83713
43602.8109 | 0.77035 | 0.78077 | 0.7719 | 0.77813 | 0.7563 | 0.7634 | 0.76635 | 0.83211
43602.8111 | 0.7583 | 0.76973 | 0.76014 | 0.76609 | 0.74354 | 0.75148 | 0.75544 | 0.82417
43602.8111 | 0.75079 | 0.76249 | 0.75225 | 0.75836 | 0.73562 | 0.74385 | 0.74825 | 0.81908
43602.8113 | 0.74072 | 0.75301 | 0.74254 | 0.74893 | 0.7256 | 0.73428 | 0.73849 | 0.81268
43602.8112 | 0.73828 | 0.75072 | 0.73957 | 0.74607 | 0.72248 | 0.73101 | 0.73471 | 0.81017
43602.8114 | 0.733 | 0.7461 | 0.73472 | 0.74179 | 0.71778 | 0.72647 | 0.73001 | 0.80686
43602.8114 | 0.73015 | 0.74308 | 0.73167 | 0.73851 | 0.71425 | 0.72333 | 0.72967 | 0.80491
43602.8116 | 0.7212 | 0.73488 | 0.72313 | 0.72952 | 0.7054 | 0.71501 | 0.71951 | 0.79947
43602.8116 | 0.71432 | 0.72816 | 0.71631 | 0.72237 | 0.69791 | 0.70775 | 0.71255 | 0.7948
43602.8118 | 0.70073 | 0.71567 | 0.70293 | 0.70933 | 0.68381 | 0.69424 | 0.69964 | 0.78588
43602.8118 | 0.69467 | 0.7097 | 0.69662 | 0.70305 | 0.6771 | 0.68777 | 0.69347 | 0.78146
43602.812 | 0.6848 | 0.70081 | 0.68755 | 0.69405 | 0.66687 | 0.67795 | 0.6825 | 0.77462
43602.812 | 0.68386 | 0.6999 | 0.68656 | 0.69275 | 0.66585 | 0.67689 | 0.68261 | 0.7738
43602.8122 | 0.67597 | 0.6924 | 0.67851 | 0.68456 | 0.65696 | 0.66854 | 0.67435 | 0.76833
43602.8122 | 0.67399 | 0.69089 | 0.67698 | 0.68289 | 0.65464 | 0.66616 | 0.67185 | 0.76651
43602.8124 | 0.69215 | 0.70734 | 0.69424 | 0.70076 | 0.67308 | 0.68379 | 0.68872 | 0.7783
43602.8124 | 0.69507 | 0.70998 | 0.69685 | 0.70347 | 0.67635 | 0.68694 | 0.69112 | 0.78058
43602.8126 | 0.71527 | 0.7293 | 0.71775 | 0.72388 | 0.69843 | 0.70814 | 0.71218 | 0.79459
43602.8126 | 0.719 | 0.73272 | 0.721 | 0.72712 | 0.7023 | 0.71186 | 0.71597 | 0.79729
43602.8128 | 0.72261 | 0.73618 | 0.72464 | 0.73113 | 0.70631 | 0.7157 | 0.71966 | 0.80002
43602.8128 | 0.72533 | 0.73863 | 0.72708 | 0.73338 | 0.70847 | 0.71754 | 0.72251 | 0.8013
43602.813 | 0.72929 | 0.74267 | 0.7313 | 0.73792 | 0.71293 | 0.7219 | 0.72623 | 0.80402
43602.8129 | 0.73294 | 0.74576 | 0.73489 | 0.74124 | 0.71672 | 0.72541 | 0.73001 | 0.80639
43602.8131 | 0.73469 | 0.74735 | 0.7365 | 0.74276 | 0.71907 | 0.72781 | 0.73155 | 0.80794
43602.8131 | 0.73572 | 0.74853 | 0.73782 | 0.74386 | 0.72018 | 0.72874 | 0.7332 | 0.80876
43602.8133 | 0.73613 | 0.74907 | 0.73807 | 0.74437 | 0.72066 | 0.72925 | 0.73362 | 0.8095
43602.8133 | 0.73626 | 0.74911 | 0.7381 | 0.74464 | 0.72091 | 0.72963 | 0.73416 | 0.80975
43602.8135 | 0.73608 | 0.74906 | 0.73812 | 0.74434 | 0.72074 | 0.72974 | 0.73579 | 0.8096
43602.8135 | 0.73613 | 0.74883 | 0.73811 | 0.74435 | 0.72076 | 0.72964 | 0.73464 | 0.8095
43602.8137 | 0.737 | 0.74962 | 0.73872 | 0.74503 | 0.7213 | 0.73014 | 0.7366 | 0.81024
43602.8137 | 0.73682 | 0.74968 | 0.7389 | 0.74493 | 0.7213 | 0.73028 | 0.73804 | 0.81012
43602.8139 | 0.73755 | 0.75012 | 0.73944 | 0.74591 | 0.7221 | 0.73095 | 0.73476 | 0.81064
43602.8139 | 0.73772 | 0.7506 | 0.73962 | 0.74589 | 0.72239 | 0.73099 | 0.73832 | 0.8107
43602.8141 | 0.74001 | 0.75255 | 0.74173 | 0.74832 | 0.72419 | 0.73295 | 0.73759 | 0.81197
43602.8141 | 0.74348 | 0.75613 | 0.74529 | 0.75169 | 0.72771 | 0.73608 | 0.73977 | 0.81343
43602.8143 | 0.74986 | 0.762 | 0.7515 | 0.75799 | 0.73504 | 0.743 | 0.74826 | 0.81801
43602.8143 | 0.75127 | 0.76341 | 0.7532 | 0.75957 | 0.73669 | 0.74461 | 0.74821 | 0.81921
43602.8145 | 0.75307 | 0.76518 | 0.75504 | 0.76137 | 0.73864 | 0.74669 | 0.75008 | 0.8208
43602.8145 | 0.75386 | 0.76603 | 0.75581 | 0.76233 | 0.73959 | 0.74753 | 0.75182 | 0.82163
43602.8147 | 0.75489 | 0.76669 | 0.75647 | 0.76302 | 0.74043 | 0.74823 | 0.75182 | 0.82219
43602.8147 | 0.75507 | 0.76728 | 0.75718 | 0.76333 | 0.74071 | 0.7488 | 0.75496 | 0.82261
43602.8149 | 0.75471 | 0.76687 | 0.75654 | 0.76294 | 0.74069 | 0.74875 | 0.75433 | 0.82246
43602.8148 | 0.75509 | 0.76673 | 0.75669 | 0.76295 | 0.74074 | 0.74887 | 0.75272 | 0.82247
43602.8151 | 0.7559 | 0.7678 | 0.75763 | 0.76411 | 0.74166 | 0.74971 | 0.7544 | 0.82311
43602.815 | 0.75558 | 0.76745 | 0.75718 | 0.76362 | 0.74158 | 0.74947 | 0.75517 | 0.8229
43602.8152 | 0.75598 | 0.76782 | 0.75738 | 0.76397 | 0.74189 | 0.74963 | 0.75374 | 0.82324
43602.8152 | 0.75637 | 0.76814 | 0.75802 | 0.76443 | 0.74213 | 0.75008 | 0.75409 | 0.82328
43602.8154 | 0.75749 | 0.76925 | 0.75924 | 0.76554 | 0.74314 | 0.75109 | 0.75506 | 0.82406
43602.8154 | 0.75829 | 0.77019 | 0.76005 | 0.76633 | 0.74414 | 0.75216 | 0.75689 | 0.8247
43602.8156 | 0.759 | 0.771 | 0.76062 | 0.76761 | 0.74497 | 0.75282 | 0.75903 | 0.82521
43602.8156 | 0.7601 | 0.77178 | 0.7618 | 0.76806 | 0.74579 | 0.75372 | 0.7585 | 0.82575
43602.8158 | 0.7614 | 0.77313 | 0.76313 | 0.76953 | 0.74727 | 0.75481 | 0.75906 | 0.82665
43602.8158 | 0.76199 | 0.77369 | 0.76372 | 0.76988 | 0.74796 | 0.75557 | 0.75966 | 0.82714
43602.816 | 0.76218 | 0.77431 | 0.76448 | 0.77057 | 0.74868 | 0.75625 | 0.76173 | 0.8276
43602.816 | 0.76262 | 0.77452 | 0.76457 | 0.77083 | 0.74917 | 0.75667 | 0.76039 | 0.82775
43602.8162 | 0.76336 | 0.77514 | 0.76495 | 0.77153 | 0.74955 | 0.75717 | 0.76203 | 0.82819
43602.8162 | 0.76356 | 0.77506 | 0.76535 | 0.77155 | 0.74972 | 0.7574 | 0.76136 | 0.82823
43602.8164 | 0.76418 | 0.7759 | 0.76619 | 0.77251 | 0.75056 | 0.75805 | 0.762 | 0.82882
43602.8164 | 0.76456 | 0.77606 | 0.7665 | 0.77255 | 0.75076 | 0.75838 | 0.76204 | 0.82893
43602.8166 | 0.765 | 0.77649 | 0.76653 | 0.77275 | 0.75146 | 0.75894 | 0.76272 | 0.82927
43602.8166 | 0.76535 | 0.77705 | 0.76721 | 0.77355 | 0.75191 | 0.75939 | 0.76379 | 0.8295
43602.8168 | 0.76615 | 0.77783 | 0.768 | 0.7743 | 0.75271 | 0.7599 | 0.76558 | 0.82991
43602.8168 | 0.7666 | 0.77809 | 0.76829 | 0.77505 | 0.75321 | 0.76063 | 0.76657 | 0.83037
43602.817 | 0.76713 | 0.77844 | 0.76881 | 0.77536 | 0.75396 | 0.76105 | 0.76578 | 0.83063
43602.817 | 0.76735 | 0.77874 | 0.76918 | 0.77564 | 0.75402 | 0.76154 | 0.76503 | 0.83099
43602.8172 | 0.76762 | 0.77928 | 0.76958 | 0.77586 | 0.75451 | 0.76192 | 0.76799 | 0.83121
43602.8171 | 0.76777 | 0.77895 | 0.76956 | 0.77577 | 0.75452 | 0.76173 | 0.76566 | 0.83119
43602.8173 | 0.76858 | 0.77994 | 0.77056 | 0.7765 | 0.75501 | 0.76259 | 0.76846 | 0.8317
43602.8173 | 0.76906 | 0.78043 | 0.77102 | 0.77698 | 0.756 | 0.76325 | 0.7673 | 0.83213
43602.8175 | 0.76909 | 0.78029 | 0.77072 | 0.77688 | 0.75605 | 0.76345 | 0.76867 | 0.83233
43602.8175 | 0.76874 | 0.78022 | 0.77067 | 0.77697 | 0.75563 | 0.76327 | 0.76716 | 0.83198
43602.8177 | 0.76927 | 0.7806 | 0.77155 | 0.77704 | 0.75595 | 0.76351 | 0.76724 | 0.83223
43602.8177 | 0.76974 | 0.78107 | 0.77151 | 0.77741 | 0.75646 | 0.76391 | 0.76782 | 0.83247
43602.8179 | 0.76064 | 0.77313 | 0.76322 | 0.76923 | 0.74787 | 0.75541 | 0.75944 | 0.82691
43602.8179 | 0.75182 | 0.76449 | 0.75413 | 0.76042 | 0.73869 | 0.74687 | 0.75079 | 0.82116
43602.8181 | 0.7385 | 0.75182 | 0.74071 | 0.74681 | 0.72405 | 0.7327 | 0.73712 | 0.81184
43602.8181 | 0.7354 | 0.74907 | 0.73767 | 0.74376 | 0.72046 | 0.7292 | 0.73381 | 0.80936
43602.8183 | 0.7313 | 0.74518 | 0.73377 | 0.73984 | 0.7161 | 0.72496 | 0.72869 | 0.80594
43602.8183 | 0.72984 | 0.74355 | 0.73185 | 0.73816 | 0.71387 | 0.72283 | 0.72653 | 0.80478
43602.8185 | 0.72332 | 0.73713 | 0.72546 | 0.73131 | 0.70748 | 0.71702 | 0.72127 | 0.80104
43602.8185 | 0.71787 | 0.73177 | 0.71995 | 0.72601 | 0.70173 | 0.71121 | 0.71712 | 0.79725
43602.8187 | 0.70521 | 0.71987 | 0.70749 | 0.71331 | 0.6883 | 0.69869 | 0.70496 | 0.78898
43602.8187 | 0.69742 | 0.71235 | 0.69949 | 0.70539 | 0.6798 | 0.69039 | 0.69627 | 0.78347
43602.8189 | 0.68739 | 0.70286 | 0.68929 | 0.69583 | 0.66995 | 0.68079 | 0.68527 | 0.77677
43602.8189 | 0.68355 | 0.69947 | 0.68611 | 0.69187 | 0.66545 | 0.67685 | 0.6827 | 0.77398
43602.8191 | 0.67595 | 0.69255 | 0.67878 | 0.68452 | 0.65821 | 0.66963 | 0.67501 | 0.76919
43602.8191 | 0.67434 | 0.69134 | 0.67758 | 0.6828 | 0.65621 | 0.66784 | 0.67436 | 0.7678
43602.8193 | 0.68478 | 0.70072 | 0.68705 | 0.69349 | 0.6653 | 0.67658 | 0.6817 | 0.77384
43602.8193 | 0.69388 | 0.70938 | 0.69611 | 0.70205 | 0.67458 | 0.68541 | 0.69107 | 0.77965
43602.8195 | 0.70923 | 0.72379 | 0.71106 | 0.71701 | 0.69164 | 0.70186 | 0.70719 | 0.79052
43602.8195 | 0.7126 | 0.72717 | 0.71481 | 0.72023 | 0.6958 | 0.70589 | 0.71066 | 0.79313
43602.8197 | 0.7159 | 0.73016 | 0.71814 | 0.72407 | 0.69932 | 0.70945 | 0.7135 | 0.79574
43602.8197 | 0.71867 | 0.73262 | 0.72071 | 0.72674 | 0.70231 | 0.71175 | 0.71693 | 0.79747
43602.8199 | 0.72211 | 0.73595 | 0.72428 | 0.73003 | 0.70584 | 0.71534 | 0.71928 | 0.79976
43602.8199 | 0.72316 | 0.73689 | 0.72522 | 0.73091 | 0.70706 | 0.71628 | 0.72012 | 0.80046
43602.8201 | 0.7249 | 0.73856 | 0.72687 | 0.73253 | 0.70902 | 0.71838 | 0.72287 | 0.80197
43602.82 | 0.72616 | 0.73967 | 0.72806 | 0.73374 | 0.71023 | 0.71946 | 0.72384 | 0.80273
43602.8202 | 0.72633 | 0.74001 | 0.72824 | 0.73396 | 0.7104 | 0.71943 | 0.72443 | 0.80295
43602.8202 | 0.72572 | 0.73933 | 0.72761 | 0.7333 | 0.71002 | 0.71894 | 0.72674 | 0.80287
43602.8204 | 0.72497 | 0.73884 | 0.72701 | 0.73264 | 0.70902 | 0.71871 | 0.72442 | 0.8025
43602.8204 | 0.72525 | 0.7386 | 0.72699 | 0.73259 | 0.70873 | 0.71835 | 0.7231 | 0.80234
43602.8206 | 0.72458 | 0.73835 | 0.72677 | 0.73237 | 0.70851 | 0.71791 | 0.72301 | 0.80214
43602.8206 | 0.72433 | 0.73801 | 0.72638 | 0.73196 | 0.70859 | 0.7174 | 0.7229 | 0.80199
43602.8208 | 0.72443 | 0.73836 | 0.72651 | 0.73216 | 0.70855 | 0.71775 | 0.72269 | 0.80203
43602.8208 | 0.72488 | 0.73839 | 0.72717 | 0.73248 | 0.70874 | 0.71801 | 0.72262 | 0.80219
43602.821 | 0.72605 | 0.73961 | 0.7285 | 0.73348 | 0.71022 | 0.71935 | 0.72452 | 0.8031
43602.821 | 0.72616 | 0.73981 | 0.72819 | 0.73343 | 0.71014 | 0.71932 | 0.72556 | 0.80308
43602.8212 | 0.72751 | 0.74076 | 0.72936 | 0.73492 | 0.71162 | 0.7208 | 0.72652 | 0.8041
43602.8212 | 0.72791 | 0.74141 | 0.73015 | 0.73564 | 0.71219 | 0.72136 | 0.72574 | 0.80417
43602.8214 | 0.7397 | 0.75353 | 0.74291 | 0.7478 | 0.7242 | 0.73289 | 0.73871 | 0.81097
43602.8214 | 0.74201 | 0.75503 | 0.74437 | 0.74978 | 0.72695 | 0.73566 | 0.73923 | 0.81298
43602.8216 | 0.74236 | 0.75496 | 0.7445 | 0.74978 | 0.72753 | 0.73602 | 0.74012 | 0.81384
43602.8216 | 0.74268 | 0.75493 | 0.74423 | 0.74997 | 0.72732 | 0.73607 | 0.74056 | 0.81388
43602.8218 | 0.74257 | 0.75538 | 0.74462 | 0.75047 | 0.72774 | 0.73647 | 0.74266 | 0.8143
43602.8218 | 0.74234 | 0.75554 | 0.74469 | 0.75037 | 0.72762 | 0.73635 | 0.74085 | 0.81431
43602.822 | 0.74252 | 0.75536 | 0.74494 | 0.7509 | 0.72825 | 0.7369 | 0.74017 | 0.81459
43602.822 | 0.74283 | 0.75555 | 0.74509 | 0.75078 | 0.72838 | 0.73703 | 0.74169 | 0.81459
43602.8222 | 0.7435 | 0.7561 | 0.74531 | 0.75157 | 0.72872 | 0.73721 | 0.74159 | 0.81469
43602.8222 | 0.74378 | 0.75636 | 0.74563 | 0.75164 | 0.7292 | 0.73761 | 0.74185 | 0.815
43602.8224 | 0.74421 | 0.75687 | 0.7464 | 0.75218 | 0.72947 | 0.73798 | 0.7414 | 0.81539
43602.8224 | 0.74454 | 0.75709 | 0.74642 | 0.75238 | 0.72984 | 0.73835 | 0.7434 | 0.81569
43602.8226 | 0.74564 | 0.75804 | 0.74753 | 0.75321 | 0.73089 | 0.73948 | 0.74542 | 0.81633
43602.8226 | 0.74642 | 0.75843 | 0.748 | 0.75391 | 0.73157 | 0.73991 | 0.74438 | 0.81656
43602.8228 | 0.74746 | 0.75958 | 0.74968 | 0.75529 | 0.73274 | 0.74108 | 0.74788 | 0.81742
43602.8228 | 0.74772 | 0.76011 | 0.74971 | 0.75525 | 0.73294 | 0.74152 | 0.74579 | 0.81776
43602.823 | 0.74918 | 0.76138 | 0.751 | 0.75689 | 0.73458 | 0.74322 | 0.74709 | 0.81869
43602.823 | 0.74929 | 0.76172 | 0.7513 | 0.75707 | 0.7351 | 0.74369 | 0.74742 | 0.81891
43602.8232 | 0.75056 | 0.76279 | 0.75224 | 0.75838 | 0.7361 | 0.74439 | 0.75186 | 0.81952
43602.8232 | 0.75049 | 0.76288 | 0.7524 | 0.75823 | 0.73625 | 0.74453 | 0.74841 | 0.81959
43602.8234 | 0.75124 | 0.76342 | 0.75289 | 0.75861 | 0.73677 | 0.74498 | 0.74949 | 0.82003
43602.8234 | 0.75149 | 0.76351 | 0.75309 | 0.75882 | 0.73696 | 0.74533 | 0.74947 | 0.82016
43602.8236 | 0.75221 | 0.76418 | 0.75401 | 0.75999 | 0.73767 | 0.74603 | 0.75012 | 0.82064
43602.8236 | 0.75228 | 0.76409 | 0.75395 | 0.76002 | 0.73796 | 0.74626 | 0.74962 | 0.82084
43602.8238 | 0.75318 | 0.76506 | 0.7547 | 0.76097 | 0.73873 | 0.74686 | 0.75286 | 0.82126
43602.8237 | 0.75324 | 0.765 | 0.75487 | 0.76086 | 0.73868 | 0.74682 | 0.75058 | 0.82126
43602.824 | 0.75401 | 0.76567 | 0.7554 | 0.76142 | 0.73951 | 0.74765 | 0.75398 | 0.82182
43602.8239 | 0.75366 | 0.76551 | 0.75513 | 0.76093 | 0.73926 | 0.74743 | 0.75159 | 0.82159
43602.8242 | 0.75439 | 0.76596 | 0.75612 | 0.76179 | 0.73981 | 0.74828 | 0.75186 | 0.82193
43602.8241 | 0.75453 | 0.76626 | 0.75626 | 0.76186 | 0.74019 | 0.74857 | 0.75247 | 0.82207
43602.8243 | 0.75474 | 0.76664 | 0.75637 | 0.76204 | 0.74047 | 0.74858 | 0.75511 | 0.82246
43602.8243 | 0.75483 | 0.76688 | 0.75687 | 0.76201 | 0.74077 | 0.74868 | 0.75339 | 0.82253
43602.8245 | 0.75526 | 0.76705 | 0.75711 | 0.76277 | 0.74112 | 0.74912 | 0.75453 | 0.82258
43602.8245 | 0.75559 | 0.76723 | 0.75713 | 0.76301 | 0.74115 | 0.7496 | 0.75359 | 0.82277
43602.8247 | 0.75551 | 0.76741 | 0.75716 | 0.76311 | 0.74156 | 0.74962 | 0.75401 | 0.82304
43602.8247 | 0.75211 | 0.76437 | 0.75383 | 0.75961 | 0.73876 | 0.74703 | 0.75195 | 0.82126
43602.8249 | 0.74 | 0.75254 | 0.7417 | 0.74738 | 0.72559 | 0.73445 | 0.73829 | 0.81292
43602.8249 | 0.73435 | 0.74707 | 0.73584 | 0.74155 | 0.71958 | 0.72848 | 0.73366 | 0.80907
43602.8251 | 0.72564 | 0.73938 | 0.72784 | 0.73318 | 0.70914 | 0.71864 | 0.72218 | 0.80183
43602.8251 | 0.72349 | 0.73765 | 0.72605 | 0.73163 | 0.70815 | 0.71754 | 0.7213 | 0.80093
43602.8255 | 0.71769 | 0.73163 | 0.71943 | 0.7255 | 0.70175 | 0.7114 | 0.71623 | 0.79702
43602.8254 | 0.71112 | 0.72505 | 0.71294 | 0.71871 | 0.69444 | 0.70444 | 0.71227 | 0.79277
43602.8257 | 0.69498 | 0.7099 | 0.69677 | 0.70279 | 0.67771 | 0.68823 | 0.69393 | 0.78213
43602.8257 | 0.68807 | 0.7034 | 0.69009 | 0.69573 | 0.67029 | 0.68129 | 0.68975 | 0.77755
43602.8259 | 0.67833 | 0.69432 | 0.68051 | 0.68634 | 0.65979 | 0.67132 | 0.67715 | 0.77023
43602.8259 | 0.6732 | 0.68996 | 0.67527 | 0.68136 | 0.65444 | 0.66603 | 0.67158 | 0.76675
43602.8261 | 0.66901 | 0.68559 | 0.67142 | 0.67696 | 0.64978 | 0.66152 | 0.67025 | 0.76364
43602.8261 | 0.66897 | 0.68576 | 0.67166 | 0.67689 | 0.64878 | 0.66062 | 0.6663 | 0.76301
43602.8263 | 0.68635 | 0.70245 | 0.68922 | 0.69463 | 0.66657 | 0.6781 | 0.68362 | 0.77462
43602.8263 | 0.69426 | 0.70974 | 0.69654 | 0.70205 | 0.67611 | 0.68693 | 0.69136 | 0.78051
43602.8265 | 0.7028 | 0.71771 | 0.70503 | 0.71079 | 0.68554 | 0.69608 | 0.7009 | 0.78662
43602.8265 | 0.70522 | 0.71986 | 0.70762 | 0.71325 | 0.68757 | 0.69797 | 0.70397 | 0.78812
43602.8267 | 0.7086 | 0.72282 | 0.71049 | 0.71649 | 0.69088 | 0.70092 | 0.7058 | 0.79023
43602.8267 | 0.70941 | 0.72341 | 0.71132 | 0.71701 | 0.69197 | 0.70216 | 0.70767 | 0.79107
43602.8269 | 0.71334 | 0.7273 | 0.71522 | 0.72102 | 0.69648 | 0.70622 | 0.71159 | 0.79379
43602.8269 | 0.71528 | 0.72932 | 0.7173 | 0.72308 | 0.69863 | 0.70841 | 0.71333 | 0.79506
43602.8271 | 0.71583 | 0.72963 | 0.71762 | 0.72328 | 0.6989 | 0.7089 | 0.71454 | 0.79527
43602.8271 | 0.71709 | 0.73083 | 0.71891 | 0.72444 | 0.70038 | 0.71017 | 0.7146 | 0.79645
43602.8273 | 0.71929 | 0.73286 | 0.72117 | 0.72706 | 0.7029 | 0.71243 | 0.71707 | 0.79811
43602.8273 | 0.72031 | 0.734 | 0.72219 | 0.72795 | 0.70414 | 0.71342 | 0.71999 | 0.79883
43602.8275 | 0.72298 | 0.73673 | 0.72522 | 0.73061 | 0.70671 | 0.71627 | 0.72078 | 0.8005
43602.8275 | 0.72614 | 0.73977 | 0.72844 | 0.73389 | 0.70964 | 0.71895 | 0.72272 | 0.8022
43602.8277 | 0.72929 | 0.74252 | 0.73139 | 0.73696 | 0.71314 | 0.72227 | 0.72587 | 0.80418
43602.8277 | 0.7313 | 0.74466 | 0.73357 | 0.73907 | 0.71539 | 0.72442 | 0.72798 | 0.80574
43602.8279 | 0.73415 | 0.74715 | 0.7364 | 0.74169 | 0.71847 | 0.72751 | 0.73278 | 0.80816
43602.8279 | 0.73612 | 0.7492 | 0.73861 | 0.7439 | 0.72091 | 0.72974 | 0.73395 | 0.80949
43602.8281 | 0.73809 | 0.75094 | 0.74046 | 0.74629 | 0.72308 | 0.73172 | 0.73537 | 0.81091
43602.8281 | 0.74089 | 0.75365 | 0.74334 | 0.74873 | 0.72582 | 0.73441 | 0.73883 | 0.81266
43602.8283 | 0.74429 | 0.75696 | 0.74641 | 0.75222 | 0.72954 | 0.73788 | 0.74172 | 0.81486
43602.8283 | 0.74506 | 0.75759 | 0.74695 | 0.75276 | 0.73015 | 0.73874 | 0.74281 | 0.81545
43602.8285 | 0.74769 | 0.75967 | 0.74962 | 0.75545 | 0.73262 | 0.7412 | 0.74759 | 0.81721
43602.8284 | 0.74929 | 0.76127 | 0.75101 | 0.75673 | 0.73433 | 0.74264 | 0.74671 | 0.81801
43602.8286 | 0.75153 | 0.76368 | 0.7534 | 0.75934 | 0.73698 | 0.74501 | 0.75016 | 0.81979
43602.8286 | 0.75197 | 0.76377 | 0.75357 | 0.75949 | 0.73721 | 0.74517 | 0.75012 | 0.81996
43602.8288 | 0.75491 | 0.76692 | 0.75646 | 0.76218 | 0.7403 | 0.7485 | 0.7541 | 0.82208
43602.8288 | 0.75558 | 0.76716 | 0.75691 | 0.76266 | 0.74109 | 0.749 | 0.75411 | 0.82245
43602.829 | 0.75802 | 0.76943 | 0.75969 | 0.76565 | 0.74384 | 0.75175 | 0.75544 | 0.82431
43602.829 | 0.75906 | 0.77056 | 0.76131 | 0.7664 | 0.74492 | 0.75286 | 0.75694 | 0.82501
43602.8292 | 0.7598 | 0.77168 | 0.76209 | 0.76742 | 0.74631 | 0.75382 | 0.75771 | 0.82581
43602.8292 | 0.76169 | 0.77316 | 0.76345 | 0.76911 | 0.74775 | 0.75537 | 0.76123 | 0.82663
43602.8294 | 0.76375 | 0.77513 | 0.7655 | 0.7708 | 0.74992 | 0.75768 | 0.76271 | 0.82806
43602.8294 | 0.76466 | 0.77594 | 0.76641 | 0.77191 | 0.7511 | 0.75867 | 0.76241 | 0.82872
43602.8296 | 0.76623 | 0.77755 | 0.76791 | 0.77359 | 0.75282 | 0.7603 | 0.76465 | 0.83003
43602.8296 | 0.7674 | 0.77868 | 0.76902 | 0.77479 | 0.75412 | 0.76155 | 0.76702 | 0.83072
43602.8298 | 0.76877 | 0.77983 | 0.77048 | 0.77608 | 0.75538 | 0.76286 | 0.76677 | 0.83164
43602.8298 | 0.77006 | 0.781 | 0.77173 | 0.77718 | 0.75644 | 0.76402 | 0.76803 | 0.83228
43602.83 | 0.77159 | 0.78274 | 0.7733 | 0.77907 | 0.75842 | 0.76604 | 0.76953 | 0.83358
43602.83 | 0.77258 | 0.78359 | 0.77431 | 0.77997 | 0.7594 | 0.76694 | 0.77159 | 0.83427
43602.8302 | 0.77418 | 0.78509 | 0.7759 | 0.78177 | 0.7614 | 0.7687 | 0.77403 | 0.83545
43602.8302 | 0.77529 | 0.78604 | 0.77664 | 0.78246 | 0.76195 | 0.7694 | 0.77277 | 0.83592
43602.8304 | 0.77691 | 0.78794 | 0.77855 | 0.78422 | 0.76418 | 0.77128 | 0.77557 | 0.83711
43602.8304 | 0.77807 | 0.7889 | 0.77973 | 0.78529 | 0.76513 | 0.77242 | 0.77785 | 0.8379
43602.8306 | 0.77918 | 0.78994 | 0.78114 | 0.7863 | 0.76643 | 0.7735 | 0.7788 | 0.83871
43602.8306 | 0.78065 | 0.7913 | 0.78243 | 0.78789 | 0.768 | 0.77504 | 0.77824 | 0.8395
43602.8308 | 0.78294 | 0.79376 | 0.78519 | 0.79059 | 0.77012 | 0.77736 | 0.78029 | 0.84101
43602.8308 | 0.78322 | 0.79393 | 0.78506 | 0.79063 | 0.77061 | 0.77771 | 0.78081 | 0.84158
43602.8311 | 0.78565 | 0.79579 | 0.78748 | 0.79282 | 0.773 | 0.77958 | 0.7827 | 0.84279
43602.831 | 0.78625 | 0.79663 | 0.78798 | 0.79372 | 0.77364 | 0.78044 | 0.78413 | 0.84336
43602.8313 | 0.78799 | 0.79834 | 0.78971 | 0.79498 | 0.77535 | 0.78195 | 0.78709 | 0.84408
43602.8312 | 0.78839 | 0.79854 | 0.79023 | 0.79529 | 0.77592 | 0.78265 | 0.7859 | 0.84459
43602.8314 | 0.79052 | 0.80038 | 0.79211 | 0.79731 | 0.77791 | 0.78473 | 0.78821 | 0.84583
43602.8314 | 0.79065 | 0.80048 | 0.79227 | 0.79732 | 0.77798 | 0.78447 | 0.7877 | 0.84599
43602.8316 | 0.79218 | 0.80194 | 0.7937 | 0.79907 | 0.77975 | 0.7866 | 0.78961 | 0.84713
43602.8316 | 0.79264 | 0.80242 | 0.79412 | 0.79962 | 0.7801 | 0.78661 | 0.78949 | 0.84724
43602.8318 | 0.79415 | 0.80405 | 0.79568 | 0.80102 | 0.78218 | 0.78839 | 0.79129 | 0.84842
43602.8318 | 0.79474 | 0.80468 | 0.79625 | 0.80149 | 0.78264 | 0.78885 | 0.79163 | 0.84877
43602.832 | 0.79611 | 0.80572 | 0.79782 | 0.80271 | 0.78378 | 0.79016 | 0.79503 | 0.84954
43602.832 | 0.79631 | 0.80603 | 0.79819 | 0.80323 | 0.78444 | 0.79062 | 0.79336 | 0.84986
43602.8322 | 0.79716 | 0.80712 | 0.79901 | 0.80467 | 0.78559 | 0.792 | 0.79493 | 0.85072
43602.8322 | 0.79857 | 0.80814 | 0.80026 | 0.80576 | 0.78704 | 0.79307 | 0.79584 | 0.85152
43602.8324 | 0.79887 | 0.80869 | 0.80058 | 0.80594 | 0.78748 | 0.79344 | 0.79822 | 0.85197
43602.8324 | 0.79927 | 0.80928 | 0.80082 | 0.80624 | 0.788 | 0.79372 | 0.79758 | 0.85216
43602.8326 | 0.8011 | 0.81097 | 0.80288 | 0.80868 | 0.79006 | 0.79577 | 0.79925 | 0.8535
43602.8326 | 0.80163 | 0.81122 | 0.80342 | 0.80872 | 0.79029 | 0.79618 | 0.80012 | 0.85358
43602.8328 | 0.80252 | 0.81214 | 0.80422 | 0.80996 | 0.79139 | 0.79727 | 0.80012 | 0.85449
43602.8328 | 0.80229 | 0.81202 | 0.80413 | 0.80979 | 0.79136 | 0.79747 | 0.80086 | 0.85434
43602.833 | 0.80309 | 0.81286 | 0.80505 | 0.81077 | 0.79149 | 0.79762 | 0.80023 | 0.85462
43602.833 | 0.80406 | 0.81366 | 0.80589 | 0.81153 | 0.79321 | 0.79918 | 0.80266 | 0.8554
43602.8332 | 0.80409 | 0.81387 | 0.80583 | 0.8113 | 0.79307 | 0.79903 | 0.80194 | 0.85553
43602.8332 | 0.8043 | 0.81397 | 0.80597 | 0.81172 | 0.79338 | 0.79942 | 0.80195 | 0.85569
43602.8334 | 0.80522 | 0.81473 | 0.80724 | 0.81274 | 0.79454 | 0.80029 | 0.80304 | 0.85621
43602.8334 | 0.80585 | 0.81491 | 0.80744 | 0.81299 | 0.79472 | 0.80055 | 0.80309 | 0.85634
43602.8336 | 0.8066 | 0.81584 | 0.80802 | 0.81336 | 0.79534 | 0.8012 | 0.80502 | 0.85673
43602.8336 | 0.80613 | 0.81548 | 0.80773 | 0.81293 | 0.79522 | 0.80088 | 0.80348 | 0.85655
43602.8338 | 0.8067 | 0.81579 | 0.80832 | 0.81401 | 0.79566 | 0.80152 | 0.80402 | 0.857
43602.8338 | 0.80785 | 0.81694 | 0.80973 | 0.81461 | 0.79646 | 0.80219 | 0.80671 | 0.85747
43602.834 | 0.80731 | 0.81654 | 0.80924 | 0.81478 | 0.79669 | 0.80212 | 0.80696 | 0.85743
43602.834 | 0.80768 | 0.81705 | 0.80977 | 0.81504 | 0.79685 | 0.80252 | 0.80522 | 0.85759
43602.8342 | 0.80839 | 0.81763 | 0.81025 | 0.81571 | 0.79756 | 0.80316 | 0.80621 | 0.85809
43602.8341 | 0.80766 | 0.81713 | 0.80967 | 0.81509 | 0.79713 | 0.80281 | 0.80547 | 0.85779
43602.8344 | 0.80806 | 0.81759 | 0.81035 | 0.81528 | 0.79736 | 0.80305 | 0.80518 | 0.85804
43602.8343 | 0.80854 | 0.81773 | 0.81052 | 0.81569 | 0.79791 | 0.80339 | 0.80716 | 0.85829
43602.8345 | 0.80801 | 0.8177 | 0.81007 | 0.81574 | 0.79761 | 0.80326 | 0.80543 | 0.85809
43602.8345 | 0.80846 | 0.81804 | 0.81074 | 0.81585 | 0.79799 | 0.8036 | 0.80671 | 0.85828
43602.8347 | 0.80835 | 0.81817 | 0.81079 | 0.81591 | 0.79817 | 0.80356 | 0.80629 | 0.85843
43602.8347 | 0.8084 | 0.81804 | 0.81072 | 0.81577 | 0.79798 | 0.80375 | 0.80807 | 0.85822
43602.8349 | 0.80856 | 0.81802 | 0.81044 | 0.81615 | 0.79769 | 0.8034 | 0.80783 | 0.85818
43602.8349 | 0.80839 | 0.81766 | 0.8102 | 0.81567 | 0.79758 | 0.8033 | 0.80616 | 0.85812
43602.8351 | 0.80843 | 0.8177 | 0.81037 | 0.81565 | 0.79786 | 0.80346 | 0.80791 | 0.85838
43602.8351 | 0.80879 | 0.81775 | 0.81051 | 0.81581 | 0.79764 | 0.80335 | 0.80569 | 0.85812
43602.8353 | 0.80893 | 0.81792 | 0.81064 | 0.81613 | 0.79814 | 0.80369 | 0.80638 | 0.85838
43602.8353 | 0.80914 | 0.81825 | 0.81095 | 0.8163 | 0.79802 | 0.80386 | 0.80694 | 0.85841
43602.8355 | 0.80969 | 0.81861 | 0.81144 | 0.81657 | 0.79835 | 0.80419 | 0.80717 | 0.85862
43602.8355 | 0.80945 | 0.81849 | 0.81134 | 0.81654 | 0.79835 | 0.80423 | 0.80749 | 0.85862
43602.8357 | 0.81004 | 0.81868 | 0.81189 | 0.81685 | 0.79885 | 0.80453 | 0.80943 | 0.85885
43602.8357 | 0.80999 | 0.81884 | 0.81156 | 0.81697 | 0.79901 | 0.80484 | 0.80789 | 0.859
43602.8359 | 0.81059 | 0.81964 | 0.81231 | 0.81744 | 0.79982 | 0.80534 | 0.8078 | 0.85934
43602.8359 | 0.81066 | 0.81955 | 0.81235 | 0.81769 | 0.79988 | 0.80546 | 0.81044 | 0.85943
43602.8361 | 0.81063 | 0.81987 | 0.8128 | 0.81753 | 0.79976 | 0.80543 | 0.80861 | 0.85952
43602.8361 | 0.81095 | 0.8198 | 0.81254 | 0.81776 | 0.79968 | 0.80551 | 0.80794 | 0.85949
43602.8363 | 0.80979 | 0.81902 | 0.8114 | 0.81677 | 0.79908 | 0.80463 | 0.80711 | 0.85902
43602.8363 | 0.81132 | 0.82042 | 0.81288 | 0.81809 | 0.80029 | 0.80594 | 0.80846 | 0.85976
43602.8365 | 0.81151 | 0.82052 | 0.81329 | 0.81815 | 0.80002 | 0.80564 | 0.81009 | 0.8597
43602.8365 | 0.81229 | 0.82125 | 0.81398 | 0.81933 | 0.80154 | 0.80682 | 0.81007 | 0.86057
43602.8367 | 0.81183 | 0.82091 | 0.81349 | 0.81883 | 0.801 | 0.80674 | 0.81085 | 0.86032
43602.8367 | 0.81288 | 0.82154 | 0.8142 | 0.81951 | 0.80184 | 0.80746 | 0.81071 | 0.86087
43602.8369 | 0.81437 | 0.82321 | 0.81599 | 0.82128 | 0.80361 | 0.80942 | 0.81197 | 0.86197
43602.8369 | 0.81416 | 0.82276 | 0.81575 | 0.82099 | 0.80356 | 0.80918 | 0.81154 | 0.86187
43602.8371 | 0.81404 | 0.82278 | 0.81573 | 0.82108 | 0.80283 | 0.80859 | 0.812 | 0.86144
43602.8371 | 0.81457 | 0.82316 | 0.81611 | 0.82106 | 0.80347 | 0.80927 | 0.81205 | 0.86194
43602.8373 | 0.8157 | 0.82447 | 0.81753 | 0.8226 | 0.8051 | 0.81076 | 0.8136 | 0.86291
43602.8373 | 0.81582 | 0.8244 | 0.81745 | 0.82252 | 0.80522 | 0.81086 | 0.81322 | 0.86282
43602.8375 | 0.81601 | 0.82463 | 0.81773 | 0.82325 | 0.80545 | 0.81102 | 0.81507 | 0.86285
43602.8375 | 0.81594 | 0.82459 | 0.81772 | 0.82293 | 0.80529 | 0.81071 | 0.81419 | 0.86289
43602.8377 | 0.81725 | 0.82608 | 0.81909 | 0.82408 | 0.80646 | 0.81209 | 0.81624 | 0.86376
43602.8377 | 0.81679 | 0.82552 | 0.8185 | 0.82386 | 0.80616 | 0.81165 | 0.81411 | 0.86341
43602.8379 | 0.8181 | 0.82681 | 0.82021 | 0.82513 | 0.80781 | 0.81272 | 0.81558 | 0.86449
43602.8378 | 0.81795 | 0.82649 | 0.81967 | 0.82474 | 0.80726 | 0.8127 | 0.81505 | 0.8642
43602.8381 | 0.81765 | 0.82608 | 0.81945 | 0.82459 | 0.80704 | 0.81233 | 0.81488 | 0.864
43602.838 | 0.8185 | 0.82701 | 0.81993 | 0.82523 | 0.80791 | 0.81317 | 0.8153 | 0.86444
43602.8382 | 0.81827 | 0.82692 | 0.81998 | 0.8254 | 0.80766 | 0.81277 | 0.81578 | 0.86419
43602.8382 | 0.81778 | 0.82645 | 0.81964 | 0.82454 | 0.80745 | 0.81263 | 0.81624 | 0.86411
43602.8384 | 0.81752 | 0.82617 | 0.8193 | 0.82481 | 0.8071 | 0.81241 | 0.81522 | 0.86405
43602.8384 | 0.81793 | 0.82654 | 0.81975 | 0.82479 | 0.80743 | 0.8125 | 0.81573 | 0.8642
43602.8387 | 0.81727 | 0.82571 | 0.81912 | 0.82433 | 0.80638 | 0.81176 | 0.81589 | 0.86351
43602.8386 | 0.81777 | 0.82655 | 0.81956 | 0.82471 | 0.80727 | 0.81269 | 0.81564 | 0.86399
43602.8388 | 0.81769 | 0.82637 | 0.81913 | 0.8243 | 0.80682 | 0.81226 | 0.81579 | 0.86361
43602.8388 | 0.81769 | 0.82645 | 0.81907 | 0.82449 | 0.80686 | 0.81229 | 0.81502 | 0.86381
43602.839 | 0.81684 | 0.82532 | 0.81859 | 0.82381 | 0.80654 | 0.81156 | 0.81501 | 0.86342
43602.839 | 0.81697 | 0.82554 | 0.81869 | 0.82368 | 0.80656 | 0.81173 | 0.81518 | 0.86351
43602.8392 | 0.81781 | 0.82649 | 0.81961 | 0.82472 | 0.80743 | 0.81245 | 0.81698 | 0.86406
43602.8392 | 0.81719 | 0.82567 | 0.81843 | 0.82415 | 0.80648 | 0.81165 | 0.8147 | 0.86357
43602.8394 | 0.81788 | 0.8264 | 0.81965 | 0.82468 | 0.80724 | 0.81225 | 0.81485 | 0.8639
43602.8394 | 0.81723 | 0.82593 | 0.81911 | 0.82414 | 0.80715 | 0.81237 | 0.81495 | 0.86391
43602.8396 | 0.81667 | 0.82514 | 0.81844 | 0.82379 | 0.80625 | 0.81165 | 0.81558 | 0.86334
43602.8396 | 0.81695 | 0.8256 | 0.81883 | 0.8237 | 0.80638 | 0.8119 | 0.81501 | 0.86353
43602.8398 | 0.81795 | 0.82669 | 0.82016 | 0.82493 | 0.80742 | 0.81281 | 0.81663 | 0.8641
43602.8398 | 0.81675 | 0.82517 | 0.81842 | 0.82337 | 0.80624 | 0.8117 | 0.81463 | 0.86338
43602.84 | 0.81685 | 0.82535 | 0.81904 | 0.82369 | 0.80629 | 0.81174 | 0.81407 | 0.8634
43602.84 | 0.8182 | 0.82691 | 0.82035 | 0.8249 | 0.80796 | 0.81322 | 0.81728 | 0.8644
43602.8402 | 0.8163 | 0.82525 | 0.81879 | 0.82334 | 0.80612 | 0.81123 | 0.81516 | 0.86318
43602.8402 | 0.81671 | 0.82551 | 0.81901 | 0.82356 | 0.80684 | 0.81178 | 0.81455 | 0.8635
43602.8404 | 0.81471 | 0.82368 | 0.81677 | 0.82158 | 0.80444 | 0.8096 | 0.81219 | 0.86217
43602.8404 | 0.8162 | 0.82507 | 0.81829 | 0.82332 | 0.80602 | 0.81135 | 0.8135 | 0.86309
43602.8406 | 0.81445 | 0.82374 | 0.81672 | 0.82195 | 0.80417 | 0.80963 | 0.81247 | 0.86209
43602.8406 | 0.81578 | 0.82466 | 0.81816 | 0.82284 | 0.8051 | 0.81059 | 0.81344 | 0.86262
43602.8408 | 0.81435 | 0.8232 | 0.81661 | 0.82166 | 0.80405 | 0.80958 | 0.81168 | 0.86206
43602.8408 | 0.81445 | 0.82343 | 0.8164 | 0.82143 | 0.80409 | 0.8093 | 0.81176 | 0.86186
43602.841 | 0.81407 | 0.82324 | 0.81644 | 0.82152 | 0.80402 | 0.80915 | 0.81158 | 0.86176
43602.841 | 0.81533 | 0.82438 | 0.81766 | 0.82261 | 0.80526 | 0.81045 | 0.81361 | 0.86267
43602.8412 | 0.81412 | 0.823 | 0.81612 | 0.82125 | 0.80358 | 0.8089 | 0.8116 | 0.86159
43602.8412 | 0.81542 | 0.82439 | 0.81757 | 0.82251 | 0.80515 | 0.81023 | 0.81279 | 0.86252
43602.8414 | 0.81296 | 0.82197 | 0.81532 | 0.8202 | 0.80291 | 0.80804 | 0.81195 | 0.86103
43602.8414 | 0.81436 | 0.82363 | 0.81658 | 0.82178 | 0.80435 | 0.80959 | 0.81217 | 0.8619
43602.8416 | 0.81263 | 0.82196 | 0.8151 | 0.82002 | 0.80209 | 0.80762 | 0.8104 | 0.86062
43602.8416 | 0.81383 | 0.823 | 0.81595 | 0.82091 | 0.80358 | 0.80864 | 0.8116 | 0.86157
43602.8418 | 0.81314 | 0.82242 | 0.81524 | 0.82053 | 0.803 | 0.80837 | 0.81076 | 0.86121
43602.8418 | 0.8135 | 0.8227 | 0.81578 | 0.82046 | 0.80322 | 0.8085 | 0.81133 | 0.8613
43602.842 | 0.81271 | 0.82212 | 0.81504 | 0.82012 | 0.80251 | 0.80805 | 0.81135 | 0.86086
43602.842 | 0.81281 | 0.82213 | 0.81515 | 0.81969 | 0.80263 | 0.80791 | 0.81139 | 0.86094
43602.8422 | 0.81181 | 0.82102 | 0.81416 | 0.81898 | 0.80156 | 0.80688 | 0.81133 | 0.8602
43602.8422 | 0.81239 | 0.82175 | 0.81457 | 0.8196 | 0.80208 | 0.80754 | 0.81045 | 0.86064
43602.8424 | 0.81105 | 0.82045 | 0.81339 | 0.81841 | 0.80039 | 0.80586 | 0.80834 | 0.85954
43602.8424 | 0.81191 | 0.82096 | 0.81399 | 0.81905 | 0.80142 | 0.80696 | 0.81088 | 0.86015
43602.8426 | 0.81058 | 0.82004 | 0.81293 | 0.81813 | 0.79981 | 0.80597 | 0.80989 | 0.85924
43602.8426 | 0.80993 | 0.81944 | 0.81256 | 0.81712 | 0.79953 | 0.80512 | 0.80818 | 0.85892
43602.8428 | 0.80949 | 0.819 | 0.81194 | 0.81698 | 0.79921 | 0.80496 | 0.80812 | 0.85888
43602.8428 | 0.8094 | 0.81876 | 0.81189 | 0.81675 | 0.79896 | 0.80449 | 0.80724 | 0.85842
43602.843 | 0.80827 | 0.81804 | 0.81068 | 0.81625 | 0.79802 | 0.80361 | 0.80687 | 0.85795
43602.843 | 0.80799 | 0.81749 | 0.81025 | 0.81544 | 0.79774 | 0.80339 | 0.80718 | 0.85775
43602.8432 | 0.80761 | 0.81732 | 0.8102 | 0.81523 | 0.79777 | 0.80302 | 0.8067 | 0.85749
43602.8432 | 0.80724 | 0.81699 | 0.80979 | 0.81484 | 0.79724 | 0.80276 | 0.80527 | 0.85724
43602.8434 | 0.80569 | 0.81549 | 0.80814 | 0.81322 | 0.79544 | 0.80126 | 0.80408 | 0.85627
43602.8434 | 0.80689 | 0.81651 | 0.80958 | 0.8142 | 0.79645 | 0.80238 | 0.80521 | 0.85689
43602.8436 | 0.80612 | 0.81557 | 0.80803 | 0.81327 | 0.79533 | 0.80111 | 0.806 | 0.8562
43602.8436 | 0.80611 | 0.81546 | 0.80807 | 0.81297 | 0.79539 | 0.80101 | 0.80397 | 0.85603
43602.8438 | 0.80487 | 0.81446 | 0.80726 | 0.81203 | 0.7941 | 0.79997 | 0.80495 | 0.85531
43602.8438 | 0.80558 | 0.81524 | 0.808 | 0.81271 | 0.7947 | 0.80079 | 0.80404 | 0.85584
43602.844 | 0.80362 | 0.8133 | 0.80591 | 0.81069 | 0.79285 | 0.79878 | 0.80166 | 0.85454
43602.844 | 0.80414 | 0.81358 | 0.80614 | 0.81126 | 0.79342 | 0.79875 | 0.80213 | 0.85484
43602.8442 | 0.80142 | 0.81111 | 0.80397 | 0.80883 | 0.79072 | 0.79689 | 0.79931 | 0.85315
43602.8442 | 0.80263 | 0.81215 | 0.80494 | 0.80984 | 0.7919 | 0.79797 | 0.80128 | 0.85393
43602.8444 | 0.80082 | 0.81053 | 0.80334 | 0.80806 | 0.79037 | 0.79604 | 0.79904 | 0.85282
43602.8444 | 0.80101 | 0.81066 | 0.80324 | 0.80779 | 0.78999 | 0.79583 | 0.79962 | 0.85256
43602.8446 | 0.80239 | 0.81189 | 0.80494 | 0.80929 | 0.79186 | 0.79768 | 0.80205 | 0.85383
43602.8446 | 0.79971 | 0.80934 | 0.80216 | 0.80681 | 0.78912 | 0.79496 | 0.79801 | 0.85207
43602.8448 | 0.80075 | 0.81032 | 0.80284 | 0.80793 | 0.78998 | 0.79576 | 0.7986 | 0.8524
43602.8448 | 0.80029 | 0.8098 | 0.80254 | 0.80745 | 0.78954 | 0.79513 | 0.79786 | 0.85227
43602.845 | 0.79702 | 0.80683 | 0.79948 | 0.80478 | 0.78579 | 0.79198 | 0.79717 | 0.84997
43602.845 | 0.79965 | 0.80935 | 0.80216 | 0.80717 | 0.78857 | 0.79441 | 0.79761 | 0.85177
43602.8452 | 0.79828 | 0.80783 | 0.8001 | 0.80543 | 0.78691 | 0.79303 | 0.79769 | 0.85075
43602.8452 | 0.79731 | 0.80692 | 0.79915 | 0.80466 | 0.78565 | 0.79174 | 0.79507 | 0.84998
43602.8454 | 0.79815 | 0.80775 | 0.80023 | 0.80519 | 0.7869 | 0.79306 | 0.79606 | 0.85066
43602.8454 | 0.79624 | 0.80562 | 0.79798 | 0.80272 | 0.7844 | 0.7908 | 0.79361 | 0.8491
43602.8456 | 0.79512 | 0.80465 | 0.79689 | 0.80163 | 0.78335 | 0.78976 | 0.79302 | 0.84852
43602.8456 | 0.79334 | 0.8031 | 0.79551 | 0.80004 | 0.78151 | 0.78796 | 0.7931 | 0.84733
43602.8458 | 0.796 | 0.80581 | 0.79799 | 0.80303 | 0.78454 | 0.79078 | 0.79397 | 0.84921
43602.8458 | 0.79379 | 0.80366 | 0.79565 | 0.80085 | 0.78223 | 0.78873 | 0.7936 | 0.84773
43602.846 | 0.79444 | 0.80399 | 0.79653 | 0.80144 | 0.7814 | 0.78783 | 0.79105 | 0.84725
43602.846 | 0.79502 | 0.80465 | 0.7969 | 0.80169 | 0.78307 | 0.78949 | 0.79273 | 0.84834
43602.8462 | 0.79172 | 0.80144 | 0.7936 | 0.7985 | 0.77975 | 0.78616 | 0.78938 | 0.8461
43602.8462 | 0.79153 | 0.80176 | 0.79397 | 0.79835 | 0.77893 | 0.78548 | 0.78879 | 0.84561
43602.8464 | 0.79094 | 0.80082 | 0.79287 | 0.79778 | 0.77917 | 0.78582 | 0.78933 | 0.84574
43602.8464 | 0.78929 | 0.79907 | 0.7911 | 0.79612 | 0.77717 | 0.78375 | 0.78875 | 0.84448
43602.8466 | 0.78897 | 0.7989 | 0.79103 | 0.79593 | 0.77704 | 0.78352 | 0.78686 | 0.84422
43602.8466 | 0.78808 | 0.79795 | 0.78982 | 0.79483 | 0.77598 | 0.78247 | 0.78764 | 0.84374
43602.8468 | 0.78665 | 0.79658 | 0.78887 | 0.7933 | 0.77422 | 0.78058 | 0.78443 | 0.84267
43602.8468 | 0.78574 | 0.79584 | 0.78795 | 0.79232 | 0.77344 | 0.78016 | 0.78564 | 0.84216
43602.8471 | 0.78713 | 0.79735 | 0.78943 | 0.794 | 0.77484 | 0.78137 | 0.78518 | 0.84285
43602.847 | 0.78724 | 0.79745 | 0.78927 | 0.79434 | 0.77514 | 0.78198 | 0.78517 | 0.84304
43602.8473 | 0.78396 | 0.79426 | 0.7861 | 0.79086 | 0.77203 | 0.77861 | 0.78181 | 0.84106
43602.8473 | 0.7853 | 0.79555 | 0.78769 | 0.79231 | 0.77345 | 0.77991 | 0.78303 | 0.84193
43602.8475 | 0.78545 | 0.79537 | 0.78762 | 0.79246 | 0.77377 | 0.78029 | 0.7834 | 0.84214
43602.8475 | 0.78284 | 0.79329 | 0.7853 | 0.79003 | 0.77101 | 0.77764 | 0.78256 | 0.84032
43602.8477 | 0.78373 | 0.79398 | 0.7862 | 0.79083 | 0.77184 | 0.77807 | 0.78184 | 0.8407
43602.8477 | 0.78375 | 0.79408 | 0.78599 | 0.79082 | 0.77175 | 0.77797 | 0.78155 | 0.84091
43602.8479 | 0.78039 | 0.79093 | 0.78264 | 0.78758 | 0.76847 | 0.77521 | 0.77852 | 0.83866
43602.8479 | 0.78242 | 0.79294 | 0.78492 | 0.78945 | 0.77057 | 0.77696 | 0.78061 | 0.83994
43602.8481 | 0.78304 | 0.79333 | 0.78512 | 0.78984 | 0.77134 | 0.77787 | 0.78086 | 0.84051
43602.8481 | 0.78122 | 0.79148 | 0.78326 | 0.78803 | 0.76906 | 0.77592 | 0.77904 | 0.83901
43602.8483 | 0.7822 | 0.79242 | 0.78451 | 0.78919 | 0.76996 | 0.77659 | 0.78018 | 0.83957
43602.8483 | 0.78117 | 0.79142 | 0.78347 | 0.78825 | 0.76925 | 0.77565 | 0.77912 | 0.83903
43602.8485 | 0.77838 | 0.78878 | 0.78038 | 0.7854 | 0.76592 | 0.77261 | 0.77676 | 0.83706
43602.8485 | 0.77848 | 0.78896 | 0.78102 | 0.78561 | 0.76611 | 0.77282 | 0.77651 | 0.83732
43602.8487 | 0.77875 | 0.78923 | 0.78111 | 0.78596 | 0.76636 | 0.77295 | 0.77813 | 0.83732
43602.8487 | 0.7786 | 0.78933 | 0.78105 | 0.7859 | 0.76634 | 0.77291 | 0.77712 | 0.83747
43602.8489 | 0.77872 | 0.78963 | 0.78123 | 0.78577 | 0.76644 | 0.77305 | 0.77727 | 0.83735
43602.8489 | 0.77797 | 0.78888 | 0.7804 | 0.78485 | 0.76567 | 0.7724 | 0.77597 | 0.83686
43602.8491 | 0.7762 | 0.78683 | 0.77851 | 0.78309 | 0.76343 | 0.77029 | 0.77414 | 0.83545
43602.8491 | 0.77692 | 0.78742 | 0.77902 | 0.78383 | 0.76401 | 0.77074 | 0.77393 | 0.83587
43602.8494 | 0.77826 | 0.78885 | 0.78034 | 0.7856 | 0.76549 | 0.77256 | 0.77619 | 0.83695
43602.8493 | 0.77673 | 0.78714 | 0.77895 | 0.78368 | 0.76394 | 0.77084 | 0.77497 | 0.83582
43602.8496 | 0.77509 | 0.78587 | 0.77769 | 0.78264 | 0.76292 | 0.76956 | 0.7733 | 0.83499
43602.8496 | 0.77548 | 0.78619 | 0.77783 | 0.78271 | 0.76309 | 0.76996 | 0.77381 | 0.83514
43602.8498 | 0.7761 | 0.78678 | 0.77853 | 0.78318 | 0.7635 | 0.77036 | 0.77518 | 0.83531
43602.8498 | 0.77647 | 0.78702 | 0.77855 | 0.78351 | 0.76385 | 0.77058 | 0.77639 | 0.83557
43602.85 | 0.77693 | 0.7877 | 0.77941 | 0.78436 | 0.76443 | 0.77123 | 0.77641 | 0.83618
43602.85 | 0.77818 | 0.78897 | 0.78046 | 0.78546 | 0.76577 | 0.77249 | 0.77678 | 0.83695
43602.8502 | 0.77603 | 0.7868 | 0.77849 | 0.78346 | 0.76389 | 0.7705 | 0.77445 | 0.83551
43602.8502 | 0.77457 | 0.78552 | 0.77676 | 0.78159 | 0.76203 | 0.76881 | 0.77366 | 0.83441
43602.8504 | 0.77458 | 0.7851 | 0.77657 | 0.7816 | 0.76187 | 0.76881 | 0.7726 | 0.83423
43602.8504 | 0.77413 | 0.78482 | 0.7765 | 0.78131 | 0.76164 | 0.76852 | 0.77217 | 0.83406
43602.8506 | 0.77392 | 0.78487 | 0.77609 | 0.78087 | 0.76169 | 0.76848 | 0.77154 | 0.83416
43602.8506 | 0.77363 | 0.78429 | 0.77566 | 0.78071 | 0.76125 | 0.76818 | 0.77174 | 0.83396
43602.8509 | 0.7734 | 0.78408 | 0.77559 | 0.78039 | 0.76089 | 0.76792 | 0.77424 | 0.83362
43602.8508 | 0.7733 | 0.78417 | 0.77574 | 0.78028 | 0.76077 | 0.76782 | 0.77104 | 0.83364
43602.8511 | 0.77343 | 0.78413 | 0.77547 | 0.78051 | 0.76084 | 0.76794 | 0.77133 | 0.8336
43602.8511 | 0.77313 | 0.78384 | 0.77535 | 0.77984 | 0.76061 | 0.76758 | 0.77177 | 0.83346
43602.8513 | 0.77315 | 0.78361 | 0.77499 | 0.77942 | 0.76029 | 0.76733 | 0.77219 | 0.83334
43602.8513 | 0.77298 | 0.78376 | 0.77507 | 0.77974 | 0.76038 | 0.76714 | 0.77097 | 0.8333
43602.8515 | 0.7728 | 0.78359 | 0.7749 | 0.77967 | 0.76035 | 0.76705 | 0.77023 | 0.8331
43602.8515 | 0.7729 | 0.78369 | 0.77546 | 0.77973 | 0.7603 | 0.76698 | 0.77134 | 0.83314
43602.8517 | 0.77242 | 0.78356 | 0.77521 | 0.77905 | 0.76007 | 0.76694 | 0.77235 | 0.83303
43602.8517 | 0.7724 | 0.78334 | 0.77491 | 0.77903 | 0.75995 | 0.76651 | 0.77058 | 0.83295
43602.8519 | 0.77218 | 0.78305 | 0.77455 | 0.77906 | 0.75939 | 0.76641 | 0.76995 | 0.8327
43602.8519 | 0.77217 | 0.78308 | 0.7744 | 0.77937 | 0.75947 | 0.76654 | 0.77269 | 0.83273
43602.8521 | 0.77214 | 0.78287 | 0.77434 | 0.77934 | 0.75961 | 0.76662 | 0.77056 | 0.83284
43602.8521 | 0.77181 | 0.78306 | 0.77446 | 0.77904 | 0.75967 | 0.76665 | 0.77007 | 0.83286
43602.8523 | 0.77204 | 0.78281 | 0.7743 | 0.7791 | 0.75946 | 0.7666 | 0.77091 | 0.83272
43602.8523 | 0.77181 | 0.78289 | 0.77448 | 0.77931 | 0.75956 | 0.76638 | 0.77028 | 0.83259
43602.8526 | 0.77174 | 0.78246 | 0.77423 | 0.7788 | 0.75935 | 0.76649 | 0.77063 | 0.83253
43602.8525 | 0.77177 | 0.78248 | 0.77382 | 0.77839 | 0.759 | 0.76606 | 0.77024 | 0.83235
43602.8528 | 0.7711 | 0.78209 | 0.77323 | 0.77813 | 0.75865 | 0.76551 | 0.76995 | 0.83192
43602.8528 | 0.77064 | 0.78166 | 0.77311 | 0.77775 | 0.75798 | 0.76516 | 0.76985 | 0.83169
43602.853 | 0.77028 | 0.78128 | 0.77225 | 0.77752 | 0.75779 | 0.7648 | 0.76902 | 0.83153
43602.853 | 0.77017 | 0.78123 | 0.77247 | 0.77715 | 0.75779 | 0.76485 | 0.76792 | 0.83137
43602.8532 | 0.77009 | 0.78104 | 0.77233 | 0.77666 | 0.75766 | 0.76466 | 0.76838 | 0.83125
43602.8532 | 0.76986 | 0.78083 | 0.77224 | 0.77667 | 0.7574 | 0.76462 | 0.76891 | 0.83121
43602.8534 | 0.76953 | 0.78056 | 0.77233 | 0.77687 | 0.75708 | 0.76435 | 0.76961 | 0.83107
43602.8534 | 0.7694 | 0.78064 | 0.77178 | 0.77682 | 0.75658 | 0.76408 | 0.76788 | 0.83075
43602.8536 | 0.76906 | 0.77997 | 0.77165 | 0.77641 | 0.75611 | 0.76365 | 0.76724 | 0.83044
43602.8536 | 0.76873 | 0.77975 | 0.77119 | 0.77593 | 0.75598 | 0.76333 | 0.76877 | 0.83026
43602.8538 | 0.76848 | 0.77964 | 0.77078 | 0.77603 | 0.75526 | 0.76284 | 0.76893 | 0.82999
43602.8538 | 0.7679 | 0.77897 | 0.77033 | 0.77545 | 0.75484 | 0.76236 | 0.76665 | 0.82971
43602.8541 | 0.76784 | 0.77873 | 0.76979 | 0.77451 | 0.75459 | 0.7619 | 0.76584 | 0.82948
43602.8541 | 0.76722 | 0.77827 | 0.76952 | 0.77437 | 0.75432 | 0.76144 | 0.7654 | 0.82929
43602.8543 | 0.76703 | 0.77818 | 0.76931 | 0.77412 | 0.75401 | 0.76128 | 0.76698 | 0.829
43602.8543 | 0.76676 | 0.77807 | 0.76897 | 0.77404 | 0.75356 | 0.76095 | 0.76579 | 0.82878
43602.8545 | 0.7661 | 0.77741 | 0.76855 | 0.77306 | 0.75323 | 0.76025 | 0.76406 | 0.82855
43602.8545 | 0.76592 | 0.7772 | 0.76839 | 0.77287 | 0.75303 | 0.76013 | 0.76448 | 0.82839
43602.8547 | 0.76504 | 0.77648 | 0.76763 | 0.77221 | 0.7521 | 0.75956 | 0.76386 | 0.82772
43602.8547 | 0.7649 | 0.77656 | 0.76767 | 0.77213 | 0.75225 | 0.75946 | 0.76459 | 0.82776
43602.8549 | 0.76418 | 0.77581 | 0.76683 | 0.77146 | 0.75156 | 0.75877 | 0.76491 | 0.82739
43602.8549 | 0.76378 | 0.77535 | 0.76636 | 0.77099 | 0.75096 | 0.75827 | 0.76449 | 0.82694
43602.8552 | 0.76339 | 0.77492 | 0.76594 | 0.7708 | 0.75068 | 0.75796 | 0.76362 | 0.82674
43602.8551 | 0.76296 | 0.77445 | 0.76561 | 0.77006 | 0.7499 | 0.7571 | 0.76241 | 0.8263
43602.8554 | 0.76264 | 0.77415 | 0.76547 | 0.76964 | 0.74974 | 0.75701 | 0.76165 | 0.82618
43602.8554 | 0.76258 | 0.77388 | 0.76497 | 0.7693 | 0.74927 | 0.75661 | 0.76195 | 0.82591
43602.8556 | 0.762 | 0.77332 | 0.76447 | 0.7689 | 0.74883 | 0.75615 | 0.76063 | 0.82539
43602.8556 | 0.76145 | 0.77288 | 0.7638 | 0.76842 | 0.74817 | 0.75553 | 0.76168 | 0.82519
43602.8558 | 0.76093 | 0.7722 | 0.76356 | 0.76807 | 0.74765 | 0.75506 | 0.75867 | 0.82478
43602.8558 | 0.76042 | 0.77187 | 0.76337 | 0.76758 | 0.74716 | 0.75481 | 0.75924 | 0.82458
43602.856 | 0.75992 | 0.77137 | 0.76259 | 0.76717 | 0.74657 | 0.75415 | 0.75967 | 0.82421
43602.856 | 0.75905 | 0.77049 | 0.76165 | 0.7663 | 0.74588 | 0.75345 | 0.75735 | 0.82362
43602.8562 | 0.75826 | 0.76955 | 0.76092 | 0.76513 | 0.74518 | 0.7526 | 0.75855 | 0.82312
43602.8562 | 0.75815 | 0.76941 | 0.76083 | 0.76498 | 0.74432 | 0.75187 | 0.7573 | 0.82269
43602.8565 | 0.75757 | 0.76901 | 0.76027 | 0.76458 | 0.74395 | 0.75179 | 0.75669 | 0.82247
43602.8564 | 0.75719 | 0.76855 | 0.75989 | 0.76393 | 0.74356 | 0.75126 | 0.75772 | 0.8223
43602.8567 | 0.75628 | 0.76797 | 0.75912 | 0.76353 | 0.74275 | 0.75042 | 0.75467 | 0.82164
43602.8567 | 0.75632 | 0.76783 | 0.75898 | 0.76341 | 0.74276 | 0.75021 | 0.75469 | 0.82161
43602.8569 | 0.75559 | 0.76724 | 0.75855 | 0.76268 | 0.74211 | 0.74977 | 0.75443 | 0.82126
43602.8569 | 0.7552 | 0.76674 | 0.75826 | 0.76231 | 0.74155 | 0.74937 | 0.75326 | 0.82099
43602.8571 | 0.75474 | 0.76624 | 0.75748 | 0.76188 | 0.74128 | 0.74902 | 0.75415 | 0.82068
43602.8571 | 0.7542 | 0.76594 | 0.75717 | 0.7615 | 0.74106 | 0.74847 | 0.75231 | 0.82041
43602.8573 | 0.75371 | 0.76562 | 0.75662 | 0.76124 | 0.7404 | 0.74809 | 0.75296 | 0.82007
43602.8573 | 0.75355 | 0.76546 | 0.75675 | 0.7613 | 0.74041 | 0.74814 | 0.75423 | 0.8201
43602.8575 | 0.75279 | 0.76475 | 0.75586 | 0.76014 | 0.73949 | 0.74727 | 0.75237 | 0.81962
43602.8575 | 0.75294 | 0.76471 | 0.75565 | 0.76009 | 0.73947 | 0.74708 | 0.75153 | 0.8194
43602.8578 | 0.75247 | 0.76423 | 0.75534 | 0.75998 | 0.73896 | 0.74676 | 0.75399 | 0.81912
43602.8577 | 0.75215 | 0.76407 | 0.75507 | 0.75907 | 0.73862 | 0.74624 | 0.75062 | 0.81883
43602.858 | 0.75186 | 0.76376 | 0.75487 | 0.75916 | 0.73839 | 0.74633 | 0.75039 | 0.81876
43602.858 | 0.75113 | 0.76325 | 0.75396 | 0.75873 | 0.73814 | 0.74577 | 0.74981 | 0.81849
43602.8582 | 0.75107 | 0.76291 | 0.75372 | 0.75841 | 0.73764 | 0.74538 | 0.75056 | 0.81814
43602.8582 | 0.75102 | 0.76272 | 0.75372 | 0.75833 | 0.73749 | 0.74504 | 0.74985 | 0.81797
43602.8584 | 0.75025 | 0.76218 | 0.75361 | 0.75789 | 0.73685 | 0.74445 | 0.74909 | 0.81769
43602.8584 | 0.75027 | 0.76214 | 0.75345 | 0.75782 | 0.73674 | 0.7444 | 0.7495 | 0.81769
43602.8586 | 0.74976 | 0.76177 | 0.75281 | 0.75718 | 0.73631 | 0.74406 | 0.749 | 0.81734
43602.8586 | 0.74956 | 0.76145 | 0.75261 | 0.75672 | 0.73577 | 0.74368 | 0.74874 | 0.81699
43602.8589 | 0.74909 | 0.76117 | 0.75226 | 0.75664 | 0.73555 | 0.74328 | 0.74778 | 0.81689
43602.8588 | 0.74905 | 0.76096 | 0.7523 | 0.75659 | 0.73538 | 0.74334 | 0.74738 | 0.8168
43602.8591 | 0.74878 | 0.76043 | 0.75174 | 0.75598 | 0.73493 | 0.74294 | 0.74713 | 0.8164
43602.8591 | 0.7486 | 0.76034 | 0.75157 | 0.75596 | 0.73453 | 0.74257 | 0.74697 | 0.81633
43602.8593 | 0.74838 | 0.75987 | 0.75091 | 0.75544 | 0.73424 | 0.74228 | 0.74676 | 0.81598
43602.8593 | 0.74791 | 0.75983 | 0.75106 | 0.75528 | 0.73411 | 0.74207 | 0.74935 | 0.81594
43602.8595 | 0.74746 | 0.75933 | 0.75031 | 0.75461 | 0.73362 | 0.74165 | 0.74788 | 0.81556
43602.8595 | 0.74732 | 0.75905 | 0.75012 | 0.75445 | 0.73348 | 0.7414 | 0.74523 | 0.81541
43602.8597 | 0.74683 | 0.75849 | 0.74959 | 0.75387 | 0.73312 | 0.74089 | 0.74642 | 0.81504
43602.8597 | 0.74666 | 0.75848 | 0.74963 | 0.75377 | 0.73284 | 0.74043 | 0.7448 | 0.81491
43602.8599 | 0.7464 | 0.75828 | 0.74953 | 0.75366 | 0.73227 | 0.74022 | 0.74398 | 0.81459
43602.8599 | 0.74619 | 0.75793 | 0.74914 | 0.75343 | 0.73205 | 0.74019 | 0.74522 | 0.81442
43602.8602 | 0.74551 | 0.75755 | 0.74877 | 0.75279 | 0.73172 | 0.73949 | 0.74363 | 0.81432
43602.8602 | 0.74547 | 0.75741 | 0.74856 | 0.75256 | 0.73128 | 0.7394 | 0.74388 | 0.81405
43602.8604 | 0.74503 | 0.757 | 0.74837 | 0.75245 | 0.73094 | 0.73906 | 0.74271 | 0.8137
43602.8604 | 0.74492 | 0.75677 | 0.74801 | 0.75221 | 0.7307 | 0.7387 | 0.74312 | 0.81354
43602.8606 | 0.7444 | 0.75646 | 0.74739 | 0.75204 | 0.7304 | 0.73848 | 0.74425 | 0.81339
43602.8606 | 0.744 | 0.75622 | 0.7473 | 0.75161 | 0.73005 | 0.738 | 0.74218 | 0.81307
43602.8608 | 0.74388 | 0.75578 | 0.74673 | 0.75106 | 0.72967 | 0.73789 | 0.74272 | 0.81289
43602.8608 | 0.74357 | 0.75557 | 0.74645 | 0.7508 | 0.72936 | 0.73742 | 0.74211 | 0.81278
43602.861 | 0.74315 | 0.75523 | 0.7464 | 0.75062 | 0.72917 | 0.73722 | 0.74217 | 0.81255
43602.861 | 0.74301 | 0.75493 | 0.74602 | 0.75039 | 0.72878 | 0.73683 | 0.74294 | 0.8124
43602.8613 | 0.74254 | 0.75478 | 0.74561 | 0.75011 | 0.72858 | 0.73669 | 0.74099 | 0.8121
43602.8612 | 0.74234 | 0.7547 | 0.74547 | 0.74977 | 0.72825 | 0.73639 | 0.74082 | 0.81199
43602.8615 | 0.74207 | 0.75439 | 0.74513 | 0.74934 | 0.72794 | 0.73611 | 0.74009 | 0.81179
43602.8615 | 0.74188 | 0.75415 | 0.74502 | 0.74907 | 0.72789 | 0.73616 | 0.74022 | 0.81171
43602.8617 | 0.74155 | 0.75383 | 0.74489 | 0.74888 | 0.7277 | 0.73583 | 0.74054 | 0.81144
43602.8617 | 0.74153 | 0.75379 | 0.74485 | 0.74871 | 0.72765 | 0.73563 | 0.73984 | 0.81135
43602.8619 | 0.74116 | 0.75326 | 0.74458 | 0.74824 | 0.72723 | 0.7355 | 0.73969 | 0.81122
43602.8619 | 0.74111 | 0.75336 | 0.74418 | 0.74829 | 0.72698 | 0.73532 | 0.74023 | 0.81107
43602.8621 | 0.74064 | 0.75276 | 0.74349 | 0.74773 | 0.72685 | 0.73494 | 0.74233 | 0.8107
43602.8621 | 0.7406 | 0.75245 | 0.74365 | 0.74741 | 0.72659 | 0.73459 | 0.73942 | 0.8107
43602.8623 | 0.74031 | 0.75251 | 0.74329 | 0.74761 | 0.72601 | 0.73417 | 0.74062 | 0.81038
43602.8623 | 0.74011 | 0.75226 | 0.74305 | 0.74752 | 0.72571 | 0.73408 | 0.74034 | 0.81018
43602.8626 | 0.73989 | 0.75188 | 0.74285 | 0.74707 | 0.7255 | 0.73379 | 0.7382 | 0.80986
43602.8625 | 0.73959 | 0.75185 | 0.74249 | 0.74692 | 0.72512 | 0.73344 | 0.73893 | 0.80979
43602.8628 | 0.73927 | 0.75167 | 0.74239 | 0.74649 | 0.72485 | 0.73324 | 0.73826 | 0.80955
43602.8628 | 0.73909 | 0.75157 | 0.74228 | 0.74639 | 0.72499 | 0.7332 | 0.7376 | 0.80962
43602.863 | 0.73896 | 0.75125 | 0.74194 | 0.74615 | 0.7245 | 0.73277 | 0.73729 | 0.80934
43602.863 | 0.73864 | 0.75095 | 0.74181 | 0.746 | 0.72427 | 0.73269 | 0.73811 | 0.80931
43602.8632 | 0.73827 | 0.75047 | 0.74133 | 0.74559 | 0.72412 | 0.73216 | 0.73648 | 0.80922
43602.8632 | 0.73804 | 0.75042 | 0.7412 | 0.74544 | 0.72385 | 0.73217 | 0.73686 | 0.80895
43602.8634 | 0.7378 | 0.74987 | 0.74076 | 0.745 | 0.72361 | 0.73209 | 0.73684 | 0.80878
43602.8634 | 0.73745 | 0.75 | 0.74072 | 0.7449 | 0.72318 | 0.73166 | 0.73903 | 0.80843
43602.8636 | 0.73706 | 0.74956 | 0.74038 | 0.74462 | 0.72297 | 0.7312 | 0.73553 | 0.80826
43602.8636 | 0.73696 | 0.74939 | 0.74028 | 0.74451 | 0.72246 | 0.73105 | 0.73777 | 0.80814
43602.8639 | 0.73658 | 0.74923 | 0.74011 | 0.74382 | 0.72226 | 0.73085 | 0.73499 | 0.80771
43602.8639 | 0.73614 | 0.7484 | 0.73954 | 0.74314 | 0.72167 | 0.73047 | 0.73524 | 0.8075
43602.8641 | 0.73608 | 0.74842 | 0.73954 | 0.74312 | 0.72144 | 0.73035 | 0.7356 | 0.80736
43602.8641 | 0.73606 | 0.74823 | 0.73912 | 0.74289 | 0.72127 | 0.72988 | 0.73435 | 0.80727
43602.8643 | 0.73542 | 0.74786 | 0.73876 | 0.74226 | 0.72116 | 0.72958 | 0.73481 | 0.80702
43602.8643 | 0.73558 | 0.74779 | 0.73876 | 0.74269 | 0.72096 | 0.72969 | 0.7345 | 0.807
43602.8645 | 0.73504 | 0.74748 | 0.73811 | 0.74221 | 0.72078 | 0.72898 | 0.73446 | 0.80679
43602.8645 | 0.73487 | 0.74733 | 0.73809 | 0.74204 | 0.72026 | 0.72882 | 0.73348 | 0.80661
43602.8647 | 0.73472 | 0.74698 | 0.73788 | 0.74174 | 0.72023 | 0.72862 | 0.73501 | 0.80636
43602.8647 | 0.73424 | 0.74671 | 0.73759 | 0.74172 | 0.72004 | 0.7284 | 0.73164 | 0.80629
43602.865 | 0.73392 | 0.74651 | 0.73726 | 0.74082 | 0.71946 | 0.72786 | 0.73302 | 0.80594
43602.8649 | 0.73393 | 0.74613 | 0.73685 | 0.74084 | 0.71932 | 0.72771 | 0.73266 | 0.80581
43602.8652 | 0.7335 | 0.74621 | 0.73671 | 0.74064 | 0.71883 | 0.72749 | 0.7323 | 0.80561
43602.8652 | 0.73326 | 0.74587 | 0.73653 | 0.74042 | 0.71865 | 0.72728 | 0.73174 | 0.8054
43602.8654 | 0.73284 | 0.7453 | 0.73629 | 0.73996 | 0.71826 | 0.72675 | 0.73294 | 0.80518
43602.8654 | 0.73262 | 0.74514 | 0.73617 | 0.73961 | 0.71808 | 0.7265 | 0.73214 | 0.80503
43602.8656 | 0.73236 | 0.74491 | 0.73569 | 0.73961 | 0.71743 | 0.72598 | 0.73074 | 0.80484
43602.8656 | 0.73208 | 0.74465 | 0.73543 | 0.73952 | 0.71752 | 0.72607 | 0.73102 | 0.8047
43602.8658 | 0.73175 | 0.74449 | 0.73501 | 0.73904 | 0.71718 | 0.72567 | 0.73035 | 0.80457
43602.8658 | 0.7316 | 0.74428 | 0.73471 | 0.73896 | 0.71701 | 0.72598 | 0.73058 | 0.80432
43602.866 | 0.73118 | 0.7437 | 0.73429 | 0.7384 | 0.71675 | 0.7254 | 0.73021 | 0.80414
43602.866 | 0.73111 | 0.74364 | 0.73394 | 0.73844 | 0.71666 | 0.72522 | 0.73118 | 0.80396
43602.8663 | 0.73071 | 0.74322 | 0.73391 | 0.73792 | 0.7162 | 0.72463 | 0.7298 | 0.80363
43602.8663 | 0.73045 | 0.74313 | 0.73369 | 0.73772 | 0.71591 | 0.72437 | 0.73086 | 0.80362
43602.8665 | 0.73018 | 0.74289 | 0.73364 | 0.73738 | 0.71574 | 0.72428 | 0.72876 | 0.80337
43602.8665 | 0.72997 | 0.74282 | 0.73324 | 0.73711 | 0.71534 | 0.72386 | 0.72964 | 0.80329
43602.8667 | 0.72978 | 0.74241 | 0.73284 | 0.73688 | 0.71513 | 0.72361 | 0.72821 | 0.80292
43602.8667 | 0.7294 | 0.74212 | 0.73289 | 0.73677 | 0.71474 | 0.7234 | 0.72837 | 0.80287
43602.8669 | 0.72925 | 0.74172 | 0.73258 | 0.73648 | 0.71445 | 0.72313 | 0.72815 | 0.80272
43602.8669 | 0.72895 | 0.74171 | 0.73292 | 0.73638 | 0.71457 | 0.72303 | 0.72839 | 0.80257
43602.8671 | 0.7289 | 0.74147 | 0.73206 | 0.73578 | 0.71393 | 0.72251 | 0.72734 | 0.80229
43602.8671 | 0.72887 | 0.74152 | 0.73208 | 0.73543 | 0.7137 | 0.72223 | 0.7272 | 0.80229
43602.8674 | 0.72812 | 0.74064 | 0.7314 | 0.73501 | 0.71318 | 0.72173 | 0.72893 | 0.80176
43602.8674 | 0.7282 | 0.74064 | 0.73144 | 0.7353 | 0.71341 | 0.72216 | 0.72839 | 0.80197
43602.8676 | 0.72841 | 0.74061 | 0.73152 | 0.73519 | 0.71314 | 0.72178 | 0.72677 | 0.80164
43602.8676 | 0.72771 | 0.74018 | 0.73105 | 0.73462 | 0.71257 | 0.7212 | 0.72588 | 0.80144
43602.8678 | 0.72763 | 0.74028 | 0.73091 | 0.7347 | 0.71267 | 0.72127 | 0.72592 | 0.80147
43602.8678 | 0.72754 | 0.74011 | 0.73057 | 0.73426 | 0.71273 | 0.72129 | 0.72604 | 0.80123
43602.868 | 0.72716 | 0.73973 | 0.73051 | 0.73444 | 0.71257 | 0.72108 | 0.72549 | 0.80117
43602.868 | 0.72713 | 0.73976 | 0.73045 | 0.73438 | 0.71235 | 0.72078 | 0.72529 | 0.80104
43602.8682 | 0.72656 | 0.73965 | 0.73011 | 0.7338 | 0.71192 | 0.72076 | 0.72878 | 0.80079
43602.8682 | 0.72657 | 0.73932 | 0.73011 | 0.73365 | 0.7116 | 0.72051 | 0.72789 | 0.8007
43602.8685 | 0.72598 | 0.73893 | 0.72998 | 0.73343 | 0.71163 | 0.72049 | 0.72486 | 0.8005
43602.8684 | 0.72578 | 0.73873 | 0.72956 | 0.73318 | 0.71126 | 0.71995 | 0.72519 | 0.80047
43602.8687 | 0.72566 | 0.73851 | 0.72951 | 0.73292 | 0.71107 | 0.71963 | 0.7257 | 0.80016
43602.8687 | 0.72547 | 0.73846 | 0.72913 | 0.73279 | 0.71081 | 0.71955 | 0.72356 | 0.79998
43602.8689 | 0.72511 | 0.73798 | 0.72848 | 0.7327 | 0.71052 | 0.71892 | 0.72367 | 0.79979
43602.8689 | 0.72483 | 0.73791 | 0.72857 | 0.73241 | 0.70998 | 0.71879 | 0.72315 | 0.79967
43602.8691 | 0.72437 | 0.73765 | 0.72812 | 0.73202 | 0.70982 | 0.71846 | 0.72344 | 0.79939
43602.8691 | 0.72447 | 0.73735 | 0.72811 | 0.73192 | 0.70989 | 0.71878 | 0.72551 | 0.7993
43602.8693 | 0.72405 | 0.73713 | 0.72759 | 0.7315 | 0.70947 | 0.71842 | 0.72277 | 0.7991
43602.8693 | 0.72398 | 0.73732 | 0.7275 | 0.7312 | 0.70961 | 0.71832 | 0.72269 | 0.79902
43602.8696 | 0.72386 | 0.73672 | 0.72729 | 0.73085 | 0.70904 | 0.71775 | 0.72133 | 0.79881
43602.8696 | 0.72371 | 0.73649 | 0.72739 | 0.7309 | 0.70912 | 0.7178 | 0.72264 | 0.79884
43602.8698 | 0.72364 | 0.73639 | 0.72697 | 0.73076 | 0.70883 | 0.71759 | 0.72237 | 0.79861
43602.8698 | 0.72342 | 0.73619 | 0.72673 | 0.73041 | 0.70857 | 0.7175 | 0.72229 | 0.79851
43602.87 | 0.72299 | 0.73603 | 0.7269 | 0.73024 | 0.7082 | 0.71725 | 0.72193 | 0.79825
43602.87 | 0.72309 | 0.73574 | 0.72667 | 0.72985 | 0.70817 | 0.71704 | 0.7248 | 0.7982
43602.8702 | 0.72295 | 0.73561 | 0.72643 | 0.73039 | 0.70788 | 0.71661 | 0.72155 | 0.79797
43602.8702 | 0.72257 | 0.73542 | 0.72618 | 0.73018 | 0.70776 | 0.71654 | 0.72164 | 0.79775
43602.8704 | 0.72207 | 0.73492 | 0.72584 | 0.72978 | 0.70755 | 0.71638 | 0.72374 | 0.79768
43602.8704 | 0.72215 | 0.73495 | 0.72566 | 0.7297 | 0.70762 | 0.71642 | 0.72082 | 0.79752
43602.8707 | 0.72198 | 0.73464 | 0.72532 | 0.72893 | 0.70709 | 0.71581 | 0.72088 | 0.7974
43602.8707 | 0.722 | 0.73454 | 0.72515 | 0.72957 | 0.70672 | 0.71568 | 0.72211 | 0.79711
43602.8709 | 0.72149 | 0.73422 | 0.72476 | 0.72886 | 0.70641 | 0.71524 | 0.7205 | 0.79703
43602.8709 | 0.72118 | 0.73419 | 0.72481 | 0.72849 | 0.70623 | 0.71509 | 0.72037 | 0.79684
43602.8711 | 0.721 | 0.73399 | 0.72461 | 0.7284 | 0.706 | 0.71489 | 0.71957 | 0.79683
43602.8711 | 0.72096 | 0.7338 | 0.72453 | 0.72816 | 0.70596 | 0.71466 | 0.71979 | 0.79653
43602.8713 | 0.72084 | 0.73357 | 0.72423 | 0.72838 | 0.70536 | 0.71445 | 0.72001 | 0.79644
43602.8713 | 0.72071 | 0.73354 | 0.72412 | 0.72815 | 0.70542 | 0.71463 | 0.72001 | 0.79629
43602.8716 | 0.72063 | 0.73344 | 0.72398 | 0.72759 | 0.70535 | 0.71416 | 0.71915 | 0.79616
43602.8716 | 0.72031 | 0.73324 | 0.72394 | 0.72784 | 0.70528 | 0.7141 | 0.71915 | 0.79612
43602.8718 | 0.72014 | 0.73294 | 0.72369 | 0.72745 | 0.70475 | 0.71382 | 0.71967 | 0.79585
43602.8718 | 0.72002 | 0.73293 | 0.72361 | 0.72723 | 0.70462 | 0.71363 | 0.71847 | 0.7958
43602.872 | 0.71983 | 0.73256 | 0.72341 | 0.72726 | 0.70455 | 0.71353 | 0.72016 | 0.79574
43602.872 | 0.71974 | 0.73235 | 0.72339 | 0.72683 | 0.70433 | 0.71355 | 0.71833 | 0.79555
43602.8722 | 0.71958 | 0.73216 | 0.72318 | 0.72675 | 0.70434 | 0.71333 | 0.71866 | 0.7956
43602.8722 | 0.71919 | 0.73193 | 0.72321 | 0.72658 | 0.70427 | 0.713 | 0.71761 | 0.79533
43602.8726 | 0.71851 | 0.73091 | 0.72196 | 0.72556 | 0.70295 | 0.71185 | 0.71884 | 0.79446
43602.8726 | 0.7185 | 0.73119 | 0.72196 | 0.72563 | 0.70293 | 0.71221 | 0.71686 | 0.79456
43602.8729 | 0.71856 | 0.73123 | 0.722 | 0.72567 | 0.70282 | 0.71219 | 0.71916 | 0.79447
43602.8728 | 0.71827 | 0.73101 | 0.7219 | 0.72528 | 0.70261 | 0.71183 | 0.71632 | 0.79445
43602.8731 | 0.71827 | 0.73085 | 0.72169 | 0.72542 | 0.70244 | 0.71172 | 0.71902 | 0.79431
43602.8731 | 0.71793 | 0.7305 | 0.7217 | 0.72509 | 0.7023 | 0.71158 | 0.7167 | 0.79405
43602.8733 | 0.7178 | 0.73043 | 0.72141 | 0.72484 | 0.70238 | 0.71133 | 0.71952 | 0.79402
43602.8733 | 0.71786 | 0.73025 | 0.72103 | 0.72446 | 0.70192 | 0.71139 | 0.71603 | 0.79401
43602.8735 | 0.71712 | 0.73002 | 0.7209 | 0.72438 | 0.70189 | 0.71098 | 0.71714 | 0.7938
43602.8735 | 0.71696 | 0.73004 | 0.721 | 0.72448 | 0.70187 | 0.71101 | 0.71643 | 0.79372
43602.8737 | 0.71701 | 0.73 | 0.72033 | 0.7242 | 0.70149 | 0.71074 | 0.71643 | 0.7936
43602.8737 | 0.71685 | 0.72983 | 0.72033 | 0.72439 | 0.70142 | 0.71058 | 0.71518 | 0.7937
43602.874 | 0.71682 | 0.72954 | 0.72032 | 0.72399 | 0.70141 | 0.71043 | 0.7166 | 0.79367
43602.8739 | 0.71685 | 0.7295 | 0.72054 | 0.7241 | 0.70145 | 0.71035 | 0.71559 | 0.79347
43602.8742 | 0.71654 | 0.72934 | 0.7205 | 0.72406 | 0.70107 | 0.71039 | 0.71535 | 0.79334
43602.8742 | 0.71662 | 0.72949 | 0.72021 | 0.72353 | 0.70102 | 0.71013 | 0.71574 | 0.79326
43602.8744 | 0.71599 | 0.72923 | 0.71964 | 0.72322 | 0.70091 | 0.70999 | 0.71743 | 0.79314
43602.8744 | 0.71618 | 0.72927 | 0.71962 | 0.72335 | 0.70089 | 0.70978 | 0.71497 | 0.79301
43602.8746 | 0.71601 | 0.72889 | 0.71935 | 0.72307 | 0.70053 | 0.70979 | 0.71372 | 0.79283
43602.8746 | 0.71594 | 0.72868 | 0.71936 | 0.72295 | 0.7004 | 0.70949 | 0.71426 | 0.79277
43602.8748 | 0.71578 | 0.72874 | 0.7194 | 0.72281 | 0.70042 | 0.70916 | 0.71499 | 0.79262
43602.8748 | 0.71575 | 0.72847 | 0.7193 | 0.72282 | 0.7003 | 0.70918 | 0.71443 | 0.7926
43602.875 | 0.71528 | 0.7283 | 0.71906 | 0.72284 | 0.70013 | 0.70904 | 0.71643 | 0.79244
43602.875 | 0.71559 | 0.72811 | 0.71915 | 0.72261 | 0.69971 | 0.70872 | 0.71779 | 0.79241
43602.8753 | 0.71522 | 0.72802 | 0.71888 | 0.72199 | 0.69963 | 0.7087 | 0.71382 | 0.79224
43602.8752 | 0.71511 | 0.72792 | 0.71881 | 0.7221 | 0.69962 | 0.70857 | 0.71341 | 0.79213
43602.8755 | 0.71524 | 0.72771 | 0.71865 | 0.72184 | 0.69929 | 0.70829 | 0.7136 | 0.79199
43602.8755 | 0.71492 | 0.7274 | 0.71832 | 0.72169 | 0.6992 | 0.70831 | 0.71593 | 0.79195
43602.8757 | 0.71473 | 0.72728 | 0.71844 | 0.72166 | 0.69898 | 0.70789 | 0.71303 | 0.7919
43602.8757 | 0.71465 | 0.72731 | 0.71804 | 0.72147 | 0.69909 | 0.70807 | 0.71332 | 0.79179
43602.8759 | 0.71452 | 0.72718 | 0.71804 | 0.72108 | 0.69885 | 0.70779 | 0.71212 | 0.79159
43602.8759 | 0.71447 | 0.72687 | 0.71762 | 0.72126 | 0.69858 | 0.70767 | 0.7123 | 0.79146
43602.8761 | 0.71427 | 0.72679 | 0.71769 | 0.72102 | 0.69844 | 0.70748 | 0.71244 | 0.79139
43602.8761 | 0.71421 | 0.72692 | 0.71765 | 0.72076 | 0.69819 | 0.70767 | 0.71262 | 0.79128
43602.8763 | 0.714 | 0.72673 | 0.71773 | 0.7205 | 0.69844 | 0.70744 | 0.71251 | 0.79113
43602.8763 | 0.71388 | 0.7266 | 0.71739 | 0.72077 | 0.69828 | 0.70739 | 0.71245 | 0.79123
43602.8766 | 0.71324 | 0.726 | 0.71654 | 0.71981 | 0.69739 | 0.70669 | 0.71418 | 0.79063
43602.8765 | 0.71336 | 0.72628 | 0.71685 | 0.71995 | 0.69792 | 0.70705 | 0.71167 | 0.7909
43602.8768 | 0.71327 | 0.726 | 0.71634 | 0.72001 | 0.69743 | 0.70691 | 0.71207 | 0.7907
43602.8768 | 0.71328 | 0.72589 | 0.71648 | 0.72005 | 0.69752 | 0.7072 | 0.71252 | 0.79079
43602.877 | 0.71293 | 0.7257 | 0.71642 | 0.71993 | 0.69761 | 0.70678 | 0.71156 | 0.7906
43602.877 | 0.71239 | 0.72522 | 0.71599 | 0.71948 | 0.69722 | 0.7064 | 0.71445 | 0.79037
43602.8772 | 0.71331 | 0.72593 | 0.71675 | 0.72017 | 0.69767 | 0.70671 | 0.7129 | 0.7907
43602.8772 | 0.71342 | 0.72599 | 0.71681 | 0.72004 | 0.69775 | 0.70693 | 0.71198 | 0.79062
43602.8774 | 0.71322 | 0.72568 | 0.71638 | 0.71998 | 0.69753 | 0.70644 | 0.7147 | 0.79055
43602.8774 | 0.71316 | 0.72585 | 0.71645 | 0.71971 | 0.69719 | 0.70654 | 0.71123 | 0.79053
43602.8777 | 0.71337 | 0.72573 | 0.7165 | 0.71991 | 0.69754 | 0.7065 | 0.71423 | 0.79055
43602.8776 | 0.71351 | 0.7259 | 0.71707 | 0.72031 | 0.69774 | 0.70702 | 0.71359 | 0.79073
43602.8779 | 0.71359 | 0.72603 | 0.71695 | 0.72037 | 0.69789 | 0.70694 | 0.71201 | 0.79071
43602.8779 | 0.71379 | 0.72615 | 0.71715 | 0.7207 | 0.69785 | 0.70722 | 0.71267 | 0.79078
43602.8781 | 0.71413 | 0.72644 | 0.7172 | 0.72051 | 0.69846 | 0.70728 | 0.71149 | 0.79097
43602.8781 | 0.71425 | 0.72683 | 0.7177 | 0.72121 | 0.69862 | 0.70772 | 0.71271 | 0.79113
43602.8783 | 0.71446 | 0.72682 | 0.71793 | 0.72094 | 0.69905 | 0.70808 | 0.713 | 0.79134
43602.8783 | 0.71493 | 0.72754 | 0.7181 | 0.72149 | 0.69901 | 0.70817 | 0.71252 | 0.79147
43602.8785 | 0.71538 | 0.72768 | 0.71872 | 0.72154 | 0.69936 | 0.70861 | 0.71445 | 0.79171
43602.8785 | 0.71594 | 0.72856 | 0.71962 | 0.7223 | 0.70007 | 0.70904 | 0.71396 | 0.79202
43602.8788 | 0.71639 | 0.72861 | 0.71972 | 0.72292 | 0.70055 | 0.70956 | 0.715 | 0.79241
43602.8788 | 0.71608 | 0.72821 | 0.7196 | 0.72217 | 0.70002 | 0.70901 | 0.71378 | 0.7921
43602.879 | 0.71708 | 0.72923 | 0.72045 | 0.72364 | 0.70091 | 0.70991 | 0.71527 | 0.79261
43602.879 | 0.7175 | 0.72983 | 0.72099 | 0.7242 | 0.70263 | 0.71158 | 0.71703 | 0.7934
43602.8792 | 0.71798 | 0.73009 | 0.72184 | 0.72471 | 0.70274 | 0.71182 | 0.71652 | 0.79378
43602.8792 | 0.71865 | 0.73059 | 0.72251 | 0.72514 | 0.70306 | 0.71207 | 0.71594 | 0.79379
43602.8794 | 0.71953 | 0.73144 | 0.72284 | 0.7257 | 0.70343 | 0.71246 | 0.71759 | 0.79412
43602.8794 | 0.7204 | 0.7325 | 0.72406 | 0.72714 | 0.70467 | 0.71363 | 0.7189 | 0.79485
43602.8796 | 0.72161 | 0.7336 | 0.72503 | 0.72824 | 0.70586 | 0.71472 | 0.72263 | 0.79561
43602.8796 | 0.72274 | 0.73456 | 0.72613 | 0.72949 | 0.7073 | 0.71619 | 0.72066 | 0.79648
43602.8799 | 0.72668 | 0.73838 | 0.72999 | 0.73321 | 0.71127 | 0.71986 | 0.72533 | 0.79885
43602.8798 | 0.72815 | 0.73982 | 0.73181 | 0.73499 | 0.71357 | 0.72188 | 0.7264 | 0.80031
43602.8801 | 0.72904 | 0.7406 | 0.73239 | 0.73557 | 0.71473 | 0.72292 | 0.72857 | 0.80093
43602.8801 | 0.72701 | 0.73865 | 0.72996 | 0.73366 | 0.7128 | 0.7212 | 0.72596 | 0.7998
43602.8803 | 0.7259 | 0.73766 | 0.72957 | 0.73269 | 0.71091 | 0.71955 | 0.72272 | 0.79856
43602.8803 | 0.72687 | 0.73857 | 0.73028 | 0.73351 | 0.7118 | 0.7202 | 0.72453 | 0.79916
43602.8805 | 0.72733 | 0.73881 | 0.73066 | 0.73386 | 0.7127 | 0.72092 | 0.7255 | 0.79965
43602.8805 | 0.72669 | 0.73821 | 0.72976 | 0.73322 | 0.7119 | 0.71996 | 0.72374 | 0.79901
43602.8807 | 0.72677 | 0.7385 | 0.73043 | 0.73382 | 0.71163 | 0.71989 | 0.72554 | 0.79917
43602.8807 | 0.72767 | 0.73944 | 0.73128 | 0.73449 | 0.7128 | 0.72114 | 0.72746 | 0.79982
43602.881 | 0.72804 | 0.73982 | 0.7316 | 0.73445 | 0.713 | 0.72152 | 0.7261 | 0.79987
43602.881 | 0.72833 | 0.74013 | 0.73201 | 0.73498 | 0.71366 | 0.72221 | 0.72728 | 0.80026
43602.8812 | 0.72942 | 0.74093 | 0.73282 | 0.73623 | 0.71467 | 0.72312 | 0.72777 | 0.80102
43602.8812 | 0.73006 | 0.74175 | 0.73387 | 0.73682 | 0.7155 | 0.72397 | 0.72873 | 0.80146
43602.8814 | 0.73149 | 0.74303 | 0.73525 | 0.7382 | 0.71693 | 0.72509 | 0.72956 | 0.80232
43602.8814 | 0.73254 | 0.7441 | 0.73635 | 0.73915 | 0.71815 | 0.72634 | 0.73068 | 0.80321
43602.8817 | 0.73299 | 0.74429 | 0.73686 | 0.73984 | 0.71866 | 0.72666 | 0.73099 | 0.80329
43602.8817 | 0.73432 | 0.7456 | 0.73782 | 0.74077 | 0.71975 | 0.72782 | 0.7323 | 0.80403
43602.8819 | 0.73603 | 0.74743 | 0.74002 | 0.74302 | 0.72165 | 0.72963 | 0.73383 | 0.80534
43602.8819 | 0.73654 | 0.7478 | 0.74012 | 0.74365 | 0.72237 | 0.73054 | 0.73507 | 0.80589
43602.8821 | 0.73861 | 0.74963 | 0.74238 | 0.74532 | 0.7243 | 0.7323 | 0.73671 | 0.80695
43602.8821 | 0.73842 | 0.74957 | 0.74219 | 0.74545 | 0.72477 | 0.73253 | 0.7393 | 0.80715
43602.8824 | 0.74125 | 0.75213 | 0.74483 | 0.74763 | 0.72673 | 0.73456 | 0.74006 | 0.80857
43602.8823 | 0.74134 | 0.75246 | 0.74483 | 0.74812 | 0.72729 | 0.73509 | 0.73893 | 0.80875
43602.8826 | 0.74243 | 0.75341 | 0.74601 | 0.74901 | 0.72877 | 0.73651 | 0.7407 | 0.80974
43602.8826 | 0.74168 | 0.7526 | 0.7452 | 0.74834 | 0.72776 | 0.73534 | 0.73987 | 0.80902
43602.8828 | 0.74076 | 0.7516 | 0.74428 | 0.74719 | 0.72648 | 0.73423 | 0.73988 | 0.80827
43602.8828 | 0.7411 | 0.75194 | 0.74467 | 0.74777 | 0.72748 | 0.73502 | 0.73933 | 0.80872
43602.883 | 0.74176 | 0.7523 | 0.74521 | 0.74798 | 0.72775 | 0.73537 | 0.74171 | 0.80891
43602.883 | 0.7438 | 0.75431 | 0.74764 | 0.75017 | 0.72995 | 0.73728 | 0.7411 | 0.81029
43602.8833 | 0.74218 | 0.75296 | 0.74593 | 0.7489 | 0.72828 | 0.73596 | 0.74013 | 0.80938
43602.8833 | 0.74219 | 0.75287 | 0.74582 | 0.7485 | 0.72802 | 0.73552 | 0.74024 | 0.80922
43602.8836 | 0.74312 | 0.75406 | 0.74667 | 0.74937 | 0.72906 | 0.7368 | 0.74158 | 0.80981
43602.8835 | 0.74316 | 0.75384 | 0.74682 | 0.74933 | 0.72871 | 0.73656 | 0.74152 | 0.80968
43602.8838 | 0.743 | 0.75374 | 0.74652 | 0.74926 | 0.72894 | 0.73634 | 0.74067 | 0.8098
43602.8838 | 0.74395 | 0.75465 | 0.74766 | 0.75045 | 0.73003 | 0.73767 | 0.74271 | 0.81034
43602.8841 | 0.74535 | 0.75572 | 0.74917 | 0.75148 | 0.73163 | 0.73916 | 0.74471 | 0.81131
43602.8841 | 0.74427 | 0.75512 | 0.74824 | 0.75064 | 0.73058 | 0.73813 | 0.74142 | 0.81055
43602.8844 | 0.74462 | 0.75532 | 0.74865 | 0.75123 | 0.73095 | 0.73832 | 0.74346 | 0.81081
43602.8844 | 0.74474 | 0.75543 | 0.74847 | 0.75106 | 0.7308 | 0.73825 | 0.74222 | 0.81081
43602.8847 | 0.74488 | 0.75571 | 0.74844 | 0.7513 | 0.73083 | 0.73836 | 0.74282 | 0.81094
43602.8847 | 0.74503 | 0.75565 | 0.74858 | 0.75121 | 0.73103 | 0.7386 | 0.74396 | 0.81081
43602.8849 | 0.74471 | 0.75547 | 0.74821 | 0.75097 | 0.73101 | 0.73847 | 0.74287 | 0.81079
43602.8849 | 0.74455 | 0.75521 | 0.74811 | 0.75082 | 0.73037 | 0.7379 | 0.74238 | 0.81046
43602.8852 | 0.74556 | 0.75623 | 0.7492 | 0.75217 | 0.73186 | 0.73915 | 0.74321 | 0.81147
43602.8852 | 0.74534 | 0.75595 | 0.74895 | 0.75203 | 0.7315 | 0.7392 | 0.74504 | 0.81125
43602.8855 | 0.74476 | 0.75529 | 0.74817 | 0.7511 | 0.73099 | 0.73863 | 0.74324 | 0.81062
43602.8855 | 0.74432 | 0.75496 | 0.74777 | 0.75078 | 0.73069 | 0.73813 | 0.7419 | 0.81046
43602.8858 | 0.74462 | 0.75528 | 0.74795 | 0.75133 | 0.73104 | 0.73847 | 0.74319 | 0.81065
43602.8858 | 0.74442 | 0.7551 | 0.74824 | 0.751 | 0.73059 | 0.73825 | 0.74322 | 0.81053
43602.8861 | 0.74462 | 0.75499 | 0.74799 | 0.75081 | 0.73057 | 0.73806 | 0.74247 | 0.81049
43602.886 | 0.74431 | 0.75496 | 0.74809 | 0.75063 | 0.73047 | 0.73784 | 0.74268 | 0.81032
43602.8863 | 0.74463 | 0.75499 | 0.74804 | 0.75097 | 0.73076 | 0.73829 | 0.74245 | 0.8106
43602.8863 | 0.7446 | 0.75484 | 0.7483 | 0.7509 | 0.73055 | 0.73791 | 0.74262 | 0.81043
43602.8866 | 0.7439 | 0.75443 | 0.74759 | 0.74999 | 0.72985 | 0.7373 | 0.74209 | 0.80998
43602.8866 | 0.74389 | 0.75446 | 0.74759 | 0.75007 | 0.73018 | 0.73756 | 0.74104 | 0.81012
43602.8869 | 0.744 | 0.75467 | 0.74786 | 0.7505 | 0.73024 | 0.7376 | 0.74499 | 0.81003
43602.8869 | 0.74344 | 0.75415 | 0.74713 | 0.75 | 0.72981 | 0.73717 | 0.74057 | 0.8098
43602.8872 | 0.74327 | 0.75392 | 0.74727 | 0.74968 | 0.72946 | 0.73703 | 0.74089 | 0.8097
43602.8871 | 0.74339 | 0.75395 | 0.74734 | 0.74969 | 0.72961 | 0.73694 | 0.74143 | 0.80973
43602.8874 | 0.74311 | 0.75381 | 0.74729 | 0.74941 | 0.72944 | 0.73689 | 0.74053 | 0.80948
43602.8874 | 0.74298 | 0.75341 | 0.74683 | 0.74915 | 0.72937 | 0.7368 | 0.74125 | 0.80936
43602.8877 | 0.74299 | 0.75347 | 0.74689 | 0.74933 | 0.72923 | 0.73661 | 0.74059 | 0.80935
43602.8877 | 0.7426 | 0.75327 | 0.74667 | 0.74935 | 0.72906 | 0.73648 | 0.74191 | 0.80918
43602.888 | 0.74271 | 0.7532 | 0.74656 | 0.74894 | 0.72858 | 0.73622 | 0.7404 | 0.80895
43602.888 | 0.7424 | 0.75324 | 0.74614 | 0.74872 | 0.72857 | 0.73602 | 0.74008 | 0.80886
43602.8883 | 0.74136 | 0.75201 | 0.74511 | 0.74773 | 0.72755 | 0.73493 | 0.73969 | 0.80826
43602.8883 | 0.73973 | 0.75082 | 0.74388 | 0.74635 | 0.72594 | 0.73331 | 0.73766 | 0.80713
43602.8885 | 0.74055 | 0.7514 | 0.74418 | 0.74675 | 0.72683 | 0.73418 | 0.73985 | 0.80755
43602.8885 | 0.74087 | 0.75178 | 0.74488 | 0.74719 | 0.72723 | 0.73444 | 0.74037 | 0.80767
43602.8888 | 0.73928 | 0.75039 | 0.7434 | 0.74591 | 0.72598 | 0.73351 | 0.74138 | 0.80716
43602.8888 | 0.73939 | 0.75054 | 0.74369 | 0.74629 | 0.72569 | 0.73317 | 0.73796 | 0.80687
43602.8891 | 0.73951 | 0.75017 | 0.74374 | 0.74637 | 0.72562 | 0.73322 | 0.73764 | 0.80695
43602.8891 | 0.73966 | 0.75038 | 0.74361 | 0.74606 | 0.72564 | 0.73315 | 0.73785 | 0.80693
43602.8894 | 0.73974 | 0.75018 | 0.74356 | 0.74587 | 0.72536 | 0.7327 | 0.7374 | 0.80655
43602.8894 | 0.7406 | 0.75141 | 0.74469 | 0.74713 | 0.7269 | 0.73431 | 0.74218 | 0.80757
43602.8896 | 0.73893 | 0.75008 | 0.7429 | 0.7458 | 0.72491 | 0.73254 | 0.73897 | 0.8065
43602.8896 | 0.7407 | 0.75171 | 0.74504 | 0.74742 | 0.72686 | 0.73418 | 0.74174 | 0.80758
43602.8899 | 0.74018 | 0.75094 | 0.74408 | 0.74677 | 0.72654 | 0.73376 | 0.7402 | 0.80709
43602.8899 | 0.7415 | 0.75212 | 0.74535 | 0.74787 | 0.72775 | 0.73505 | 0.73837 | 0.80806
43602.8902 | 0.74107 | 0.7518 | 0.74495 | 0.7475 | 0.7276 | 0.73503 | 0.73939 | 0.808
43602.8902 | 0.74104 | 0.7518 | 0.7448 | 0.74785 | 0.72688 | 0.73413 | 0.74077 | 0.80743
43602.8905 | 0.741 | 0.75217 | 0.74545 | 0.74829 | 0.72786 | 0.7351 | 0.73877 | 0.80805
43602.8905 | 0.7406 | 0.75189 | 0.74536 | 0.74761 | 0.72709 | 0.73463 | 0.73828 | 0.80768
43602.8908 | 0.74119 | 0.75198 | 0.7458 | 0.74804 | 0.72775 | 0.73516 | 0.73962 | 0.80795
43602.8908 | 0.74174 | 0.75274 | 0.74621 | 0.74889 | 0.72841 | 0.7357 | 0.7435 | 0.80835
43602.891 | 0.74144 | 0.75263 | 0.74586 | 0.74874 | 0.72848 | 0.73571 | 0.74261 | 0.80825
43602.891 | 0.74206 | 0.75276 | 0.74615 | 0.74901 | 0.72859 | 0.73596 | 0.74008 | 0.80835
43602.8913 | 0.74219 | 0.75308 | 0.74646 | 0.74906 | 0.72876 | 0.73612 | 0.74135 | 0.80845
43602.8913 | 0.7417 | 0.75277 | 0.74597 | 0.74841 | 0.72831 | 0.7357 | 0.73908 | 0.80829
43602.8916 | 0.74195 | 0.75311 | 0.74637 | 0.7489 | 0.72836 | 0.73577 | 0.74189 | 0.80833
43602.8916 | 0.74216 | 0.75321 | 0.74646 | 0.74914 | 0.72838 | 0.73583 | 0.74071 | 0.80843
43602.8919 | 0.74214 | 0.75294 | 0.74661 | 0.74861 | 0.72841 | 0.73559 | 0.74013 | 0.80825
43602.8919 | 0.74242 | 0.75291 | 0.74626 | 0.74888 | 0.72842 | 0.73579 | 0.74004 | 0.80845
43602.8922 | 0.74222 | 0.75269 | 0.74622 | 0.74835 | 0.72817 | 0.73554 | 0.73977 | 0.80829
43602.8922 | 0.74237 | 0.75291 | 0.74639 | 0.74857 | 0.72819 | 0.73559 | 0.73997 | 0.8083
43602.8925 | 0.74262 | 0.75289 | 0.74626 | 0.74873 | 0.72847 | 0.73572 | 0.74239 | 0.80834
43602.8924 | 0.74269 | 0.75307 | 0.74664 | 0.74871 | 0.72851 | 0.73559 | 0.73968 | 0.80831
43602.8927 | 0.7427 | 0.7533 | 0.74661 | 0.74894 | 0.72878 | 0.73609 | 0.74135 | 0.80849
43602.8927 | 0.74291 | 0.75341 | 0.74672 | 0.74911 | 0.72938 | 0.73598 | 0.73994 | 0.80863
43602.893 | 0.74277 | 0.75345 | 0.74631 | 0.74946 | 0.72907 | 0.73612 | 0.74055 | 0.80851
43602.893 | 0.7423 | 0.75286 | 0.74617 | 0.74883 | 0.72853 | 0.73543 | 0.73977 | 0.80818
43602.8933 | 0.74266 | 0.75282 | 0.74598 | 0.74903 | 0.72849 | 0.73561 | 0.73995 | 0.80811
43602.8933 | 0.74282 | 0.75344 | 0.74652 | 0.74944 | 0.72876 | 0.73615 | 0.74018 | 0.80829
43602.8936 | 0.74276 | 0.75311 | 0.7465 | 0.7493 | 0.72932 | 0.73614 | 0.74359 | 0.80854
43602.8936 | 0.74309 | 0.75335 | 0.74705 | 0.74958 | 0.72943 | 0.73643 | 0.74044 | 0.80866
43602.8939 | 0.74222 | 0.75237 | 0.74606 | 0.74837 | 0.72855 | 0.73555 | 0.74142 | 0.80813
43602.8939 | 0.74232 | 0.75302 | 0.74637 | 0.74895 | 0.72846 | 0.73587 | 0.73992 | 0.8082
43602.8942 | 0.74179 | 0.75223 | 0.74563 | 0.74844 | 0.72811 | 0.73515 | 0.74247 | 0.80785
43602.8941 | 0.74212 | 0.75265 | 0.74573 | 0.74876 | 0.72817 | 0.73545 | 0.73951 | 0.80798
43602.8944 | 0.74196 | 0.75219 | 0.74545 | 0.74827 | 0.72782 | 0.73499 | 0.73927 | 0.80777
43602.8944 | 0.74152 | 0.75167 | 0.74498 | 0.74794 | 0.72742 | 0.73467 | 0.74016 | 0.80748
43602.8947 | 0.74139 | 0.7516 | 0.74488 | 0.74791 | 0.72711 | 0.73462 | 0.74082 | 0.80728
43602.8947 | 0.74155 | 0.75184 | 0.74506 | 0.7481 | 0.7277 | 0.73484 | 0.74098 | 0.80752
43602.895 | 0.74082 | 0.75148 | 0.74497 | 0.74721 | 0.72731 | 0.73444 | 0.7386 | 0.80729
43602.895 | 0.741 | 0.75145 | 0.7448 | 0.74751 | 0.72701 | 0.73435 | 0.73918 | 0.80724
43602.8953 | 0.74135 | 0.75178 | 0.74491 | 0.74755 | 0.72743 | 0.73456 | 0.73968 | 0.80736
43602.8953 | 0.74083 | 0.7515 | 0.74465 | 0.74702 | 0.72709 | 0.7343 | 0.73826 | 0.80701
43602.8956 | 0.74135 | 0.75151 | 0.74545 | 0.74755 | 0.72765 | 0.73473 | 0.74076 | 0.80739
43602.8956 | 0.74126 | 0.75145 | 0.74515 | 0.74757 | 0.72729 | 0.7343 | 0.73837 | 0.80698
43602.8959 | 0.74109 | 0.75133 | 0.7446 | 0.74721 | 0.72752 | 0.73462 | 0.73958 | 0.8073
43602.8959 | 0.74174 | 0.75182 | 0.74538 | 0.74758 | 0.7275 | 0.73454 | 0.73899 | 0.8073
43602.8961 | 0.7435 | 0.75343 | 0.74739 | 0.74962 | 0.72965 | 0.73687 | 0.74059 | 0.80863
43602.8961 | 0.7437 | 0.75421 | 0.74777 | 0.75022 | 0.72999 | 0.73689 | 0.74107 | 0.80859
43602.8964 | 0.74601 | 0.75624 | 0.7499 | 0.75231 | 0.73276 | 0.73965 | 0.74465 | 0.81063
43602.8964 | 0.74678 | 0.75702 | 0.75099 | 0.75308 | 0.73389 | 0.74055 | 0.74762 | 0.81121
43602.8967 | 0.75063 | 0.76018 | 0.75461 | 0.75696 | 0.73657 | 0.74362 | 0.74743 | 0.81297
43602.8967 | 0.7516 | 0.76147 | 0.75549 | 0.75757 | 0.73827 | 0.74507 | 0.74961 | 0.81397
43602.897 | 0.75307 | 0.76269 | 0.75728 | 0.75908 | 0.7393 | 0.74591 | 0.75287 | 0.81445
43602.897 | 0.75408 | 0.76387 | 0.75826 | 0.76004 | 0.74079 | 0.74712 | 0.75079 | 0.81542
43602.8973 | 0.75992 | 0.76913 | 0.76375 | 0.76593 | 0.74704 | 0.75302 | 0.75696 | 0.81945
43602.8973 | 0.76291 | 0.77179 | 0.76664 | 0.76884 | 0.74997 | 0.75599 | 0.76075 | 0.82126
43602.8976 | 0.76622 | 0.7748 | 0.76977 | 0.77188 | 0.75307 | 0.75899 | 0.76294 | 0.82311
43602.8975 | 0.76624 | 0.77489 | 0.77003 | 0.7722 | 0.75374 | 0.75966 | 0.76333 | 0.8235
43602.8978 | 0.76124 | 0.77015 | 0.76523 | 0.76701 | 0.74858 | 0.75491 | 0.75838 | 0.82031
43602.8978 | 0.76123 | 0.77 | 0.76494 | 0.76704 | 0.74832 | 0.75455 | 0.75812 | 0.82014
43602.898 | 0.76071 | 0.76974 | 0.76471 | 0.76665 | 0.74793 | 0.7543 | 0.75996 | 0.81987
43602.898 | 0.75964 | 0.76878 | 0.76374 | 0.76557 | 0.74671 | 0.75298 | 0.75647 | 0.81904
43602.8983 | 0.75693 | 0.76621 | 0.76109 | 0.76272 | 0.74388 | 0.75068 | 0.75384 | 0.81739
43602.8983 | 0.75669 | 0.76623 | 0.76083 | 0.76279 | 0.7438 | 0.75046 | 0.75592 | 0.81721
43602.8985 | 0.75566 | 0.76481 | 0.7593 | 0.76172 | 0.74255 | 0.74912 | 0.75554 | 0.81656
43602.8985 | 0.75609 | 0.76533 | 0.75971 | 0.76203 | 0.74292 | 0.74953 | 0.7536 | 0.81668
43602.8987 | 0.75694 | 0.76606 | 0.76092 | 0.76269 | 0.74397 | 0.7505 | 0.75425 | 0.81726
43602.8987 | 0.7578 | 0.76702 | 0.76179 | 0.76356 | 0.74457 | 0.75101 | 0.7546 | 0.81772
43602.899 | 0.75896 | 0.76818 | 0.76302 | 0.76496 | 0.74599 | 0.75232 | 0.7582 | 0.81856
43602.8989 | 0.76027 | 0.76952 | 0.76486 | 0.76651 | 0.74731 | 0.75371 | 0.75671 | 0.81948
43602.8992 | 0.77028 | 0.77874 | 0.77434 | 0.77621 | 0.75789 | 0.76368 | 0.76702 | 0.82615
43602.8992 | 0.78099 | 0.78892 | 0.78511 | 0.78698 | 0.76562 | 0.7713 | 0.77641 | 0.83107
43602.8994 | 0.79277 | 0.79996 | 0.79667 | 0.79834 | 0.78185 | 0.78675 | 0.79019 | 0.84128
43602.8994 | 0.7929 | 0.80018 | 0.79687 | 0.79878 | 0.78221 | 0.78708 | 0.79017 | 0.84133
43602.8996 | 0.78318 | 0.79095 | 0.78702 | 0.78925 | 0.77234 | 0.77755 | 0.78046 | 0.83519
43602.8996 | 0.7797 | 0.78784 | 0.78365 | 0.78585 | 0.76855 | 0.77393 | 0.77763 | 0.83277
43602.8999 | 0.77588 | 0.78409 | 0.77991 | 0.78215 | 0.7639 | 0.76953 | 0.77223 | 0.82977
43602.8999 | 0.77732 | 0.78546 | 0.78095 | 0.78341 | 0.76515 | 0.77066 | 0.77548 | 0.83049
43602.9001 | 0.78233 | 0.79014 | 0.78607 | 0.78814 | 0.7711 | 0.77629 | 0.77914 | 0.83445
43602.9001 | 0.77999 | 0.78823 | 0.78424 | 0.78619 | 0.76885 | 0.77417 | 0.77786 | 0.83306
43602.9003 | 0.77606 | 0.78421 | 0.78018 | 0.78222 | 0.76434 | 0.76962 | 0.77292 | 0.82993
43602.9003 | 0.77566 | 0.78395 | 0.77986 | 0.78148 | 0.76421 | 0.76968 | 0.77404 | 0.82992
43602.9005 | 0.77455 | 0.78304 | 0.77896 | 0.7807 | 0.76291 | 0.76859 | 0.77132 | 0.82914
43602.9005 | 0.7758 | 0.78422 | 0.77995 | 0.78186 | 0.76367 | 0.76936 | 0.77438 | 0.82976
43602.9008 | 0.77409 | 0.78266 | 0.77835 | 0.7802 | 0.76238 | 0.76779 | 0.77145 | 0.82886
43602.9008 | 0.77471 | 0.78321 | 0.77891 | 0.78107 | 0.76306 | 0.7685 | 0.77229 | 0.82919
43602.901 | 0.77519 | 0.7839 | 0.77937 | 0.78147 | 0.76397 | 0.76943 | 0.77272 | 0.82971
43602.901 | 0.77516 | 0.78391 | 0.77947 | 0.78163 | 0.76372 | 0.76918 | 0.77292 | 0.82951
43602.9012 | 0.7755 | 0.78449 | 0.78005 | 0.78167 | 0.76414 | 0.76946 | 0.77312 | 0.82984
43602.9012 | 0.77604 | 0.7848 | 0.78053 | 0.78244 | 0.76465 | 0.76998 | 0.77314 | 0.83
43602.9015 | 0.77722 | 0.78568 | 0.78122 | 0.78349 | 0.76542 | 0.77103 | 0.7739 | 0.83079
43602.9015 | 0.77659 | 0.7848 | 0.78088 | 0.78298 | 0.76519 | 0.7707 | 0.7741 | 0.83044
43602.9017 | 0.77566 | 0.78439 | 0.78009 | 0.78229 | 0.76436 | 0.76987 | 0.7738 | 0.83005
43602.9017 | 0.77543 | 0.78378 | 0.77948 | 0.78169 | 0.76373 | 0.76912 | 0.77234 | 0.82951
43602.9019 | 0.77595 | 0.7847 | 0.78024 | 0.78237 | 0.7647 | 0.77007 | 0.77538 | 0.83012
43602.9019 | 0.77649 | 0.78507 | 0.78101 | 0.78298 | 0.76507 | 0.7705 | 0.77384 | 0.83029
43602.9021 | 0.77633 | 0.78471 | 0.78065 | 0.78251 | 0.76448 | 0.77 | 0.77644 | 0.83003
43602.9021 | 0.77494 | 0.7838 | 0.77959 | 0.78157 | 0.76366 | 0.76901 | 0.77509 | 0.82944
43602.9024 | 0.77366 | 0.78258 | 0.77822 | 0.78012 | 0.76219 | 0.76727 | 0.77108 | 0.82839
43602.9024 | 0.77306 | 0.78194 | 0.77777 | 0.77958 | 0.76164 | 0.76694 | 0.76956 | 0.82806
43602.9026 | 0.77417 | 0.78269 | 0.77872 | 0.78037 | 0.76254 | 0.76778 | 0.77341 | 0.82866
43602.9026 | 0.77454 | 0.78317 | 0.77906 | 0.78091 | 0.76255 | 0.76828 | 0.77142 | 0.82884
43602.9028 | 0.77483 | 0.78309 | 0.77894 | 0.78057 | 0.76316 | 0.7685 | 0.77181 | 0.82914
43602.9028 | 0.77438 | 0.78278 | 0.77841 | 0.78042 | 0.7625 | 0.76793 | 0.7739 | 0.82872
43602.9031 | 0.77348 | 0.78235 | 0.77779 | 0.77981 | 0.76157 | 0.76721 | 0.77102 | 0.82828
43602.903 | 0.77359 | 0.78222 | 0.77794 | 0.77999 | 0.76227 | 0.76738 | 0.77124 | 0.82836
43602.9033 | 0.77314 | 0.78166 | 0.77769 | 0.77942 | 0.76137 | 0.76688 | 0.77022 | 0.82792
43602.9033 | 0.77202 | 0.78063 | 0.77636 | 0.77813 | 0.76026 | 0.76579 | 0.76967 | 0.82711
43602.9035 | 0.76882 | 0.77776 | 0.77318 | 0.77487 | 0.7571 | 0.76289 | 0.76864 | 0.82511
43602.9035 | 0.76787 | 0.77687 | 0.7725 | 0.774 | 0.75607 | 0.7617 | 0.76591 | 0.82445
43602.9037 | 0.77112 | 0.78 | 0.77584 | 0.77732 | 0.75936 | 0.7649 | 0.76916 | 0.82655
43602.9037 | 0.77509 | 0.78349 | 0.77955 | 0.7813 | 0.76326 | 0.76874 | 0.77215 | 0.82886
43602.904 | 0.78649 | 0.79463 | 0.79125 | 0.7927 | 0.77506 | 0.78025 | 0.78241 | 0.83652
43602.904 | 0.8193 | 0.82544 | 0.82392 | 0.82539 | 0.80974 | 0.81339 | 0.81532 | 0.85827
43602.9042 | 0.81381 | 0.82029 | 0.81844 | 0.82 | 0.80484 | 0.80837 | 0.81084 | 0.85512
43602.9042 | 0.80935 | 0.81603 | 0.81398 | 0.81574 | 0.80047 | 0.80448 | 0.80681 | 0.85247
43602.9045 | 0.80256 | 0.80968 | 0.80694 | 0.80867 | 0.79311 | 0.79709 | 0.80014 | 0.84764
43602.9045 | 0.80014 | 0.80727 | 0.80463 | 0.80619 | 0.7901 | 0.79451 | 0.7968 | 0.84598
43602.9048 | 0.79359 | 0.80094 | 0.79809 | 0.79987 | 0.78322 | 0.7879 | 0.79063 | 0.84157
43602.9048 | 0.79129 | 0.79868 | 0.79561 | 0.79737 | 0.78065 | 0.78556 | 0.78802 | 0.83995
43602.9051 | 0.78669 | 0.79453 | 0.79118 | 0.79287 | 0.77597 | 0.78097 | 0.78359 | 0.83693
43602.905 | 0.78525 | 0.79307 | 0.78973 | 0.79144 | 0.77445 | 0.77927 | 0.78454 | 0.83594
43602.9053 | 0.78464 | 0.79255 | 0.78935 | 0.79073 | 0.77389 | 0.77865 | 0.78458 | 0.83552
43602.9053 | 0.78434 | 0.79254 | 0.7891 | 0.79054 | 0.77338 | 0.77814 | 0.78254 | 0.8352
43602.9056 | 0.78398 | 0.79226 | 0.78843 | 0.7905 | 0.77314 | 0.77806 | 0.78183 | 0.83517
43602.9056 | 0.78397 | 0.79208 | 0.78838 | 0.79014 | 0.77295 | 0.77788 | 0.78138 | 0.83497
43602.9059 | 0.78307 | 0.79113 | 0.78772 | 0.78965 | 0.77184 | 0.77689 | 0.78028 | 0.83433
43602.9059 | 0.78231 | 0.79034 | 0.78726 | 0.78872 | 0.77161 | 0.77628 | 0.77951 | 0.83407
43602.9062 | 0.78047 | 0.78837 | 0.7851 | 0.78695 | 0.76937 | 0.77425 | 0.7789 | 0.83266
43602.9062 | 0.77947 | 0.78773 | 0.78455 | 0.78609 | 0.76863 | 0.77368 | 0.77656 | 0.83207
43602.9065 | 0.78436 | 0.79236 | 0.78878 | 0.79059 | 0.77268 | 0.77768 | 0.78014 | 0.83468
43602.9065 | 0.80588 | 0.81254 | 0.81043 | 0.8121 | 0.7955 | 0.79928 | 0.80209 | 0.84919
43602.9068 | 0.82257 | 0.82838 | 0.82727 | 0.82874 | 0.8129 | 0.81587 | 0.81835 | 0.86029
43602.9068 | 0.83527 | 0.84046 | 0.83973 | 0.84137 | 0.82393 | 0.82666 | 0.82868 | 0.86702
43602.9071 | 0.83205 | 0.83721 | 0.83639 | 0.83805 | 0.82435 | 0.82689 | 0.82847 | 0.86719
43602.9071 | 0.8248 | 0.83013 | 0.82922 | 0.83082 | 0.81669 | 0.81961 | 0.8229 | 0.86243
43602.9074 | 0.81481 | 0.82086 | 0.81934 | 0.8208 | 0.8058 | 0.8092 | 0.81123 | 0.85567
43602.9073 | 0.8113 | 0.81754 | 0.81618 | 0.81775 | 0.80208 | 0.80586 | 0.80915 | 0.8533
43602.9076 | 0.80356 | 0.81041 | 0.80808 | 0.8102 | 0.79427 | 0.79819 | 0.80097 | 0.84831
43602.9076 | 0.80144 | 0.8084 | 0.80586 | 0.80786 | 0.79185 | 0.7959 | 0.79908 | 0.84673
43602.9079 | 0.79681 | 0.80419 | 0.80116 | 0.8034 | 0.78675 | 0.79122 | 0.79602 | 0.84364
43602.9079 | 0.79539 | 0.80253 | 0.79988 | 0.80165 | 0.78501 | 0.78966 | 0.79259 | 0.84252
43602.9082 | 0.79252 | 0.79997 | 0.7972 | 0.79907 | 0.78221 | 0.78668 | 0.7896 | 0.84065
43602.9082 | 0.79185 | 0.79952 | 0.79646 | 0.79835 | 0.78144 | 0.78612 | 0.78997 | 0.84011
43602.9085 | 0.79242 | 0.8001 | 0.79735 | 0.79891 | 0.78202 | 0.78665 | 0.79011 | 0.84058
43602.9085 | 0.79693 | 0.80434 | 0.80224 | 0.80323 | 0.78707 | 0.79141 | 0.79354 | 0.84365
43602.909 | 0.79671 | 0.80418 | 0.80177 | 0.80312 | 0.78672 | 0.79103 | 0.79349 | 0.84334
43602.909 | 0.80104 | 0.80823 | 0.80579 | 0.80735 | 0.79049 | 0.79457 | 0.79883 | 0.84582
43602.9092 | 0.88772 | 0.89021 | 0.89225 | 0.89374 | 0.8827 | 0.88308 | 0.88322 | 0.90419
43602.9092 | 0.88615 | 0.88899 | 0.89061 | 0.89235 | 0.88179 | 0.88203 | 0.88407 | 0.90378
43602.9095 | 0.88495 | 0.8876 | 0.88919 | 0.89077 | 0.87941 | 0.87991 | 0.88119 | 0.90223
43602.9094 | 0.87674 | 0.87953 | 0.88116 | 0.88267 | 0.8717 | 0.87232 | 0.87459 | 0.89733
43602.9097 | 0.86756 | 0.87099 | 0.87213 | 0.87369 | 0.86191 | 0.8632 | 0.86661 | 0.89118
43602.9097 | 0.86223 | 0.86609 | 0.86718 | 0.86832 | 0.8559 | 0.85733 | 0.86059 | 0.88728
43602.9099 | 0.85874 | 0.86273 | 0.86382 | 0.86486 | 0.85197 | 0.85351 | 0.85512 | 0.88491
43602.9099 | 0.86086 | 0.8645 | 0.86531 | 0.86699 | 0.85499 | 0.85611 | 0.85838 | 0.88669
43602.9101 | 0.86023 | 0.86393 | 0.86491 | 0.86618 | 0.8517 | 0.85327 | 0.85697 | 0.88472
43602.9101 | 0.87183 | 0.875 | 0.87633 | 0.87773 | 0.86538 | 0.86634 | 0.86797 | 0.89337
43602.9104 | 0.86904 | 0.87225 | 0.87316 | 0.87475 | 0.8633 | 0.8642 | 0.86747 | 0.89198
43602.9103 | 0.86253 | 0.86619 | 0.86704 | 0.86843 | 0.85602 | 0.85745 | 0.859 | 0.88748
43602.9106 | 0.85782 | 0.86181 | 0.86255 | 0.86385 | 0.85136 | 0.85267 | 0.85464 | 0.88446
43602.9106 | 0.85574 | 0.85936 | 0.8602 | 0.86173 | 0.84898 | 0.85042 | 0.85474 | 0.88295
43602.9108 | 0.85238 | 0.85602 | 0.8568 | 0.85826 | 0.8451 | 0.84642 | 0.84823 | 0.8803
43602.9108 | 0.85054 | 0.85451 | 0.8552 | 0.85656 | 0.84344 | 0.84521 | 0.84671 | 0.87938
43602.911 | 0.84815 | 0.85248 | 0.85267 | 0.85412 | 0.84136 | 0.84301 | 0.84478 | 0.87798
43602.911 | 0.84824 | 0.85246 | 0.85285 | 0.85411 | 0.84059 | 0.84267 | 0.8442 | 0.87774
43602.9113 | 0.84948 | 0.85364 | 0.85431 | 0.85552 | 0.84177 | 0.84371 | 0.84588 | 0.87841
43602.9113 | 0.84937 | 0.85367 | 0.85401 | 0.85572 | 0.84221 | 0.84418 | 0.84636 | 0.87854
43602.9115 | 0.84646 | 0.85065 | 0.85113 | 0.85247 | 0.83866 | 0.84088 | 0.84503 | 0.87629
43602.9115 | 0.84527 | 0.84951 | 0.84963 | 0.85106 | 0.83774 | 0.84 | 0.84257 | 0.87582
43602.9117 | 0.84998 | 0.85402 | 0.85446 | 0.85613 | 0.84177 | 0.84346 | 0.84525 | 0.8781
43602.9117 | 0.85125 | 0.85518 | 0.85559 | 0.85715 | 0.84439 | 0.84626 | 0.84786 | 0.87995
43602.9119 | 0.85727 | 0.86117 | 0.86181 | 0.86333 | 0.85141 | 0.85293 | 0.85512 | 0.88441
43602.9119 | 0.85283 | 0.8567 | 0.85716 | 0.85869 | 0.84596 | 0.84759 | 0.84999 | 0.88103
43602.9122 | 0.86222 | 0.86589 | 0.86683 | 0.86827 | 0.85533 | 0.85641 | 0.85799 | 0.88676
43602.9122 | 0.86072 | 0.86464 | 0.86585 | 0.86674 | 0.85401 | 0.85541 | 0.85875 | 0.88609
43602.9124 | 0.86242 | 0.86587 | 0.86704 | 0.86822 | 0.85584 | 0.85706 | 0.8588 | 0.88707
43602.9124 | 0.86661 | 0.86966 | 0.87125 | 0.87228 | 0.8602 | 0.86124 | 0.86261 | 0.88994
43602.9126 | 0.87452 | 0.87741 | 0.87905 | 0.88044 | 0.86822 | 0.86874 | 0.86949 | 0.89483
43602.9126 | 0.87667 | 0.87944 | 0.88153 | 0.8827 | 0.87197 | 0.87239 | 0.87445 | 0.89709
43602.9129 | 0.87562 | 0.87827 | 0.88056 | 0.88156 | 0.87025 | 0.87065 | 0.87266 | 0.89617
43602.9128 | 0.87272 | 0.8758 | 0.8775 | 0.87889 | 0.86756 | 0.86793 | 0.87004 | 0.89428
43602.9131 | 0.86564 | 0.86917 | 0.87058 | 0.87185 | 0.86016 | 0.86121 | 0.86226 | 0.88975
43602.9131 | 0.86195 | 0.86556 | 0.86694 | 0.86824 | 0.85596 | 0.85717 | 0.86001 | 0.88717
43602.9133 | 0.85676 | 0.86064 | 0.8616 | 0.86298 | 0.8505 | 0.85194 | 0.85355 | 0.88363
43602.9133 | 0.85398 | 0.85771 | 0.85889 | 0.85985 | 0.84722 | 0.84879 | 0.85143 | 0.88152
43602.9135 | 0.84959 | 0.85404 | 0.85483 | 0.8559 | 0.84306 | 0.8448 | 0.84729 | 0.87894
43602.9135 | 0.84777 | 0.85225 | 0.85274 | 0.85389 | 0.84076 | 0.84249 | 0.84508 | 0.87754
43602.9138 | 0.8695 | 0.87267 | 0.87482 | 0.87553 | 0.86212 | 0.86293 | 0.86398 | 0.89093
43602.9138 | 0.86982 | 0.87279 | 0.87485 | 0.87588 | 0.86425 | 0.86501 | 0.86771 | 0.89236
43602.914 | 0.86406 | 0.8675 | 0.86922 | 0.87008 | 0.85773 | 0.85905 | 0.86096 | 0.88822
43602.914 | 0.86755 | 0.87087 | 0.87287 | 0.87377 | 0.86243 | 0.86299 | 0.86493 | 0.89107
43602.9143 | 0.87073 | 0.87399 | 0.8758 | 0.87697 | 0.86447 | 0.86523 | 0.86829 | 0.89247
43602.9143 | 0.87942 | 0.88216 | 0.88444 | 0.88568 | 0.87396 | 0.87441 | 0.87577 | 0.8986
43602.9145 | 0.89766 | 0.89949 | 0.90262 | 0.90385 | 0.89345 | 0.89304 | 0.89364 | 0.91093
43602.9145 | 0.8977 | 0.89943 | 0.90276 | 0.90385 | 0.89389 | 0.89334 | 0.89371 | 0.91116
43602.9148 | 0.89406 | 0.89576 | 0.89898 | 0.89997 | 0.88985 | 0.88957 | 0.89172 | 0.90857
43602.9147 | 0.88816 | 0.89043 | 0.893 | 0.89452 | 0.88387 | 0.88384 | 0.88567 | 0.90476
43602.915 | 0.87994 | 0.88278 | 0.88501 | 0.88617 | 0.87533 | 0.87548 | 0.87686 | 0.89946
43602.915 | 0.87692 | 0.87974 | 0.88169 | 0.883 | 0.87177 | 0.87237 | 0.87507 | 0.89712
43602.9152 | 0.87108 | 0.87436 | 0.87647 | 0.87713 | 0.86661 | 0.86706 | 0.86834 | 0.89364
43602.9152 | 0.86808 | 0.87171 | 0.87353 | 0.87426 | 0.86308 | 0.86348 | 0.86494 | 0.89146
43602.9155 | 0.86372 | 0.8675 | 0.86937 | 0.87016 | 0.85791 | 0.85894 | 0.86087 | 0.88837
43602.9154 | 0.86283 | 0.86661 | 0.86841 | 0.86933 | 0.85762 | 0.85854 | 0.86001 | 0.888
43602.9157 | 0.86329 | 0.86705 | 0.86867 | 0.86932 | 0.85767 | 0.85857 | 0.86025 | 0.8881
43602.9157 | 0.86105 | 0.86515 | 0.86661 | 0.86768 | 0.8553 | 0.85637 | 0.8595 | 0.88669
43602.9159 | 0.86819 | 0.8715 | 0.87322 | 0.8743 | 0.86062 | 0.86164 | 0.86331 | 0.89002
43602.9159 | 0.87393 | 0.877 | 0.87922 | 0.88016 | 0.86874 | 0.86917 | 0.87047 | 0.89492
43602.9161 | 0.86939 | 0.87252 | 0.8742 | 0.87547 | 0.86462 | 0.86505 | 0.86651 | 0.89245
43602.9161 | 0.8641 | 0.86744 | 0.8692 | 0.87032 | 0.85842 | 0.85921 | 0.86052 | 0.8885
43602.9164 | 0.86009 | 0.86359 | 0.86506 | 0.86603 | 0.854 | 0.85505 | 0.85931 | 0.88578
43602.9164 | 0.85847 | 0.86228 | 0.8639 | 0.8646 | 0.85227 | 0.85349 | 0.85556 | 0.88471
43602.9166 | 0.86923 | 0.8721 | 0.87385 | 0.8751 | 0.86124 | 0.86209 | 0.86375 | 0.89037
43602.9166 | 0.88085 | 0.88327 | 0.88593 | 0.88699 | 0.87575 | 0.87601 | 0.87692 | 0.89953
43602.9168 | 0.90911 | 0.91019 | 0.91422 | 0.91523 | 0.90649 | 0.90541 | 0.90655 | 0.91895
43602.9168 | 0.9 | 0.90142 | 0.90478 | 0.90613 | 0.89652 | 0.89609 | 0.89636 | 0.9126
43602.9171 | 0.91685 | 0.91723 | 0.92148 | 0.92264 | 0.91567 | 0.91403 | 0.91516 | 0.9248
43602.917 | 0.90599 | 0.90709 | 0.91072 | 0.91207 | 0.90261 | 0.90156 | 0.90226 | 0.91633
43602.9173 | 0.90198 | 0.90332 | 0.90678 | 0.90759 | 0.89838 | 0.89759 | 0.89788 | 0.91373
43602.9173 | 0.90067 | 0.90197 | 0.90555 | 0.90616 | 0.89705 | 0.89613 | 0.89669 | 0.91301
43602.9175 | 0.90298 | 0.90433 | 0.9078 | 0.9091 | 0.8999 | 0.89922 | 0.89976 | 0.915
43602.9175 | 0.89971 | 0.90106 | 0.9043 | 0.90549 | 0.89575 | 0.89509 | 0.89552 | 0.91215
43602.9178 | 0.89106 | 0.89303 | 0.89629 | 0.8971 | 0.88721 | 0.88698 | 0.88967 | 0.90672
43602.9177 | 0.88801 | 0.89017 | 0.89307 | 0.89428 | 0.88346 | 0.88316 | 0.88439 | 0.9044
43602.918 | 0.88385 | 0.88603 | 0.88875 | 0.88976 | 0.8794 | 0.87958 | 0.88044 | 0.90202
43602.918 | 0.88191 | 0.88407 | 0.88709 | 0.88766 | 0.8769 | 0.87702 | 0.87793 | 0.90028
43602.9182 | 0.8796 | 0.88174 | 0.88428 | 0.88544 | 0.87404 | 0.87429 | 0.87537 | 0.89837
43602.9182 | 0.87834 | 0.88061 | 0.88301 | 0.88442 | 0.87258 | 0.87302 | 0.87382 | 0.89745
43602.9185 | 0.89409 | 0.89582 | 0.89878 | 0.89986 | 0.89016 | 0.88985 | 0.89216 | 0.90877
43602.9184 | 0.88797 | 0.88989 | 0.89284 | 0.89389 | 0.88354 | 0.8833 | 0.88449 | 0.90453
43602.9187 | 0.88463 | 0.88637 | 0.88911 | 0.89008 | 0.87945 | 0.87969 | 0.88034 | 0.90186
43602.9187 | 0.884 | 0.88599 | 0.88872 | 0.89 | 0.87834 | 0.87845 | 0.87927 | 0.9011
43602.9189 | 0.89169 | 0.89344 | 0.89655 | 0.89776 | 0.88738 | 0.88727 | 0.88974 | 0.90705
43602.9189 | 0.88435 | 0.88641 | 0.88937 | 0.89054 | 0.88021 | 0.88018 | 0.88115 | 0.90241
43602.9191 | 0.88548 | 0.88762 | 0.89066 | 0.89144 | 0.88072 | 0.88078 | 0.88235 | 0.90281
43602.9191 | 0.88408 | 0.88628 | 0.88924 | 0.89001 | 0.87917 | 0.87934 | 0.88058 | 0.90162
43602.9194 | 0.89093 | 0.8926 | 0.89569 | 0.89665 | 0.88641 | 0.88599 | 0.88709 | 0.90637
43602.9194 | 0.88562 | 0.88776 | 0.89048 | 0.89143 | 0.88061 | 0.88057 | 0.88179 | 0.90259
43602.9196 | 0.89017 | 0.89175 | 0.89495 | 0.89602 | 0.88471 | 0.88444 | 0.88541 | 0.90518
43602.9196 | 0.88826 | 0.88972 | 0.89279 | 0.89403 | 0.88393 | 0.88369 | 0.88468 | 0.90453
43602.9198 | 0.89576 | 0.89676 | 0.90029 | 0.90153 | 0.89205 | 0.89142 | 0.89273 | 0.90969
43602.9198 | 0.90629 | 0.90708 | 0.91134 | 0.91233 | 0.90129 | 0.90051 | 0.90126 | 0.91565
43602.9201 | 0.92924 | 0.92881 | 0.93433 | 0.93518 | 0.92704 | 0.92523 | 0.92518 | 0.93198
43602.9201 | 0.92928 | 0.92883 | 0.9342 | 0.93495 | 0.92662 | 0.92465 | 0.92479 | 0.93173
43602.9203 | 0.92662 | 0.92668 | 0.93166 | 0.93258 | 0.9245 | 0.92266 | 0.92278 | 0.93041
43602.9203 | 0.92528 | 0.92516 | 0.93019 | 0.93106 | 0.92142 | 0.91985 | 0.92021 | 0.92853
43602.9205 | 0.92814 | 0.92792 | 0.9333 | 0.93414 | 0.92614 | 0.92422 | 0.92478 | 0.93158
43602.9205 | 0.92637 | 0.9262 | 0.93137 | 0.93226 | 0.92389 | 0.92211 | 0.92232 | 0.9301
43602.9208 | 0.92181 | 0.92169 | 0.92677 | 0.92732 | 0.91944 | 0.91786 | 0.9185 | 0.92731
43602.9208 | 0.91384 | 0.91451 | 0.91907 | 0.92 | 0.91128 | 0.91004 | 0.91211 | 0.92196
43602.921 | 0.90464 | 0.90561 | 0.90966 | 0.9106 | 0.90152 | 0.9005 | 0.90092 | 0.91584
43602.921 | 0.9037 | 0.90477 | 0.90872 | 0.90951 | 0.90032 | 0.89956 | 0.90045 | 0.91509
43602.9212 | 0.90632 | 0.90703 | 0.9113 | 0.9119 | 0.90202 | 0.90134 | 0.90177 | 0.91606
43602.9212 | 0.91086 | 0.91145 | 0.91568 | 0.91679 | 0.90553 | 0.90459 | 0.90543 | 0.91831
43602.9215 | 0.91927 | 0.91951 | 0.9241 | 0.9249 | 0.91623 | 0.91471 | 0.9163 | 0.92516
43602.9215 | 0.91642 | 0.9168 | 0.92152 | 0.9223 | 0.91327 | 0.91195 | 0.91234 | 0.92334
43602.9217 | 0.91981 | 0.92 | 0.92482 | 0.92581 | 0.91655 | 0.91518 | 0.9156 | 0.92535
43602.9217 | 0.92103 | 0.92146 | 0.92582 | 0.92698 | 0.91803 | 0.91632 | 0.91731 | 0.92632
43602.9219 | 0.91464 | 0.91511 | 0.91944 | 0.92049 | 0.91101 | 0.90962 | 0.91005 | 0.9218
43602.9219 | 0.91893 | 0.91926 | 0.92407 | 0.92511 | 0.91497 | 0.91343 | 0.9148 | 0.92435
43602.9222 | 0.92354 | 0.92324 | 0.92795 | 0.92926 | 0.92071 | 0.91913 | 0.91966 | 0.92814
43602.9222 | 0.91926 | 0.91965 | 0.92398 | 0.9253 | 0.91649 | 0.91494 | 0.91538 | 0.92526
43602.9224 | 0.92359 | 0.92341 | 0.92833 | 0.92942 | 0.9201 | 0.91857 | 0.91931 | 0.92767
43602.9224 | 0.92658 | 0.9264 | 0.93139 | 0.93229 | 0.92366 | 0.92187 | 0.92242 | 0.92982
43602.9226 | 0.92564 | 0.92555 | 0.93064 | 0.93109 | 0.92356 | 0.92149 | 0.92206 | 0.92969
43602.9226 | 0.91969 | 0.91982 | 0.92479 | 0.92527 | 0.91807 | 0.91634 | 0.918 | 0.92614
43602.9229 | 0.91308 | 0.91358 | 0.91832 | 0.91867 | 0.91052 | 0.90926 | 0.91028 | 0.92135
43602.9229 | 0.91661 | 0.91708 | 0.92204 | 0.92273 | 0.91307 | 0.91175 | 0.91268 | 0.92302
43602.9231 | 0.91199 | 0.91265 | 0.91696 | 0.91768 | 0.90792 | 0.90662 | 0.90727 | 0.91957
43602.9231 | 0.92162 | 0.92167 | 0.92629 | 0.92732 | 0.91891 | 0.91708 | 0.91745 | 0.92661
43602.9233 | 0.93459 | 0.93415 | 0.93928 | 0.94061 | 0.93232 | 0.92991 | 0.93011 | 0.93532
43602.9233 | 0.93333 | 0.93269 | 0.93821 | 0.93929 | 0.93139 | 0.92944 | 0.92973 | 0.9348
43602.9236 | 0.94059 | 0.93958 | 0.94562 | 0.94653 | 0.93959 | 0.93722 | 0.9374 | 0.94
43602.9236 | 0.94051 | 0.93961 | 0.94549 | 0.94647 | 0.93884 | 0.93629 | 0.937 | 0.93922
43602.9238 | 0.94907 | 0.94738 | 0.95408 | 0.95485 | 0.94818 | 0.94548 | 0.94511 | 0.94532
43602.9238 | 0.94865 | 0.94725 | 0.95371 | 0.95439 | 0.94794 | 0.9452 | 0.94501 | 0.94516
43602.924 | 0.94272 | 0.94157 | 0.94754 | 0.94851 | 0.94084 | 0.93814 | 0.93835 | 0.94051
43602.924 | 0.95135 | 0.94967 | 0.9558 | 0.95686 | 0.9495 | 0.94681 | 0.9469 | 0.94617
43602.9243 | 0.94977 | 0.94831 | 0.95471 | 0.95531 | 0.9492 | 0.94595 | 0.94597 | 0.94586
43602.9243 | 0.94612 | 0.9447 | 0.95128 | 0.95141 | 0.94485 | 0.9421 | 0.94261 | 0.94334
43602.9245 | 0.93769 | 0.93687 | 0.94263 | 0.94296 | 0.93613 | 0.93377 | 0.93391 | 0.93769
43602.9245 | 0.94799 | 0.94634 | 0.95278 | 0.95336 | 0.94617 | 0.94335 | 0.9438 | 0.94401
43602.9247 | 0.9495 | 0.94772 | 0.95425 | 0.95505 | 0.9484 | 0.94556 | 0.94577 | 0.94542
43602.9247 | 0.94637 | 0.9451 | 0.95139 | 0.95166 | 0.94486 | 0.94208 | 0.94213 | 0.94314
43602.925 | 0.9431 | 0.94207 | 0.94796 | 0.9488 | 0.94236 | 0.93965 | 0.93939 | 0.94139
43602.925 | 0.93483 | 0.93393 | 0.93961 | 0.94025 | 0.93306 | 0.93074 | 0.93158 | 0.93563
43602.9252 | 0.93794 | 0.93706 | 0.94272 | 0.94339 | 0.93524 | 0.93265 | 0.93281 | 0.93712
43602.9252 | 0.94292 | 0.94169 | 0.9477 | 0.9484 | 0.94199 | 0.93935 | 0.93944 | 0.94134
43602.9254 | 0.94572 | 0.94431 | 0.95053 | 0.95098 | 0.94446 | 0.94186 | 0.94222 | 0.94291
43602.9254 | 0.93893 | 0.9382 | 0.94406 | 0.94424 | 0.93707 | 0.93475 | 0.93539 | 0.9383
43602.9257 | 0.93639 | 0.93582 | 0.94144 | 0.9421 | 0.93443 | 0.932 | 0.93235 | 0.93649
43602.9257 | 0.93902 | 0.93832 | 0.94442 | 0.94504 | 0.93867 | 0.93629 | 0.93654 | 0.93926
43602.9259 | 0.9417 | 0.94096 | 0.94694 | 0.94751 | 0.93992 | 0.93745 | 0.93787 | 0.94011
43602.9259 | 0.93846 | 0.93809 | 0.94399 | 0.9447 | 0.93709 | 0.93469 | 0.9346 | 0.93818
43602.9261 | 0.93887 | 0.9382 | 0.94424 | 0.94442 | 0.93702 | 0.93443 | 0.93439 | 0.93827
43602.9261 | 0.93928 | 0.93859 | 0.94448 | 0.94501 | 0.93709 | 0.93461 | 0.93503 | 0.93836
43602.9264 | 0.94225 | 0.94121 | 0.94759 | 0.94783 | 0.94148 | 0.93849 | 0.93847 | 0.94094
43602.9264 | 0.94804 | 0.94661 | 0.95318 | 0.95371 | 0.94681 | 0.94376 | 0.94373 | 0.94437
43602.9266 | 0.94916 | 0.94793 | 0.95455 | 0.95498 | 0.9484 | 0.94547 | 0.94554 | 0.94554
43602.9266 | 0.94546 | 0.9441 | 0.95046 | 0.951 | 0.94395 | 0.94146 | 0.9415 | 0.94275
43602.9268 | 0.94944 | 0.948 | 0.95437 | 0.95509 | 0.9477 | 0.94479 | 0.94477 | 0.9451
43602.9268 | 0.95035 | 0.94912 | 0.95559 | 0.95603 | 0.94905 | 0.94602 | 0.94613 | 0.94587
43602.9271 | 0.94566 | 0.94457 | 0.9511 | 0.95143 | 0.9445 | 0.94164 | 0.94221 | 0.94295
43602.9271 | 0.94097 | 0.93998 | 0.94618 | 0.94649 | 0.94014 | 0.93747 | 0.9378 | 0.94013
43602.9273 | 0.95045 | 0.94911 | 0.95575 | 0.95584 | 0.95049 | 0.94707 | 0.94722 | 0.94667
43602.9273 | 0.9495 | 0.94835 | 0.95488 | 0.95511 | 0.94897 | 0.9458 | 0.94566 | 0.94571
43602.9275 | 0.9548 | 0.95332 | 0.96007 | 0.96015 | 0.95403 | 0.95036 | 0.94991 | 0.94881
43602.9275 | 0.95628 | 0.95457 | 0.96131 | 0.96164 | 0.95554 | 0.95229 | 0.95212 | 0.95002
43602.9278 | 0.94728 | 0.94597 | 0.95244 | 0.95286 | 0.94716 | 0.94442 | 0.94447 | 0.94471
43602.9278 | 0.94063 | 0.93964 | 0.94557 | 0.94644 | 0.93956 | 0.9369 | 0.93743 | 0.93985
43602.928 | 0.9513 | 0.94943 | 0.95617 | 0.95639 | 0.95035 | 0.94735 | 0.94756 | 0.94678
43602.928 | 0.94661 | 0.94546 | 0.95182 | 0.95202 | 0.94565 | 0.94296 | 0.94332 | 0.94374
43602.9282 | 0.95684 | 0.95492 | 0.96186 | 0.9622 | 0.9555 | 0.9522 | 0.95222 | 0.95006
43602.9282 | 0.96313 | 0.96089 | 0.96788 | 0.96879 | 0.96225 | 0.95876 | 0.9583 | 0.9543
43602.9285 | 0.97146 | 0.96903 | 0.97688 | 0.97722 | 0.97108 | 0.96744 | 0.96687 | 0.95995
43602.9285 | 0.97443 | 0.9719 | 0.97971 | 0.97953 | 0.97414 | 0.97024 | 0.96959 | 0.96185
43602.9287 | 0.97325 | 0.97061 | 0.97855 | 0.97892 | 0.97323 | 0.9692 | 0.96885 | 0.9612
43602.9287 | 0.97431 | 0.97165 | 0.97963 | 0.97966 | 0.97404 | 0.97015 | 0.96957 | 0.96186
43602.9289 | 0.97846 | 0.9755 | 0.98325 | 0.98359 | 0.97793 | 0.97409 | 0.97338 | 0.96428
43602.9289 | 0.97683 | 0.97432 | 0.98206 | 0.98253 | 0.97694 | 0.97322 | 0.97265 | 0.96381
43602.9292 | 0.9785 | 0.97594 | 0.98392 | 0.98438 | 0.97821 | 0.97412 | 0.9736 | 0.96456
43602.9292 | 0.98159 | 0.97915 | 0.98673 | 0.98751 | 0.98148 | 0.97744 | 0.97675 | 0.96724
43602.9294 | 0.98093 | 0.97845 | 0.98624 | 0.98648 | 0.98113 | 0.97717 | 0.97674 | 0.96719
43602.9294 | 0.97595 | 0.97352 | 0.98124 | 0.98177 | 0.97714 | 0.97315 | 0.9727 | 0.96378
43602.9296 | 0.98255 | 0.98034 | 0.98788 | 0.98859 | 0.98215 | 0.97853 | 0.97773 | 0.96806
43602.9296 | 0.98395 | 0.98158 | 0.98961 | 0.99003 | 0.98416 | 0.98051 | 0.97975 | 0.96994
43602.9299 | 0.97978 | 0.97742 | 0.98531 | 0.98572 | 0.97998 | 0.97622 | 0.9759 | 0.96596
43602.9299 | 0.97357 | 0.97126 | 0.97941 | 0.97942 | 0.97433 | 0.97045 | 0.97049 | 0.96203
43602.9301 | 0.971 | 0.96867 | 0.97621 | 0.97658 | 0.96968 | 0.96579 | 0.96563 | 0.95886
43602.9301 | 0.97978 | 0.97748 | 0.98513 | 0.98551 | 0.97935 | 0.97574 | 0.97496 | 0.96554
43602.9304 | 0.98046 | 0.97764 | 0.98548 | 0.98586 | 0.9804 | 0.97665 | 0.97622 | 0.96614
43602.9303 | 0.9772 | 0.97438 | 0.98233 | 0.98272 | 0.9772 | 0.97365 | 0.97306 | 0.96395
43602.9306 | 0.95856 | 0.95641 | 0.96368 | 0.96395 | 0.95883 | 0.95521 | 0.95576 | 0.95193
43602.9306 | 0.9542 | 0.95264 | 0.95937 | 0.95994 | 0.95349 | 0.95012 | 0.95062 | 0.94867
43602.9308 | 0.97458 | 0.97215 | 0.97971 | 0.98011 | 0.97374 | 0.97002 | 0.96939 | 0.96163
43602.9308 | 0.97447 | 0.97171 | 0.97961 | 0.9802 | 0.97438 | 0.97061 | 0.97013 | 0.96215
43602.9311 | 0.95917 | 0.95673 | 0.96405 | 0.96466 | 0.95848 | 0.95536 | 0.95562 | 0.95198
43602.931 | 0.9548 | 0.95293 | 0.95999 | 0.9607 | 0.95417 | 0.95098 | 0.95136 | 0.94921
43602.9313 | 0.95868 | 0.9566 | 0.96398 | 0.96448 | 0.95659 | 0.95313 | 0.95328 | 0.95062
43602.9313 | 0.96225 | 0.95976 | 0.96712 | 0.96798 | 0.96129 | 0.95779 | 0.95739 | 0.95368
43602.9315 | 0.96452 | 0.96209 | 0.97021 | 0.97054 | 0.96274 | 0.95909 | 0.95901 | 0.95459
43602.9315 | 0.97032 | 0.96814 | 0.97618 | 0.97654 | 0.96999 | 0.96616 | 0.96547 | 0.9592
43602.9318 | 0.98256 | 0.98002 | 0.9883 | 0.98845 | 0.98174 | 0.97779 | 0.97728 | 0.96763
43602.9318 | 0.98408 | 0.9812 | 0.98958 | 0.98988 | 0.98439 | 0.98068 | 0.97987 | 0.97025
43602.932 | 0.98429 | 0.9814 | 0.98964 | 0.98979 | 0.98441 | 0.98047 | 0.97988 | 0.97035
43602.932 | 0.98192 | 0.97899 | 0.98715 | 0.98759 | 0.98127 | 0.97738 | 0.97701 | 0.96723
43602.9322 | 0.98186 | 0.97894 | 0.98708 | 0.98721 | 0.98051 | 0.97684 | 0.97641 | 0.96658
43602.9322 | 0.98426 | 0.98154 | 0.98965 | 0.9901 | 0.98424 | 0.98037 | 0.97988 | 0.97024
43602.9325 | 0.98468 | 0.98193 | 0.98983 | 0.9903 | 0.98451 | 0.98056 | 0.98031 | 0.97049
43602.9325 | 0.97847 | 0.97566 | 0.98374 | 0.98415 | 0.97804 | 0.9743 | 0.97424 | 0.96456
43602.9327 | 0.9835 | 0.98046 | 0.98862 | 0.98892 | 0.98208 | 0.97812 | 0.97803 | 0.96803
43602.9327 | 0.98686 | 0.98426 | 0.99231 | 0.99238 | 0.98642 | 0.98258 | 0.982 | 0.97231
43602.933 | 0.99035 | 0.98781 | 0.99597 | 0.99642 | 0.98967 | 0.98564 | 0.98516 | 0.9757
43602.933 | 0.995 | 0.99227 | 1.0003 | 1.0007 | 0.99509 | 0.99118 | 0.9904 | 0.98084
43602.9332 | 0.98978 | 0.98695 | 0.99508 | 0.99548 | 0.9905 | 0.98645 | 0.98575 | 0.97644
43602.9332 | 0.98498 | 0.98246 | 0.99053 | 0.99064 | 0.98631 | 0.98233 | 0.98162 | 0.97215
43602.9334 | 0.99425 | 0.99133 | 0.99945 | 1.0001 | 0.99411 | 0.9903 | 0.98956 | 0.97988
43602.9334 | 0.99099 | 0.98834 | 0.99638 | 0.99697 | 0.99167 | 0.9876 | 0.98685 | 0.97721
43602.9337 | 0.98438 | 0.98148 | 0.98987 | 0.99008 | 0.98343 | 0.97942 | 0.97898 | 0.96933
43602.9337 | 0.98849 | 0.98563 | 0.99386 | 0.99433 | 0.98879 | 0.98467 | 0.98422 | 0.97454
43602.9339 | 0.99528 | 0.99277 | 1.0009 | 1.0011 | 0.99514 | 0.9912 | 0.99058 | 0.98109
43602.9339 | 0.99519 | 0.99255 | 1.0007 | 1.0012 | 0.99539 | 0.9913 | 0.99075 | 0.98109
43602.9342 | 0.99112 | 0.98856 | 0.99662 | 0.99698 | 0.99103 | 0.98692 | 0.98632 | 0.97674
43602.9342 | 0.99699 | 0.99425 | 1.0026 | 1.0029 | 0.99694 | 0.99312 | 0.99237 | 0.98278
43602.9344 | 0.99202 | 0.98931 | 0.99786 | 0.99794 | 0.99307 | 0.98886 | 0.98851 | 0.97898
43602.9344 | 0.98257 | 0.98002 | 0.98864 | 0.98871 | 0.9832 | 0.97916 | 0.97872 | 0.96896
43602.9346 | 0.99352 | 0.99092 | 0.99916 | 0.99958 | 0.9931 | 0.98881 | 0.98837 | 0.97895
43602.9346 | 0.99418 | 0.99163 | 0.99992 | 1.0002 | 0.99417 | 0.99018 | 0.98954 | 0.9803
43602.9349 | 1.0003 | 0.99753 | 1.0053 | 1.0057 | 1.0005 | 0.99638 | 0.99575 | 0.98644
43602.9349 | 0.99925 | 0.99639 | 1.0047 | 1.0051 | 0.99947 | 0.99563 | 0.99494 | 0.98552
43602.9351 | 0.99553 | 0.99277 | 1.001 | 1.0014 | 0.99586 | 0.99207 | 0.99155 | 0.98174
43602.9351 | 0.99894 | 0.99635 | 1.0048 | 1.0046 | 0.99848 | 0.99445 | 0.99402 | 0.9845
43602.9353 | 1 | 0.99748 | 1.0057 | 1.0059 | 1.0002 | 0.99624 | 0.99546 | 0.98625
43602.9353 | 0.99493 | 0.99204 | 1.0003 | 1.0008 | 0.99479 | 0.99103 | 0.9904 | 0.98089
43602.9356 | 0.99937 | 0.99657 | 1.0048 | 1.0049 | 0.99916 | 0.99545 | 0.99505 | 0.9854
43602.9356 | 0.995 | 0.9925 | 1.0007 | 1.0007 | 0.99604 | 0.99241 | 0.99178 | 0.98214
43602.9358 | 1.0026 | 0.99986 | 1.0085 | 1.0083 | 1.0019 | 0.99799 | 0.9974 | 0.98781
43602.9358 | 1.0044 | 1.0018 | 1.0102 | 1.01 | 1.0046 | 1.0006 | 1.0001 | 0.99049
43602.9361 | 1.0018 | 0.99934 | 1.0077 | 1.0079 | 1.0011 | 0.99731 | 0.99642 | 0.98684
43602.936 | 1.0041 | 1.0018 | 1.0098 | 1.01 | 1.0046 | 1.0006 | 0.99991 | 0.99029
43602.9363 | 0.9972 | 0.99468 | 1.0027 | 1.0029 | 0.99811 | 0.99429 | 0.99361 | 0.98405
43602.9363 | 0.98958 | 0.98707 | 0.9952 | 0.99567 | 0.99057 | 0.98677 | 0.98612 | 0.97644
43602.9365 | 0.99828 | 0.99564 | 1.004 | 1.004 | 0.99893 | 0.99489 | 0.99434 | 0.98449
43602.9365 | 0.99258 | 0.99002 | 0.99811 | 0.99837 | 0.99316 | 0.98917 | 0.98847 | 0.97903
43602.9368 | 1.0012 | 0.99863 | 1.0068 | 1.0072 | 1.0021 | 0.99813 | 0.99752 | 0.98802
43602.9368 | 0.99631 | 0.99351 | 1.0018 | 1.0021 | 0.99738 | 0.9934 | 0.99272 | 0.98292
43602.937 | 0.98568 | 0.98288 | 0.99116 | 0.99144 | 0.98412 | 0.98025 | 0.97965 | 0.96996
43602.937 | 0.99431 | 0.9916 | 1.0002 | 1.0002 | 0.99339 | 0.98955 | 0.98904 | 0.97944
43602.9372 | 0.9894 | 0.98636 | 0.99491 | 0.99522 | 0.98962 | 0.98559 | 0.98507 | 0.97546
43602.9372 | 0.98603 | 0.98326 | 0.99181 | 0.99237 | 0.98636 | 0.9824 | 0.98185 | 0.9721
43602.9375 | 0.98951 | 0.98675 | 0.99491 | 0.99565 | 0.9909 | 0.98685 | 0.98642 | 0.97666
43602.9375 | 0.98266 | 0.98006 | 0.98828 | 0.98886 | 0.98353 | 0.9794 | 0.97885 | 0.96913
43602.9377 | 0.98594 | 0.983 | 0.99136 | 0.99182 | 0.98589 | 0.98187 | 0.98132 | 0.97177
43602.9377 | 0.98412 | 0.98123 | 0.98989 | 0.99018 | 0.98476 | 0.98083 | 0.98007 | 0.97065
43602.938 | 0.98401 | 0.98113 | 0.98922 | 0.98974 | 0.98281 | 0.97909 | 0.97835 | 0.96882
43602.938 | 0.98471 | 0.98198 | 0.99005 | 0.99032 | 0.98396 | 0.98028 | 0.97941 | 0.96972
43602.9382 | 0.97755 | 0.97458 | 0.98276 | 0.98286 | 0.97765 | 0.97385 | 0.97309 | 0.96404
43602.9382 | 0.97493 | 0.972 | 0.98064 | 0.98031 | 0.97445 | 0.97084 | 0.97015 | 0.96206
43602.9384 | 0.96945 | 0.96694 | 0.97518 | 0.97506 | 0.9697 | 0.96599 | 0.96562 | 0.95908
43602.9384 | 0.97953 | 0.97686 | 0.98494 | 0.98535 | 0.97835 | 0.97448 | 0.97393 | 0.96473
43602.9387 | 0.99318 | 0.99074 | 0.99894 | 0.99897 | 0.99288 | 0.98878 | 0.98841 | 0.97862
43602.9387 | 0.9946 | 0.99211 | 1.0007 | 1.0006 | 0.99414 | 0.99003 | 0.98957 | 0.98009
43602.9389 | 1.0097 | 1.0073 | 1.0151 | 1.0153 | 1.0101 | 1.0062 | 1.0056 | 0.99599
43602.9389 | 1.008 | 1.0055 | 1.0138 | 1.014 | 1.0082 | 1.0042 | 1.0037 | 0.99426
43602.9392 | 0.99901 | 0.99649 | 1.0046 | 1.0047 | 1.0001 | 0.99601 | 0.99525 | 0.98576
43602.9392 | 0.99072 | 0.98834 | 0.99598 | 0.99651 | 0.99133 | 0.98705 | 0.98645 | 0.97686
43602.9394 | 1.0004 | 0.99783 | 1.0058 | 1.0061 | 0.99957 | 0.99555 | 0.99477 | 0.98525
43602.9394 | 1.0056 | 1.003 | 1.011 | 1.0111 | 1.005 | 1.001 | 1.0002 | 0.99072
43602.9396 | 1.0125 | 1.0099 | 1.0183 | 1.0183 | 1.0126 | 1.0086 | 1.0078 | 0.99847
43602.9396 | 1.0093 | 1.007 | 1.015 | 1.0153 | 1.0109 | 1.0068 | 1.0061 | 0.99636
43602.9399 | 0.99346 | 0.9909 | 0.99882 | 0.99899 | 0.99421 | 0.99028 | 0.98951 | 0.98014
43602.9399 | 0.99133 | 0.98874 | 0.99674 | 0.99691 | 0.99204 | 0.9881 | 0.98756 | 0.97799
43602.9401 | 0.99863 | 0.99602 | 1.0038 | 1.0041 | 0.99909 | 0.99502 | 0.99433 | 0.98472
43602.9401 | 1.002 | 0.99906 | 1.0075 | 1.0075 | 1.0008 | 0.99693 | 0.99638 | 0.98702
43602.9404 | 1.0048 | 1.0019 | 1.0103 | 1.0103 | 1.0049 | 1.0009 | 1.0002 | 0.99074
43602.9404 | 1.0001 | 0.99752 | 1.0057 | 1.0058 | 1 | 0.99624 | 0.99548 | 0.98609
43602.9406 | 0.98675 | 0.98418 | 0.99244 | 0.9924 | 0.98717 | 0.98332 | 0.98259 | 0.97318
43602.9406 | 0.98712 | 0.9847 | 0.99241 | 0.9929 | 0.98582 | 0.9818 | 0.98116 | 0.97169
43602.9408 | 0.99171 | 0.98951 | 0.9973 | 0.99786 | 0.99249 | 0.98854 | 0.98792 | 0.97848
43602.9408 | 0.99086 | 0.9883 | 0.99657 | 0.99707 | 0.99143 | 0.9875 | 0.98698 | 0.97746
43602.9411 | 0.99378 | 0.99149 | 0.99967 | 1.0001 | 0.99282 | 0.98854 | 0.98822 | 0.97871
43602.9411 | 0.99395 | 0.99182 | 1.0002 | 1.0006 | 0.99375 | 0.98972 | 0.98933 | 0.97968
43602.9413 | 1.0019 | 0.99948 | 1.0075 | 1.0083 | 1.0015 | 0.99767 | 0.99698 | 0.98731
43602.9413 | 1.0066 | 1.0045 | 1.0128 | 1.0132 | 1.006 | 1.0023 | 1.0015 | 0.99195
43602.9416 | 1.0121 | 1.0099 | 1.0178 | 1.0184 | 1.0128 | 1.0087 | 1.0081 | 0.99858
43602.9415 | 1.009 | 1.0065 | 1.0151 | 1.0151 | 1.0094 | 1.0055 | 1.0049 | 0.9953
43602.9418 | 1.0018 | 0.99921 | 1.0079 | 1.0079 | 1.0012 | 0.99702 | 0.99653 | 0.98684
43602.9418 | 1.0014 | 0.99888 | 1.0073 | 1.0075 | 1.0006 | 0.99643 | 0.99597 | 0.98644
43602.942 | 1.0043 | 1.0018 | 1.0099 | 1.0106 | 1.0041 | 0.99991 | 0.99922 | 0.98998
43602.942 | 1.0064 | 1.0036 | 1.0119 | 1.0123 | 1.0057 | 1.0016 | 1.0012 | 0.99158
43602.9423 | 1.0135 | 1.0112 | 1.0191 | 1.0196 | 1.0142 | 1.0103 | 1.0098 | 1.0003
43602.9423 | 1.0167 | 1.0145 | 1.0224 | 1.0228 | 1.0168 | 1.0126 | 1.0121 | 1.0027
43602.9425 | 1.0096 | 1.0071 | 1.0154 | 1.0156 | 1.0101 | 1.0062 | 1.0057 | 0.99632
43602.9425 | 1.0004 | 0.99764 | 1.0058 | 1.0064 | 1.0007 | 0.99682 | 0.99637 | 0.98667
43602.9427 | 1.0066 | 1.0042 | 1.0127 | 1.0126 | 1.0055 | 1.0016 | 1.0012 | 0.99153
43602.9427 | 1.0087 | 1.0059 | 1.0143 | 1.0144 | 1.0081 | 1.0042 | 1.0036 | 0.99415
43602.943 | 1.0095 | 1.0071 | 1.0149 | 1.0156 | 1.0091 | 1.0052 | 1.0047 | 0.99486
43602.943 | 1.0124 | 1.0099 | 1.0183 | 1.0188 | 1.0119 | 1.0081 | 1.0075 | 0.9979
43602.9432 | 1.0116 | 1.009 | 1.0173 | 1.0178 | 1.0117 | 1.0075 | 1.0069 | 0.99762
43602.9432 | 1.0062 | 1.0036 | 1.0121 | 1.0122 | 1.007 | 1.0028 | 1.0025 | 0.993
43602.9435 | 1.0096 | 1.0076 | 1.0155 | 1.016 | 1.0096 | 1.0057 | 1.005 | 0.99553
43602.9435 | 1.0113 | 1.0089 | 1.0168 | 1.0174 | 1.0112 | 1.0075 | 1.007 | 0.99725
43602.9437 | 1.01 | 1.0073 | 1.0158 | 1.016 | 1.0099 | 1.0059 | 1.0054 | 0.99586
43602.9437 | 1.0128 | 1.0098 | 1.0186 | 1.0191 | 1.0126 | 1.0086 | 1.0081 | 0.99838
43602.944 | 1.0128 | 1.0101 | 1.0185 | 1.0188 | 1.0126 | 1.0087 | 1.0083 | 0.9988
43602.944 | 1.0065 | 1.0039 | 1.0124 | 1.0125 | 1.0063 | 1.0025 | 1.002 | 0.99241
43602.9442 | 1.011 | 1.0081 | 1.0165 | 1.017 | 1.0103 | 1.0064 | 1.0057 | 0.9964
43602.9442 | 1.0076 | 1.005 | 1.0132 | 1.0136 | 1.0072 | 1.0031 | 1.0026 | 0.99335
43602.9444 | 1.0032 | 1.0009 | 1.0091 | 1.0097 | 1.0039 | 0.99975 | 0.9996 | 0.98999
43602.9444 | 1.0042 | 1.0015 | 1.0096 | 1.0106 | 1.0043 | 1.0003 | 0.9996 | 0.99034
43602.9447 | 1.006 | 1.0034 | 1.0116 | 1.0117 | 1.0058 | 1.0023 | 1.0014 | 0.99206
43602.9447 | 1.0085 | 1.006 | 1.0142 | 1.0145 | 1.0092 | 1.0053 | 1.0048 | 0.99511
43602.9449 | 1.0033 | 1.0009 | 1.009 | 1.0095 | 1.0034 | 0.99973 | 0.99924 | 0.98951
43602.9449 | 1.0041 | 1.0018 | 1.0101 | 1.0103 | 1.0047 | 1.001 | 1.0006 | 0.99077
43602.9452 | 0.9991 | 0.99708 | 1.0051 | 1.0053 | 0.99887 | 0.99512 | 0.99465 | 0.98507
43602.9452 | 1.0032 | 1.0006 | 1.0089 | 1.0092 | 1.0023 | 0.99822 | 0.99769 | 0.98803
43602.9454 | 1.0046 | 1.0021 | 1.0107 | 1.0106 | 1.0046 | 1.0007 | 1.0005 | 0.99089
43602.9454 | 0.99903 | 0.99634 | 1.0045 | 1.0048 | 0.99966 | 0.99566 | 0.99525 | 0.98581
43602.9456 | 1.0001 | 0.99722 | 1.0057 | 1.0059 | 0.99904 | 0.99474 | 0.99438 | 0.98492
43602.9456 | 1.0022 | 0.99951 | 1.0077 | 1.0084 | 1.0023 | 0.99816 | 0.99773 | 0.98822
43602.9459 | 0.99838 | 0.99568 | 1.0035 | 1.0047 | 0.99893 | 0.99496 | 0.99451 | 0.98494
43602.9459 | 0.99761 | 0.99471 | 1.0032 | 1.0038 | 0.99712 | 0.99339 | 0.99259 | 0.98314
43602.9461 | 0.99772 | 0.99499 | 1.0033 | 1.0042 | 0.99841 | 0.99431 | 0.99406 | 0.9844
43602.9461 | 0.99695 | 0.99435 | 1.0027 | 1.0031 | 0.99733 | 0.99311 | 0.9925 | 0.98323
43602.9464 | 0.99774 | 0.99498 | 1.0031 | 1.0038 | 0.99679 | 0.9927 | 0.99207 | 0.9825
43602.9463 | 0.99885 | 0.99629 | 1.0042 | 1.0048 | 0.99873 | 0.99485 | 0.9941 | 0.98505
43602.9466 | 0.9938 | 0.99117 | 0.99961 | 0.99997 | 0.99388 | 0.99009 | 0.98944 | 0.97998
43602.9466 | 0.99594 | 0.99339 | 1.0016 | 1.0023 | 0.99476 | 0.99084 | 0.99021 | 0.98085
43602.9468 | 0.99482 | 0.99221 | 1.0004 | 1.0008 | 0.99494 | 0.99123 | 0.99043 | 0.98103
43602.9468 | 0.99454 | 0.99214 | 1.0003 | 1.0008 | 0.99399 | 0.99022 | 0.98958 | 0.9802
43602.9471 | 0.99673 | 0.99401 | 1.002 | 1.0027 | 0.99651 | 0.99236 | 0.99187 | 0.98251
43602.9471 | 0.99593 | 0.99301 | 1.0012 | 1.0018 | 0.9963 | 0.99244 | 0.99179 | 0.9823
43602.9473 | 0.99344 | 0.99092 | 0.99914 | 0.99985 | 0.99229 | 0.98838 | 0.98766 | 0.97842
43602.9473 | 0.99395 | 0.99109 | 0.99934 | 0.99979 | 0.99434 | 0.99046 | 0.98986 | 0.9805
43602.9476 | 0.99252 | 0.9898 | 0.99814 | 0.99882 | 0.9921 | 0.98814 | 0.98718 | 0.97774
43602.9475 | 0.99304 | 0.99064 | 0.99888 | 0.99933 | 0.99253 | 0.9884 | 0.98785 | 0.97838
43602.9478 | 0.98983 | 0.98754 | 0.99578 | 0.996 | 0.99059 | 0.9864 | 0.98608 | 0.97665
43602.9478 | 0.98833 | 0.98616 | 0.99453 | 0.99483 | 0.98773 | 0.98383 | 0.9831 | 0.97359
43602.948 | 0.99038 | 0.98779 | 0.99629 | 0.99672 | 0.99087 | 0.98684 | 0.98625 | 0.97687
43602.948 | 0.99005 | 0.98775 | 0.99607 | 0.99658 | 0.98944 | 0.98562 | 0.98498 | 0.97546
43602.9483 | 0.99101 | 0.98815 | 0.99691 | 0.99692 | 0.99097 | 0.98715 | 0.98647 | 0.97718
43602.9483 | 0.99002 | 0.98722 | 0.99572 | 0.99659 | 0.98992 | 0.98619 | 0.98555 | 0.976
43602.9485 | 0.99059 | 0.98794 | 0.99645 | 0.99662 | 0.99061 | 0.98665 | 0.98603 | 0.9766
43602.9485 | 0.99313 | 0.99029 | 0.99874 | 0.99906 | 0.99305 | 0.98915 | 0.98851 | 0.97899
43602.9488 | 0.98748 | 0.98471 | 0.99311 | 0.99354 | 0.98739 | 0.98415 | 0.9834 | 0.97357
43602.9487 | 0.98558 | 0.98251 | 0.99113 | 0.99145 | 0.98467 | 0.98134 | 0.98052 | 0.97076
43602.949 | 0.98638 | 0.98404 | 0.99204 | 0.99259 | 0.98652 | 0.98292 | 0.98221 | 0.97232
43602.949 | 0.98602 | 0.98338 | 0.99188 | 0.99205 | 0.98542 | 0.9816 | 0.98077 | 0.97133
43602.9492 | 0.98494 | 0.98224 | 0.99071 | 0.99068 | 0.98501 | 0.98108 | 0.98057 | 0.97094
43602.9492 | 0.98535 | 0.9828 | 0.9913 | 0.99111 | 0.98447 | 0.98028 | 0.98018 | 0.97041
43602.9495 | 0.98545 | 0.98287 | 0.99128 | 0.99149 | 0.98587 | 0.98178 | 0.98145 | 0.97194
43602.9495 | 0.98481 | 0.9823 | 0.99092 | 0.99101 | 0.98431 | 0.98011 | 0.97977 | 0.9702
43602.9497 | 0.9883 | 0.98563 | 0.99443 | 0.99475 | 0.9875 | 0.98365 | 0.98304 | 0.97356
43602.9497 | 0.98866 | 0.98592 | 0.99467 | 0.99484 | 0.98937 | 0.98534 | 0.98498 | 0.97538
43602.95 | 0.98247 | 0.97954 | 0.98831 | 0.98832 | 0.98159 | 0.97765 | 0.97728 | 0.96772
43602.9499 | 0.9824 | 0.97962 | 0.98823 | 0.98848 | 0.98288 | 0.97878 | 0.97832 | 0.96863
43602.9502 | 0.98404 | 0.98119 | 0.98996 | 0.98977 | 0.98283 | 0.97892 | 0.9785 | 0.96885
43602.9502 | 0.9834 | 0.9805 | 0.98926 | 0.9894 | 0.98329 | 0.97942 | 0.9789 | 0.96928
43602.9504 | 0.98303 | 0.98023 | 0.98888 | 0.98905 | 0.98208 | 0.97831 | 0.9778 | 0.9682
43602.9504 | 0.98034 | 0.97759 | 0.98666 | 0.98653 | 0.98038 | 0.97645 | 0.9758 | 0.9664
43602.9507 | 0.98224 | 0.97971 | 0.98854 | 0.98842 | 0.98221 | 0.97832 | 0.97769 | 0.96832
43602.9507 | 0.98022 | 0.97737 | 0.98608 | 0.98623 | 0.98029 | 0.97604 | 0.97564 | 0.96612
43602.9509 | 0.98048 | 0.97768 | 0.98631 | 0.98647 | 0.98015 | 0.97611 | 0.97561 | 0.96625
43602.9509 | 0.97885 | 0.97598 | 0.9847 | 0.98496 | 0.9787 | 0.9746 | 0.97422 | 0.9648
43602.9512 | 0.97936 | 0.97655 | 0.98536 | 0.98583 | 0.98 | 0.97594 | 0.97539 | 0.96594
43602.9512 | 0.97723 | 0.97411 | 0.98304 | 0.98337 | 0.97702 | 0.97288 | 0.97229 | 0.96362
43602.9514 | 0.97887 | 0.97606 | 0.98463 | 0.98518 | 0.97909 | 0.97496 | 0.97453 | 0.9651
43602.9514 | 0.97821 | 0.97534 | 0.98416 | 0.98482 | 0.97776 | 0.97373 | 0.97311 | 0.96427
43602.9516 | 0.97669 | 0.97361 | 0.98263 | 0.98279 | 0.97629 | 0.97233 | 0.97163 | 0.96329
43602.9516 | 0.9795 | 0.97686 | 0.98547 | 0.9856 | 0.97924 | 0.97536 | 0.97482 | 0.96516
43602.9519 | 0.98069 | 0.97776 | 0.9868 | 0.98669 | 0.98065 | 0.97688 | 0.97636 | 0.96666
43602.9519 | 0.97783 | 0.97515 | 0.9838 | 0.98395 | 0.97728 | 0.9735 | 0.97299 | 0.96385
43602.9521 | 0.97634 | 0.9737 | 0.98219 | 0.9825 | 0.97612 | 0.97212 | 0.97166 | 0.96307
43602.9521 | 0.98299 | 0.98023 | 0.98896 | 0.9892 | 0.98167 | 0.97785 | 0.97742 | 0.96766
43602.9524 | 0.98432 | 0.98157 | 0.99011 | 0.99027 | 0.98416 | 0.98059 | 0.97991 | 0.97018
43602.9524 | 0.98451 | 0.98162 | 0.9903 | 0.99065 | 0.98437 | 0.9806 | 0.97995 | 0.97018
43602.9526 | 0.99253 | 0.98966 | 0.99808 | 0.99852 | 0.99128 | 0.98763 | 0.98699 | 0.97715
43602.9526 | 0.99715 | 0.9943 | 1.0027 | 1.0035 | 0.99639 | 0.99255 | 0.99208 | 0.9822
43602.9528 | 1.0085 | 1.0053 | 1.0142 | 1.0146 | 1.0077 | 1.0037 | 1.0032 | 0.99353
43602.9528 | 1.0096 | 1.0064 | 1.0157 | 1.0157 | 1.009 | 1.0053 | 1.0046 | 0.99482
43602.9531 | 1.0096 | 1.0067 | 1.0158 | 1.0159 | 1.0091 | 1.0054 | 1.0046 | 0.99513
43602.9531 | 1.0026 | 0.99986 | 1.0089 | 1.0092 | 1.0028 | 0.99895 | 0.99826 | 0.98873
43602.9533 | 0.99079 | 0.98754 | 0.99657 | 0.99671 | 0.99115 | 0.9875 | 0.98679 | 0.97702
43602.9533 | 0.98652 | 0.98379 | 0.99254 | 0.99288 | 0.98639 | 0.9826 | 0.98203 | 0.97225
43602.9536 | 0.97767 | 0.97514 | 0.98381 | 0.98441 | 0.97807 | 0.97423 | 0.97362 | 0.96442
43602.9536 | 0.97777 | 0.9754 | 0.98421 | 0.98461 | 0.97654 | 0.97262 | 0.97226 | 0.96345
43602.9538 | 0.99238 | 0.98984 | 0.99881 | 0.99942 | 0.9919 | 0.98773 | 0.98737 | 0.97782
43602.9538 | 0.98733 | 0.98474 | 0.99338 | 0.9939 | 0.9874 | 0.98329 | 0.98282 | 0.97321
43602.9541 | 0.97463 | 0.972 | 0.98078 | 0.98113 | 0.97532 | 0.97147 | 0.9709 | 0.96273
43602.954 | 0.96917 | 0.96698 | 0.9755 | 0.97606 | 0.96973 | 0.96566 | 0.96523 | 0.95896
43602.9543 | 0.9858 | 0.98295 | 0.99136 | 0.99212 | 0.98301 | 0.979 | 0.97858 | 0.96902
43602.9543 | 0.9889 | 0.98648 | 0.99469 | 0.99523 | 0.98867 | 0.98482 | 0.98429 | 0.97454
43602.9545 | 0.9727 | 0.97013 | 0.97895 | 0.97976 | 0.97311 | 0.96905 | 0.96867 | 0.96112
43602.9545 | 0.96569 | 0.96311 | 0.97184 | 0.9721 | 0.96583 | 0.96179 | 0.96152 | 0.9564
43602.9548 | 0.96385 | 0.96149 | 0.9697 | 0.96998 | 0.96275 | 0.95875 | 0.95867 | 0.95431
43602.9548 | 0.9799 | 0.97732 | 0.98579 | 0.98646 | 0.97857 | 0.97429 | 0.97397 | 0.96454
43602.955 | 0.97206 | 0.96941 | 0.97812 | 0.97854 | 0.97205 | 0.96828 | 0.96775 | 0.96056
43602.955 | 0.9655 | 0.96315 | 0.97148 | 0.97218 | 0.96548 | 0.96169 | 0.96141 | 0.95622
43602.9553 | 0.95465 | 0.9528 | 0.96056 | 0.96117 | 0.954 | 0.95062 | 0.95062 | 0.94893
43602.9553 | 0.96509 | 0.96233 | 0.97074 | 0.9714 | 0.96186 | 0.95831 | 0.95802 | 0.95403
43602.9555 | 0.97301 | 0.96985 | 0.97881 | 0.97911 | 0.97225 | 0.96828 | 0.96814 | 0.96055
43602.9555 | 0.96889 | 0.96605 | 0.97478 | 0.97502 | 0.96835 | 0.96442 | 0.96405 | 0.95799
43602.9558 | 0.96528 | 0.96255 | 0.97106 | 0.97172 | 0.96389 | 0.9601 | 0.95997 | 0.95516
43602.9558 | 0.98316 | 0.98024 | 0.98915 | 0.98966 | 0.98322 | 0.97925 | 0.97893 | 0.96898
43602.9561 | 0.96613 | 0.96336 | 0.97225 | 0.97247 | 0.96633 | 0.96224 | 0.96206 | 0.95676
43602.9561 | 0.95907 | 0.95656 | 0.9648 | 0.96492 | 0.95858 | 0.95463 | 0.9549 | 0.95163
43602.9563 | 0.96691 | 0.9639 | 0.97306 | 0.97327 | 0.96398 | 0.96016 | 0.95975 | 0.95509
43602.9563 | 0.97073 | 0.96758 | 0.97707 | 0.97715 | 0.97066 | 0.96682 | 0.96624 | 0.95959
43602.9566 | 0.95936 | 0.95683 | 0.96506 | 0.96543 | 0.95888 | 0.95531 | 0.95497 | 0.95197
43602.9566 | 0.95272 | 0.9508 | 0.95869 | 0.95925 | 0.95205 | 0.94832 | 0.94868 | 0.94756
43602.9568 | 0.94315 | 0.94141 | 0.94903 | 0.94935 | 0.94169 | 0.93838 | 0.93897 | 0.94081
43602.9568 | 0.93951 | 0.93858 | 0.94591 | 0.94599 | 0.93792 | 0.93522 | 0.93554 | 0.9386
43602.9571 | 0.93402 | 0.93338 | 0.94062 | 0.94065 | 0.9322 | 0.92957 | 0.93031 | 0.93479
43602.9571 | 0.93438 | 0.93346 | 0.94068 | 0.94095 | 0.93208 | 0.9295 | 0.93043 | 0.93483
43602.9573 | 0.96756 | 0.96519 | 0.97417 | 0.9744 | 0.96607 | 0.96192 | 0.96198 | 0.95659
43602.9573 | 0.96966 | 0.9671 | 0.97617 | 0.97656 | 0.96993 | 0.96587 | 0.96554 | 0.95897
43602.9576 | 0.95657 | 0.95448 | 0.96301 | 0.96316 | 0.95629 | 0.95259 | 0.95286 | 0.95025
43602.9576 | 0.94997 | 0.94872 | 0.95667 | 0.9571 | 0.9492 | 0.94583 | 0.94622 | 0.94583
43602.9578 | 0.95769 | 0.95572 | 0.96432 | 0.96422 | 0.9562 | 0.95243 | 0.95266 | 0.95027
43602.9578 | 0.9601 | 0.9578 | 0.96639 | 0.96632 | 0.95927 | 0.95563 | 0.95578 | 0.95233
43602.9581 | 0.94972 | 0.94787 | 0.95561 | 0.95588 | 0.94859 | 0.94533 | 0.94566 | 0.94526
43602.9581 | 0.94356 | 0.94237 | 0.94999 | 0.95015 | 0.94202 | 0.93928 | 0.9398 | 0.9412
43602.9583 | 0.93586 | 0.93494 | 0.94191 | 0.94282 | 0.93358 | 0.93126 | 0.93209 | 0.936
43602.9583 | 0.93273 | 0.93178 | 0.93881 | 0.93923 | 0.93046 | 0.9281 | 0.92896 | 0.93365
43602.9586 | 0.92832 | 0.92751 | 0.93408 | 0.93472 | 0.92563 | 0.92321 | 0.92453 | 0.93061
43602.9586 | 0.92843 | 0.92749 | 0.9346 | 0.93501 | 0.92487 | 0.9228 | 0.92393 | 0.93031
43602.9588 | 0.92537 | 0.92492 | 0.93164 | 0.93177 | 0.9224 | 0.92036 | 0.92175 | 0.92876
43602.9588 | 0.92362 | 0.92371 | 0.92998 | 0.93064 | 0.9209 | 0.91892 | 0.92032 | 0.92768
43602.9591 | 0.92049 | 0.92023 | 0.92641 | 0.92716 | 0.91692 | 0.91532 | 0.91679 | 0.92539
43602.9591 | 0.9191 | 0.91897 | 0.92522 | 0.92554 | 0.91546 | 0.91379 | 0.91525 | 0.92439
43602.9593 | 0.9152 | 0.91526 | 0.92161 | 0.92198 | 0.91164 | 0.91023 | 0.91192 | 0.92189
43602.9593 | 0.91366 | 0.91382 | 0.91992 | 0.92042 | 0.90994 | 0.90853 | 0.91011 | 0.9209
43602.9596 | 0.91046 | 0.91094 | 0.91714 | 0.9174 | 0.90689 | 0.90548 | 0.90736 | 0.91895
43602.9596 | 0.90952 | 0.91002 | 0.9159 | 0.91592 | 0.90568 | 0.90416 | 0.90601 | 0.918
43602.9598 | 0.90696 | 0.90764 | 0.91375 | 0.91366 | 0.90324 | 0.90203 | 0.90365 | 0.91654
43602.9598 | 0.9061 | 0.90679 | 0.91257 | 0.91262 | 0.90209 | 0.90081 | 0.90301 | 0.91585
43602.9601 | 0.9042 | 0.90483 | 0.91094 | 0.91076 | 0.90005 | 0.89889 | 0.90059 | 0.91464
43602.9601 | 0.90311 | 0.90402 | 0.90993 | 0.90999 | 0.89922 | 0.89801 | 0.90011 | 0.91398
43602.9603 | 0.90141 | 0.90232 | 0.90778 | 0.90795 | 0.89723 | 0.89633 | 0.89815 | 0.91273
43602.9603 | 0.90059 | 0.90148 | 0.90704 | 0.90711 | 0.8962 | 0.89548 | 0.89767 | 0.91214
43602.9606 | 0.89909 | 0.8998 | 0.90522 | 0.90562 | 0.89455 | 0.8937 | 0.89557 | 0.91093
43602.9605 | 0.89827 | 0.89912 | 0.90454 | 0.9049 | 0.89368 | 0.89303 | 0.89501 | 0.91032
43602.9608 | 0.89678 | 0.89754 | 0.90299 | 0.90336 | 0.892 | 0.89127 | 0.89343 | 0.90926
43602.9608 | 0.89634 | 0.89723 | 0.90275 | 0.90305 | 0.89129 | 0.89062 | 0.8927 | 0.90886
43602.9611 | 0.97144 | 0.96852 | 0.97775 | 0.97788 | 0.96782 | 0.9638 | 0.96356 | 0.95765
43602.961 | 0.98028 | 0.9773 | 0.98643 | 0.98654 | 0.97873 | 0.97493 | 0.97418 | 0.96472
43602.9613 | 0.99192 | 0.98894 | 0.99821 | 0.99819 | 0.99134 | 0.98723 | 0.98649 | 0.97657
43602.9613 | 0.99295 | 0.9899 | 0.99904 | 0.99961 | 0.99254 | 0.98881 | 0.98818 | 0.97818
43602.9616 | 0.98689 | 0.98389 | 0.99303 | 0.99305 | 0.98699 | 0.98304 | 0.98254 | 0.97232
43602.9615 | 0.97989 | 0.97671 | 0.98626 | 0.98659 | 0.97969 | 0.97607 | 0.97532 | 0.96509
43602.9618 | 0.96801 | 0.96516 | 0.97424 | 0.9744 | 0.96777 | 0.96409 | 0.96377 | 0.95749
43602.9618 | 0.96165 | 0.95879 | 0.96765 | 0.96797 | 0.9611 | 0.95746 | 0.95721 | 0.95314
43602.9621 | 0.95489 | 0.95298 | 0.96115 | 0.9613 | 0.9533 | 0.94993 | 0.94996 | 0.94812
43602.962 | 0.96663 | 0.96399 | 0.97297 | 0.97348 | 0.96476 | 0.9611 | 0.96067 | 0.95551
43602.9623 | 0.97052 | 0.96813 | 0.97732 | 0.97785 | 0.97107 | 0.96678 | 0.96656 | 0.95955
43602.9623 | 0.96383 | 0.96133 | 0.9702 | 0.97044 | 0.96383 | 0.95982 | 0.95971 | 0.95478
43602.9625 | 0.9518 | 0.94996 | 0.95812 | 0.95845 | 0.9508 | 0.94741 | 0.94783 | 0.94678
43602.9625 | 0.94818 | 0.94677 | 0.95477 | 0.95529 | 0.94739 | 0.94405 | 0.94454 | 0.94437
43602.9628 | 0.95957 | 0.95735 | 0.96604 | 0.96656 | 0.959 | 0.95506 | 0.95509 | 0.95162
43602.9628 | 0.96704 | 0.96425 | 0.97333 | 0.9742 | 0.96648 | 0.96242 | 0.96212 | 0.95645
43602.963 | 0.95382 | 0.95191 | 0.96037 | 0.96074 | 0.95322 | 0.94986 | 0.95019 | 0.94822
43602.963 | 0.9483 | 0.94679 | 0.95481 | 0.95559 | 0.94718 | 0.94393 | 0.94435 | 0.94434
43602.9633 | 0.9402 | 0.93906 | 0.9469 | 0.94709 | 0.93848 | 0.93567 | 0.93636 | 0.93895
43602.9633 | 0.93725 | 0.93629 | 0.944 | 0.94429 | 0.93547 | 0.9328 | 0.93345 | 0.93696
43602.9635 | 0.93161 | 0.93097 | 0.93862 | 0.93886 | 0.9297 | 0.92738 | 0.92811 | 0.93311
43602.9635 | 0.92954 | 0.92899 | 0.93629 | 0.93677 | 0.92735 | 0.92512 | 0.9259 | 0.93169
43602.9638 | 0.92557 | 0.92499 | 0.93209 | 0.93235 | 0.92299 | 0.92108 | 0.9219 | 0.9289
43602.9638 | 0.92378 | 0.92324 | 0.93035 | 0.93062 | 0.92118 | 0.91917 | 0.9201 | 0.92767
43602.964 | 0.9208 | 0.92045 | 0.92733 | 0.92786 | 0.91795 | 0.91603 | 0.91747 | 0.92558
43602.964 | 0.91963 | 0.91926 | 0.9262 | 0.92668 | 0.91673 | 0.9147 | 0.91608 | 0.92478
43602.9643 | 0.95286 | 0.95078 | 0.95929 | 0.95987 | 0.94725 | 0.94392 | 0.94427 | 0.94412
43602.9643 | 0.97091 | 0.96808 | 0.97745 | 0.97801 | 0.97014 | 0.96589 | 0.96599 | 0.9589
43602.9645 | 0.96605 | 0.96323 | 0.97276 | 0.9728 | 0.96633 | 0.96249 | 0.96216 | 0.95634
43602.9645 | 0.96166 | 0.95912 | 0.9682 | 0.96836 | 0.96162 | 0.95773 | 0.95758 | 0.95327
43602.9648 | 0.9489 | 0.94705 | 0.95548 | 0.95586 | 0.9483 | 0.94511 | 0.94519 | 0.94498
43602.9648 | 0.94342 | 0.94178 | 0.95007 | 0.95042 | 0.94229 | 0.93914 | 0.93965 | 0.94096
43602.965 | 0.93674 | 0.93554 | 0.94362 | 0.94391 | 0.93533 | 0.93222 | 0.93296 | 0.93654
43602.965 | 0.93454 | 0.93341 | 0.94132 | 0.94137 | 0.93277 | 0.92984 | 0.93068 | 0.93486
43602.9653 | 0.93015 | 0.92929 | 0.93692 | 0.93716 | 0.92804 | 0.92558 | 0.92643 | 0.93202
43602.9653 | 0.92728 | 0.92673 | 0.93397 | 0.93465 | 0.92506 | 0.92282 | 0.92384 | 0.92997
43602.9655 | 0.92269 | 0.9222 | 0.9293 | 0.92976 | 0.91989 | 0.91763 | 0.91912 | 0.92678
43602.9655 | 0.92062 | 0.92039 | 0.92748 | 0.9282 | 0.91792 | 0.91592 | 0.91749 | 0.92563
43602.9658 | 0.91758 | 0.91742 | 0.92407 | 0.92491 | 0.91469 | 0.9126 | 0.91412 | 0.92331
43602.9658 | 0.91642 | 0.91624 | 0.92277 | 0.92334 | 0.91329 | 0.9113 | 0.91313 | 0.92253
43602.966 | 0.91401 | 0.91383 | 0.92069 | 0.92101 | 0.91089 | 0.90897 | 0.91073 | 0.9209
43602.966 | 0.91297 | 0.91301 | 0.91964 | 0.92019 | 0.90958 | 0.90794 | 0.90928 | 0.92016
43602.9663 | 0.91082 | 0.91065 | 0.91747 | 0.91771 | 0.90728 | 0.90564 | 0.90749 | 0.91889
43602.9663 | 0.90987 | 0.90988 | 0.91612 | 0.91716 | 0.90603 | 0.90457 | 0.90631 | 0.91802
43602.9665 | 0.90763 | 0.90768 | 0.91396 | 0.91486 | 0.90382 | 0.90234 | 0.90413 | 0.9166
43602.9665 | 0.90703 | 0.90693 | 0.91341 | 0.91382 | 0.9029 | 0.90129 | 0.90326 | 0.91603
43602.9668 | 0.90551 | 0.90538 | 0.91193 | 0.91218 | 0.90156 | 0.90021 | 0.90176 | 0.9151
43602.9668 | 0.90459 | 0.90467 | 0.9111 | 0.91177 | 0.90022 | 0.89916 | 0.90113 | 0.91442
43602.967 | 0.9027 | 0.90325 | 0.90992 | 0.9099 | 0.8985 | 0.89733 | 0.89952 | 0.9132
43602.967 | 0.90222 | 0.90237 | 0.90876 | 0.9093 | 0.89758 | 0.8966 | 0.89837 | 0.91277
43602.9673 | 0.90039 | 0.90089 | 0.90689 | 0.90745 | 0.8959 | 0.89515 | 0.89684 | 0.91155
43602.9673 | 0.89954 | 0.89995 | 0.90616 | 0.9068 | 0.89499 | 0.89416 | 0.89657 | 0.91099
43602.9675 | 0.8982 | 0.89861 | 0.90429 | 0.90518 | 0.89358 | 0.89237 | 0.8947 | 0.91
43602.9675 | 0.89711 | 0.89796 | 0.90362 | 0.9045 | 0.89264 | 0.89157 | 0.89372 | 0.90942
43602.9678 | 0.89557 | 0.89643 | 0.90236 | 0.90319 | 0.89115 | 0.89029 | 0.89268 | 0.90833
43602.9678 | 0.89493 | 0.89587 | 0.90167 | 0.90264 | 0.89048 | 0.88958 | 0.89205 | 0.90796
43602.968 | 0.8936 | 0.89448 | 0.90066 | 0.90092 | 0.8889 | 0.88826 | 0.89046 | 0.907
43602.968 | 0.89293 | 0.89392 | 0.89956 | 0.90027 | 0.88809 | 0.8876 | 0.88998 | 0.90666
43602.9683 | 0.89135 | 0.89268 | 0.89827 | 0.89901 | 0.88678 | 0.88599 | 0.88858 | 0.90568
43602.9683 | 0.89119 | 0.89194 | 0.89766 | 0.89855 | 0.886 | 0.88544 | 0.88802 | 0.90523
43602.9686 | 0.88972 | 0.89081 | 0.89622 | 0.89711 | 0.88492 | 0.88414 | 0.88679 | 0.90441
43602.9685 | 0.88916 | 0.89036 | 0.89584 | 0.89636 | 0.88414 | 0.8837 | 0.88628 | 0.90407
43602.9688 | 0.88802 | 0.88917 | 0.89452 | 0.89496 | 0.88274 | 0.88237 | 0.88491 | 0.90312
43602.9688 | 0.88742 | 0.88867 | 0.89414 | 0.89472 | 0.88236 | 0.88179 | 0.88472 | 0.90281
43602.9691 | 0.88632 | 0.88749 | 0.8927 | 0.89364 | 0.88102 | 0.8806 | 0.88307 | 0.90206
43602.969 | 0.88596 | 0.88687 | 0.89253 | 0.89299 | 0.88048 | 0.88015 | 0.8826 | 0.90178
43602.9693 | 0.88471 | 0.88581 | 0.89108 | 0.89162 | 0.87935 | 0.87902 | 0.88162 | 0.90093
43602.9693 | 0.88418 | 0.88517 | 0.89072 | 0.89141 | 0.87879 | 0.87797 | 0.88096 | 0.90053
43602.9696 | 0.89491 | 0.89572 | 0.90141 | 0.90191 | 0.89036 | 0.88955 | 0.89171 | 0.90791
43602.9695 | 0.93216 | 0.93097 | 0.93855 | 0.93928 | 0.92688 | 0.92439 | 0.92468 | 0.93111
43602.9698 | 0.96317 | 0.96026 | 0.96994 | 0.97046 | 0.96198 | 0.9581 | 0.95764 | 0.95323
43602.9698 | 0.97028 | 0.96705 | 0.97713 | 0.97742 | 0.96934 | 0.96529 | 0.96479 | 0.95804
43602.9701 | 0.97176 | 0.96839 | 0.9783 | 0.97893 | 0.97143 | 0.96731 | 0.96662 | 0.95927
43602.9701 | 0.96871 | 0.96544 | 0.97521 | 0.97625 | 0.96867 | 0.96475 | 0.96404 | 0.9576
43602.9703 | 0.95619 | 0.95357 | 0.96294 | 0.96337 | 0.95556 | 0.95231 | 0.95204 | 0.9492
43602.9703 | 0.9497 | 0.94753 | 0.95665 | 0.95666 | 0.94858 | 0.94579 | 0.94554 | 0.94485
43602.9706 | 0.93763 | 0.9361 | 0.94447 | 0.94455 | 0.93603 | 0.93351 | 0.93369 | 0.93677
43602.9706 | 0.93409 | 0.93292 | 0.94097 | 0.94134 | 0.93222 | 0.92986 | 0.93038 | 0.93444
43602.9708 | 0.92901 | 0.92772 | 0.93531 | 0.9358 | 0.92664 | 0.92433 | 0.92495 | 0.93073
43602.9708 | 0.92669 | 0.92557 | 0.93305 | 0.93371 | 0.92424 | 0.9219 | 0.92299 | 0.9292
43602.9711 | 0.92071 | 0.92014 | 0.92734 | 0.92792 | 0.91818 | 0.9162 | 0.9174 | 0.92537
43602.9711 | 0.91824 | 0.91765 | 0.92444 | 0.92566 | 0.91535 | 0.91352 | 0.91502 | 0.92355
43602.9713 | 0.9135 | 0.91313 | 0.92029 | 0.92096 | 0.91035 | 0.90861 | 0.91028 | 0.92034
43602.9713 | 0.91251 | 0.91187 | 0.91851 | 0.91924 | 0.90893 | 0.90731 | 0.90902 | 0.9193
43602.9716 | 0.90859 | 0.90834 | 0.91509 | 0.91578 | 0.90496 | 0.90365 | 0.9053 | 0.91687
43602.9716 | 0.90695 | 0.90679 | 0.9138 | 0.91426 | 0.90313 | 0.90188 | 0.90359 | 0.91584
43602.9718 | 0.90391 | 0.9038 | 0.9104 | 0.91086 | 0.89966 | 0.89852 | 0.90033 | 0.91368
43602.9718 | 0.90223 | 0.90242 | 0.90868 | 0.90917 | 0.89832 | 0.89731 | 0.89902 | 0.91251
43602.9721 | 0.89919 | 0.89952 | 0.90532 | 0.90599 | 0.8949 | 0.89404 | 0.89576 | 0.91055
43602.9721 | 0.89785 | 0.89805 | 0.90402 | 0.90467 | 0.89336 | 0.89271 | 0.89462 | 0.90954
43602.9723 | 0.89509 | 0.89559 | 0.90145 | 0.90213 | 0.89039 | 0.88984 | 0.89182 | 0.90774
43602.9723 | 0.89361 | 0.89421 | 0.90029 | 0.90057 | 0.88875 | 0.88825 | 0.89035 | 0.90668
43602.9726 | 0.89075 | 0.89139 | 0.89754 | 0.89788 | 0.88597 | 0.88528 | 0.88749 | 0.90479
43602.9726 | 0.88935 | 0.89013 | 0.89609 | 0.89663 | 0.88443 | 0.88381 | 0.88609 | 0.90389
43602.9728 | 0.8866 | 0.88802 | 0.89324 | 0.89397 | 0.88154 | 0.88114 | 0.88378 | 0.90204
43602.9728 | 0.88543 | 0.88651 | 0.89243 | 0.89258 | 0.88043 | 0.87981 | 0.8823 | 0.90125
43602.9731 | 0.88265 | 0.88405 | 0.88972 | 0.89023 | 0.87728 | 0.87711 | 0.87933 | 0.89935
43602.9731 | 0.88111 | 0.8825 | 0.88801 | 0.88907 | 0.87589 | 0.87562 | 0.87787 | 0.89834
43602.9734 | 0.87855 | 0.88005 | 0.88524 | 0.88635 | 0.87315 | 0.8729 | 0.87543 | 0.89659
43602.9733 | 0.87728 | 0.87895 | 0.88411 | 0.88493 | 0.87185 | 0.87153 | 0.87436 | 0.89558
43602.9736 | 0.87449 | 0.87621 | 0.88126 | 0.88184 | 0.86894 | 0.86865 | 0.87139 | 0.894
43602.9736 | 0.87325 | 0.87493 | 0.88014 | 0.88069 | 0.86764 | 0.86744 | 0.8703 | 0.89307
43602.9739 | 0.87023 | 0.87201 | 0.87742 | 0.87779 | 0.86415 | 0.86454 | 0.86698 | 0.89109
43602.9738 | 0.86876 | 0.87081 | 0.87594 | 0.87635 | 0.86287 | 0.86312 | 0.86655 | 0.89001
43602.9741 | 0.86593 | 0.86792 | 0.87297 | 0.87353 | 0.85964 | 0.86021 | 0.86289 | 0.88806
43602.9741 | 0.8647 | 0.86664 | 0.87152 | 0.8721 | 0.85829 | 0.85893 | 0.86142 | 0.88723
43602.9744 | 0.86197 | 0.86428 | 0.86908 | 0.86957 | 0.85582 | 0.85613 | 0.85911 | 0.88525
43602.9744 | 0.86063 | 0.86281 | 0.86728 | 0.86815 | 0.85414 | 0.85459 | 0.85721 | 0.88448
43602.9746 | 0.8601 | 0.86274 | 0.86718 | 0.86774 | 0.85267 | 0.85337 | 0.85648 | 0.88358
43602.9746 | 0.87049 | 0.87245 | 0.87763 | 0.87801 | 0.86306 | 0.8635 | 0.86562 | 0.89022
43602.9749 | 0.92805 | 0.92684 | 0.93483 | 0.9356 | 0.92387 | 0.92154 | 0.92199 | 0.9287
43602.9749 | 0.93755 | 0.93583 | 0.94424 | 0.94463 | 0.93512 | 0.93252 | 0.93277 | 0.93602
43602.9751 | 0.93983 | 0.93785 | 0.94665 | 0.94712 | 0.93832 | 0.93553 | 0.93566 | 0.93807
43602.9751 | 0.93549 | 0.93389 | 0.94247 | 0.94303 | 0.93372 | 0.93114 | 0.93188 | 0.93514
43602.9754 | 0.9249 | 0.92375 | 0.93203 | 0.93217 | 0.92263 | 0.92051 | 0.92133 | 0.92788
43602.9754 | 0.91928 | 0.91857 | 0.92646 | 0.9268 | 0.91647 | 0.91468 | 0.91593 | 0.92406
43602.9756 | 0.91186 | 0.91141 | 0.91926 | 0.91951 | 0.90871 | 0.90716 | 0.90861 | 0.91901
43602.9756 | 0.90983 | 0.90965 | 0.91668 | 0.91729 | 0.90621 | 0.90469 | 0.90618 | 0.91738
43602.9759 | 0.90427 | 0.90414 | 0.91151 | 0.91187 | 0.90015 | 0.89904 | 0.90099 | 0.91371
43602.9759 | 0.90165 | 0.90183 | 0.90893 | 0.90905 | 0.89748 | 0.8965 | 0.89861 | 0.91205
43602.9762 | 0.89701 | 0.89755 | 0.90371 | 0.90407 | 0.89257 | 0.89186 | 0.89358 | 0.90884
43602.9761 | 0.89516 | 0.89558 | 0.90214 | 0.90237 | 0.89064 | 0.88978 | 0.89189 | 0.90754
43602.9764 | 0.89074 | 0.8916 | 0.89787 | 0.89838 | 0.88615 | 0.88546 | 0.88739 | 0.90465
43602.9764 | 0.88868 | 0.89006 | 0.89666 | 0.8969 | 0.88446 | 0.88352 | 0.88581 | 0.90346
43602.9767 | 0.88479 | 0.88633 | 0.89234 | 0.89286 | 0.88021 | 0.87958 | 0.88232 | 0.90075
43602.9766 | 0.88274 | 0.88452 | 0.89039 | 0.89059 | 0.87825 | 0.87763 | 0.87979 | 0.89948
43602.9769 | 0.87944 | 0.88076 | 0.88682 | 0.88691 | 0.87421 | 0.87389 | 0.87666 | 0.89701
43602.9769 | 0.8775 | 0.87917 | 0.88503 | 0.88546 | 0.87247 | 0.87224 | 0.87491 | 0.89586
43602.9772 | 0.87445 | 0.87611 | 0.88223 | 0.88225 | 0.86903 | 0.86916 | 0.87113 | 0.89371
43602.9772 | 0.87249 | 0.87454 | 0.88021 | 0.88035 | 0.86699 | 0.86732 | 0.86978 | 0.89256
43602.9774 | 0.8692 | 0.87145 | 0.87667 | 0.87708 | 0.86349 | 0.86379 | 0.86736 | 0.89035
43602.9774 | 0.8678 | 0.86973 | 0.87503 | 0.87554 | 0.86178 | 0.86242 | 0.86451 | 0.8892
43602.9777 | 0.86474 | 0.86694 | 0.87171 | 0.87283 | 0.8586 | 0.85937 | 0.86221 | 0.88712
43602.9777 | 0.86311 | 0.86543 | 0.87059 | 0.87113 | 0.85692 | 0.85809 | 0.86072 | 0.88618
43602.9779 | 0.86006 | 0.86254 | 0.86717 | 0.86785 | 0.85352 | 0.85472 | 0.85734 | 0.88409
43602.9779 | 0.85868 | 0.86091 | 0.86555 | 0.86637 | 0.85181 | 0.85319 | 0.85623 | 0.88297
43602.9782 | 0.85552 | 0.85813 | 0.86271 | 0.86331 | 0.84864 | 0.84992 | 0.85258 | 0.88093
43602.9782 | 0.85386 | 0.85692 | 0.86143 | 0.86226 | 0.84703 | 0.84798 | 0.85127 | 0.87975
43602.9784 | 0.85144 | 0.85398 | 0.85855 | 0.85932 | 0.84409 | 0.84555 | 0.84789 | 0.87792
43602.9784 | 0.8496 | 0.85249 | 0.85667 | 0.85731 | 0.84235 | 0.8437 | 0.84648 | 0.87675
43602.9787 | 0.84646 | 0.84964 | 0.85367 | 0.85412 | 0.83932 | 0.84078 | 0.84387 | 0.8748
43602.9787 | 0.84533 | 0.84839 | 0.85231 | 0.85284 | 0.83793 | 0.83929 | 0.84206 | 0.87393
43602.979 | 0.84263 | 0.84577 | 0.84997 | 0.85069 | 0.83478 | 0.8363 | 0.83957 | 0.87194
43602.979 | 0.84156 | 0.84474 | 0.84876 | 0.84926 | 0.83365 | 0.83516 | 0.83895 | 0.87125
43602.9792 | 0.83792 | 0.84132 | 0.84503 | 0.84561 | 0.83006 | 0.83157 | 0.83457 | 0.86882
43602.9792 | 0.8361 | 0.83964 | 0.84354 | 0.84404 | 0.8282 | 0.83002 | 0.83282 | 0.86781
43602.9795 | 0.83204 | 0.83586 | 0.83942 | 0.84009 | 0.82397 | 0.82563 | 0.8292 | 0.86495
43602.9795 | 0.8308 | 0.83437 | 0.83783 | 0.83863 | 0.82237 | 0.82411 | 0.82782 | 0.86393
43602.9798 | 0.82708 | 0.83098 | 0.83441 | 0.83516 | 0.81836 | 0.82066 | 0.82374 | 0.86138
43602.9798 | 0.82575 | 0.83004 | 0.83306 | 0.83397 | 0.81718 | 0.81954 | 0.82295 | 0.86062
43602.98 | 0.82265 | 0.82684 | 0.82986 | 0.83052 | 0.81361 | 0.81619 | 0.81939 | 0.8584
43602.98 | 0.82106 | 0.82538 | 0.82862 | 0.82923 | 0.81227 | 0.81469 | 0.81743 | 0.85751
43602.9803 | 0.81797 | 0.82227 | 0.82527 | 0.82609 | 0.80885 | 0.81158 | 0.81478 | 0.85554
43602.9803 | 0.81647 | 0.8208 | 0.82354 | 0.82452 | 0.80724 | 0.81001 | 0.81467 | 0.85437
43602.9806 | 0.81315 | 0.81795 | 0.82046 | 0.82138 | 0.80364 | 0.80655 | 0.81183 | 0.852
43602.9805 | 0.81176 | 0.81651 | 0.81913 | 0.81996 | 0.80204 | 0.80495 | 0.80812 | 0.85114
43602.9808 | 0.80881 | 0.81363 | 0.81611 | 0.81673 | 0.79919 | 0.80207 | 0.80601 | 0.84915
43602.9808 | 0.80734 | 0.81249 | 0.8149 | 0.8156 | 0.79761 | 0.80065 | 0.80578 | 0.84817
43602.9811 | 0.80581 | 0.81058 | 0.81303 | 0.81407 | 0.79567 | 0.79883 | 0.80263 | 0.84705
43602.9811 | 0.80448 | 0.80945 | 0.81185 | 0.81284 | 0.7946 | 0.79756 | 0.80163 | 0.8462
43602.9813 | 0.8009 | 0.8063 | 0.8081 | 0.80967 | 0.79088 | 0.79407 | 0.79768 | 0.84389
43602.9813 | 0.79888 | 0.8045 | 0.80654 | 0.80783 | 0.7889 | 0.79248 | 0.79629 | 0.84275
43602.9816 | 0.7956 | 0.80124 | 0.80332 | 0.80415 | 0.78536 | 0.78865 | 0.79233 | 0.84019
43602.9816 | 0.79426 | 0.79976 | 0.80185 | 0.80294 | 0.78391 | 0.78748 | 0.79183 | 0.83928
43602.9818 | 0.791 | 0.79666 | 0.79816 | 0.79971 | 0.78052 | 0.7842 | 0.78816 | 0.83709
43602.9818 | 0.78939 | 0.79529 | 0.79685 | 0.79826 | 0.77865 | 0.78247 | 0.78705 | 0.83603
43602.9821 | 0.79914 | 0.80451 | 0.80612 | 0.80714 | 0.78661 | 0.79026 | 0.7934 | 0.84118
43602.9821 | 0.8201 | 0.82445 | 0.82696 | 0.82837 | 0.80896 | 0.81174 | 0.81502 | 0.85548
43602.9824 | 0.84875 | 0.85148 | 0.85587 | 0.85718 | 0.84103 | 0.8424 | 0.84486 | 0.87567
43602.9824 | 0.85259 | 0.85525 | 0.85986 | 0.8611 | 0.84518 | 0.84646 | 0.84888 | 0.87842
43602.9826 | 0.85528 | 0.85783 | 0.86232 | 0.86367 | 0.84887 | 0.84993 | 0.85241 | 0.88063
43602.9826 | 0.84944 | 0.85226 | 0.857 | 0.85798 | 0.84301 | 0.84424 | 0.8463 | 0.87669
43602.9829 | 0.8401 | 0.84344 | 0.8477 | 0.84878 | 0.83281 | 0.83452 | 0.83765 | 0.87048
43602.9829 | 0.83537 | 0.83881 | 0.84295 | 0.84362 | 0.82775 | 0.82941 | 0.83243 | 0.86709
43602.9831 | 0.82975 | 0.83335 | 0.83729 | 0.83798 | 0.82124 | 0.8232 | 0.8265 | 0.863
43602.9831 | 0.82798 | 0.83197 | 0.83593 | 0.83654 | 0.81974 | 0.82183 | 0.82519 | 0.86208
43602.9834 | 0.82299 | 0.82708 | 0.83009 | 0.83178 | 0.81423 | 0.81659 | 0.82018 | 0.85857
43602.9834 | 0.8207 | 0.82514 | 0.82841 | 0.82981 | 0.81193 | 0.81442 | 0.8183 | 0.85715
43602.9836 | 0.81707 | 0.82172 | 0.82494 | 0.82595 | 0.80838 | 0.81077 | 0.81425 | 0.85481
43602.9836 | 0.81561 | 0.82031 | 0.82353 | 0.82446 | 0.80675 | 0.80943 | 0.81337 | 0.85373
43602.9839 | 0.8121 | 0.81696 | 0.81986 | 0.82086 | 0.80298 | 0.8059 | 0.80913 | 0.85134
43602.9839 | 0.81054 | 0.81548 | 0.8184 | 0.81959 | 0.80141 | 0.80435 | 0.80772 | 0.85033
43602.9842 | 0.80765 | 0.8124 | 0.81508 | 0.8162 | 0.79795 | 0.80103 | 0.80475 | 0.84818
43602.9841 | 0.80612 | 0.81096 | 0.81371 | 0.81474 | 0.79656 | 0.79967 | 0.80302 | 0.84706
43602.9844 | 0.80288 | 0.80803 | 0.81036 | 0.81191 | 0.79321 | 0.79634 | 0.80219 | 0.84496
43602.9844 | 0.80153 | 0.80667 | 0.80921 | 0.81052 | 0.79148 | 0.79497 | 0.79847 | 0.84403
43602.9847 | 0.79927 | 0.80449 | 0.80673 | 0.80801 | 0.78918 | 0.79275 | 0.79598 | 0.84252
43602.9847 | 0.79741 | 0.80273 | 0.80489 | 0.80608 | 0.78731 | 0.7909 | 0.79461 | 0.84126
43602.9849 | 0.79415 | 0.79966 | 0.80158 | 0.80299 | 0.78385 | 0.78726 | 0.79176 | 0.83895
43602.9849 | 0.79268 | 0.7984 | 0.79991 | 0.80171 | 0.7822 | 0.78569 | 0.78974 | 0.83799
43602.9852 | 0.78959 | 0.79569 | 0.79704 | 0.79855 | 0.77926 | 0.78262 | 0.78666 | 0.83608
43602.9852 | 0.78855 | 0.79456 | 0.79621 | 0.7976 | 0.77788 | 0.78181 | 0.78505 | 0.83517
43602.9854 | 0.78534 | 0.79153 | 0.79293 | 0.79419 | 0.77453 | 0.7789 | 0.78455 | 0.83313
43602.9854 | 0.78387 | 0.79033 | 0.79153 | 0.79304 | 0.7731 | 0.77726 | 0.78165 | 0.83221
43602.9857 | 0.78114 | 0.78722 | 0.7887 | 0.79 | 0.76988 | 0.77408 | 0.77794 | 0.83016
43602.9857 | 0.77939 | 0.78592 | 0.78707 | 0.78877 | 0.76803 | 0.77239 | 0.77567 | 0.82911
43602.986 | 0.7766 | 0.78332 | 0.78434 | 0.78585 | 0.76504 | 0.76956 | 0.77245 | 0.82712
43602.986 | 0.77532 | 0.78189 | 0.78292 | 0.78438 | 0.76373 | 0.76827 | 0.77172 | 0.82623
43602.9862 | 0.77225 | 0.77897 | 0.78022 | 0.7814 | 0.76032 | 0.76528 | 0.76893 | 0.82418
43602.9862 | 0.77113 | 0.77771 | 0.77907 | 0.78014 | 0.75916 | 0.76394 | 0.76786 | 0.82348
43602.9865 | 0.76797 | 0.7749 | 0.77595 | 0.77668 | 0.75561 | 0.76085 | 0.76501 | 0.82131
43602.9865 | 0.76673 | 0.77375 | 0.77482 | 0.77553 | 0.75459 | 0.75959 | 0.76408 | 0.82034
43602.9867 | 0.76341 | 0.77063 | 0.77159 | 0.7724 | 0.75129 | 0.75589 | 0.76252 | 0.81831
43602.9867 | 0.76242 | 0.76968 | 0.77073 | 0.77145 | 0.75009 | 0.75521 | 0.76086 | 0.81773
43602.9871 | 0.75855 | 0.76601 | 0.76672 | 0.76747 | 0.7459 | 0.75129 | 0.75494 | 0.81497
43602.9871 | 0.75699 | 0.76431 | 0.76492 | 0.76581 | 0.74439 | 0.74978 | 0.75385 | 0.81381
43602.9874 | 0.75365 | 0.76137 | 0.76176 | 0.76304 | 0.74089 | 0.74674 | 0.75169 | 0.81177
43602.9874 | 0.75225 | 0.75996 | 0.76042 | 0.76168 | 0.73949 | 0.74515 | 0.74915 | 0.81074
43602.9876 | 0.74926 | 0.75719 | 0.75738 | 0.75839 | 0.73621 | 0.74182 | 0.74659 | 0.80869
43602.9876 | 0.74796 | 0.75591 | 0.75616 | 0.7574 | 0.73483 | 0.74062 | 0.74459 | 0.80789
43602.9879 | 0.74532 | 0.75322 | 0.75309 | 0.75437 | 0.73179 | 0.73761 | 0.74279 | 0.80587
43602.9879 | 0.74399 | 0.75205 | 0.7523 | 0.75361 | 0.73062 | 0.73625 | 0.74109 | 0.80511
43602.9881 | 0.74127 | 0.74928 | 0.74936 | 0.7506 | 0.72765 | 0.73379 | 0.73769 | 0.80304
43602.9881 | 0.73998 | 0.7483 | 0.74817 | 0.74962 | 0.7265 | 0.73247 | 0.73888 | 0.80239
43602.9884 | 0.73709 | 0.74553 | 0.74553 | 0.74665 | 0.72368 | 0.72968 | 0.7345 | 0.80053
43602.9884 | 0.73591 | 0.74438 | 0.74433 | 0.74534 | 0.72251 | 0.72847 | 0.73465 | 0.79958
43602.9887 | 0.73309 | 0.74179 | 0.74122 | 0.74239 | 0.71916 | 0.72546 | 0.73081 | 0.79763
43602.9887 | 0.73186 | 0.74067 | 0.74011 | 0.74124 | 0.7179 | 0.72411 | 0.73011 | 0.79679
43602.9889 | 0.72901 | 0.73783 | 0.73736 | 0.73823 | 0.71481 | 0.72132 | 0.72655 | 0.79497
43602.9889 | 0.72782 | 0.73669 | 0.73566 | 0.73719 | 0.71366 | 0.71981 | 0.72763 | 0.79405
43602.9892 | 0.72464 | 0.73392 | 0.73292 | 0.73433 | 0.71041 | 0.71702 | 0.7222 | 0.79217
43602.9892 | 0.72354 | 0.73245 | 0.73164 | 0.73304 | 0.70907 | 0.71564 | 0.72061 | 0.79127
43602.9894 | 0.72102 | 0.72993 | 0.729 | 0.73036 | 0.70609 | 0.71298 | 0.7203 | 0.78925
43602.9894 | 0.72007 | 0.72918 | 0.72811 | 0.72929 | 0.70488 | 0.71182 | 0.71772 | 0.78871
43602.9897 | 0.71775 | 0.72733 | 0.72566 | 0.72737 | 0.70291 | 0.70971 | 0.71514 | 0.78734
43602.9897 | 0.71661 | 0.7262 | 0.72471 | 0.72606 | 0.70142 | 0.70851 | 0.71432 | 0.7865
43602.99 | 0.71408 | 0.72407 | 0.7228 | 0.72398 | 0.69934 | 0.70621 | 0.71187 | 0.785
43602.9899 | 0.71362 | 0.72326 | 0.72193 | 0.72318 | 0.69845 | 0.70562 | 0.71172 | 0.78449
43602.9902 | 0.71117 | 0.72081 | 0.71954 | 0.72086 | 0.69585 | 0.70295 | 0.70858 | 0.78267
43602.9902 | 0.70989 | 0.71974 | 0.71843 | 0.71962 | 0.69429 | 0.70175 | 0.70781 | 0.78183
43602.9905 | 0.70737 | 0.71735 | 0.71568 | 0.7171 | 0.6916 | 0.69917 | 0.7042 | 0.78023
43602.9905 | 0.70625 | 0.71613 | 0.71458 | 0.71613 | 0.6906 | 0.69818 | 0.70686 | 0.77939
43602.9907 | 0.70369 | 0.7139 | 0.7122 | 0.71355 | 0.68777 | 0.6954 | 0.7007 | 0.77766
43602.9907 | 0.70261 | 0.71289 | 0.71143 | 0.71248 | 0.68695 | 0.69439 | 0.70165 | 0.77688
43602.991 | 0.70008 | 0.71051 | 0.70884 | 0.7104 | 0.68429 | 0.69194 | 0.70033 | 0.77537
43602.991 | 0.69894 | 0.70952 | 0.70752 | 0.70915 | 0.68323 | 0.69079 | 0.69608 | 0.77462
43602.9913 | 0.69703 | 0.70754 | 0.70552 | 0.70678 | 0.68058 | 0.68843 | 0.69427 | 0.77302
43602.9913 | 0.69575 | 0.70649 | 0.7043 | 0.70574 | 0.67939 | 0.68741 | 0.6924 | 0.77227
43602.9915 | 0.69373 | 0.70434 | 0.70265 | 0.70351 | 0.67736 | 0.68536 | 0.69322 | 0.77096
43602.9915 | 0.69315 | 0.70356 | 0.70173 | 0.70287 | 0.67634 | 0.68447 | 0.69308 | 0.77027
43602.9918 | 0.69081 | 0.70169 | 0.69945 | 0.70057 | 0.67456 | 0.68252 | 0.68838 | 0.76904
43602.9918 | 0.68909 | 0.70002 | 0.69769 | 0.69902 | 0.67232 | 0.68056 | 0.68615 | 0.76766
43602.9922 | 0.68629 | 0.69745 | 0.69504 | 0.69631 | 0.66959 | 0.67774 | 0.68362 | 0.76595